Copyright 2012 AIA
MasterSpec Professional
06/12

Copyright 2012 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 211213 - FIRE-SUPPRESSION HOSES AND NOZZLES
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. NPS 1-1/2 (DN 40) rack-type hose stations.

2. NPS 1-1/2 (DN 40) reel-type hose stations.

B. Related Requirements:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

1. Section 104413 "Fire Protection Cabinets" for hose cabinets.

2. Section 211200 "Fire-Suppression Standpipes" for fire hose valves.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product.

B. Shop Drawings:

1. Include plans, elevations, sections, and mounting and attachment details.

1.3 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

2.1 NPS 1-1/2 (DN 40) RACK-TYPE HOSE STATIONS

Coordinate cabinet-mounted units with requirements in Section 104413 "Fire Protection Cabinets."

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. American Fire Hose & Cabinet.

2. Angus; Part of Kidde Fire Fighting Organization.

3. Brooks Equipment Co., Inc.

4. Elkhart Brass Mfg. Company, Inc.

5. Fire-End & Croker Corporation.

6. GMR International Equipment Corporation.

7. Potter Roemer.

8. Viking Corporation.

9. Wilson & Cousins Inc.

10. <Insert manufacturer's name>.

C. Hose Rack:

1. Standard: UL 47.

2. Material: [Brass or bronze with polished chrome-plated] [Steel with red-enamel] finish.

3. Type: Hose-rack assembly. Include hose valve, hose rack, water-retention device, hose pins, and hose.

4. Operation: Semiautomatic.

5. Sized to hold fire hose.

D. Hose Valve:

1. Standard: UL 668, NPS 1-1/2 (DN 40), for connecting fire hose.

If retaining first option in "Type" Subparagraph below, also retain pressure-control device and insert outlet pressure setting in appropriate subparagraphs below.

2. Type: [Adjustable] [Nonadjustable].

3. Pressure-Control Device: [Not required] [Pressure reducing] [Pressure reducing or pressure restricting] [Pressure restricting].

4. Design Outlet Pressure Setting: [Not applicable] <Insert psig (kPa)>.

5. Hose Valve and Trim Finish: [Polished chrome-plated] [Rough brass or bronze] [Rough chrome-plated].

6. Pressure Rating: 300 psig (2070 kPa) minimum.

7. Pattern: Angle.

8. Material: Brass or bronze.

9. Pressure-Control Device: UL 1468 integral or for field installation if indicated.

10. Size: NPS 1-1/2 (DN 40).

11. Inlet: Female pipe threads.

12. Outlet: Male hose threads according to NFPA 1963 and matching local fire-department threads.

E. Hose:

1. Standards: NFPA 1961 and UL 219 lined fire hose with swivel inlet, coupling, gaskets, and nozzle.

2. Size: NPS 1-1/2 (DN 40).

3. Length: [50 feet (15 m)] [75 feet (23 m)] [100 feet (30 m)] <Insert dimension>.

4. Jacket: [Combination of natural and synthetic threads] [Natural thread] [Synthetic thread].

5. Lining: [Rubber, plastic, or combination of rubber and plastic compounds] [Combination of rubber and plastic compounds] [Rubber compound] [Plastic compound].

6. Cover: Rubber, plastic, or combination of rubber and plastic compounds.

7. Nozzle: UL 401.

a. Material: [Brass] [Polished brass] [Rough chrome-plated brass] [Polished chrome-plated brass] [Polycarbonate plastic].

b. Type: [Plain, for nonadjustable water stream] [Spray, adjustable from shutoff to fog spray or straight stream] [Spray, adjustable from shutoff to full fog; for use on electrical fires].

2.2 NPS 1-1/2 (DN 40) REEL-TYPE HOSE STATIONS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. American Fire Hose & Cabinet.

2. Elkhart Brass Mfg. Company, Inc.

3. Potter Roemer.

4. <Insert manufacturer's name>.

C. Hose Reel:

1. Standard: UL 47.

2. Hose Reel and Bracket Material: Steel.

3. Type: Hose-reel assembly. Include hose valve, wall bracket, hose reel, water-retention device, hose pins, and hose.

4. Operation: Semiautomatic.

5. Sized to hold fire hose.

6. Finish: Red enamel.

D. Hose Valve:

1. Standard: UL 668, NPS 1-1/2 (DN 40), for connecting fire hose.

If retaining first option in "Type" Subparagraph below, also retain pressure-control device and insert outlet pressure setting in appropriate subparagraphs below.

2. Type: [Adjustable] [Nonadjustable].

3. Pressure-Control Device: [Not required] [Pressure reducing] [Pressure reducing or pressure restricting] [Pressure restricting].

4. Design Outlet Pressure Setting: [Not applicable] <Insert psig (kPa)>.

5. Hose Valve and Trim Finish: [Polished chrome-plated] [Rough brass or bronze] [Rough chrome-plated].

6. Pressure Rating: 300 psig (2070 kPa) minimum.

7. Pattern: Angle.

8. Material: Brass or bronze.

9. Pressure-Control Device: UL 1468, integral or for field installation if indicated.

10. Size: NPS 1-1/2 (DN 40).

11. Inlet: Female pipe threads.

12. Outlet: Male hose threads according to NFPA 1963 and matching local fire-department threads.

E. Hose:

1. Standards: NFPA 1961 and UL 219 lined fire hose with swivel inlet, coupling, gaskets, and nozzle.

2. Size: NPS 1-1/2 (DN 40).

3. Length: [50 feet (15 m)] [75 feet (23 m)] [100 feet (30 m)] <Insert dimension>.

4. Jacket: [Combination of natural and synthetic threads] [Natural thread] [Synthetic thread].

5. Lining: [Rubber, plastic, or combination of rubber and plastic compounds] [Combination of rubber and plastic compounds] [Rubber compound] [Plastic compound].

6. Cover: Rubber, plastic, or combination of rubber and plastic compounds.

7. Nozzle: UL 401.

a. Material: [Brass] [Polished brass] [Rough chrome-plated brass] [Polished chrome-plated brass] [Polycarbonate plastic].

b. Type: Spray, adjustable from shutoff to [fog spray or straight stream] [full fog; for use on electrical fires].

PART 3 -  EXECUTION

3.1 HOSE-STATION INSTALLATION

Indicate hose-station locations, sizes, and special devices on Drawings.

A. Install freestanding hose stations for access and minimum passage restriction.

B. Install NPS 1-1/2 (DN 40) hose-station valves with flow-restricting device unless otherwise indicated.

C. Install freestanding hose stations with support or bracket attached to standpipe.

D. Install wall-mounted, rack hose stations in cabinets. Include pipe escutcheons, with finish matching valves, inside cabinet where water-supply piping penetrates cabinet. Install valves at angle required for connection of fire hose. Comply with requirements for cabinets in Section 104413 "Fire Protection Cabinets."

E. Install hose-reel hose stations on wall with bracket.

END OF SECTION 211213

	FIRE-SUPPRESSION HOSES AND NOZZLES
	211213 - 1



