Copyright 2012 AIA
MasterSpec Professional
06/12

Copyright 2012 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 211316 - DRY-PIPE SPRINKLER SYSTEMS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Pipes, fittings, and specialties.

2. Fire-protection valves.

3. Sprinkler specialty pipe fittings.

4. Sprinklers.

5. Alarm devices.

6. Pressure gages.

B. Related Sections:

Retain Sections in subparagraphs below that contain requirements Contractor might expect to find in this Section but are specified in other Sections.

1. Section 211119 "Fire-Department Connections" for exposed-, flush-, and yard-type fire-department connections.

2. Section 211200 "Fire-Suppression Standpipes" for standpipe piping.

3. Section 211313 "Wet-Pipe Sprinkler Systems" for wet-pipe sprinkler piping.

4. [Section 213113 "Electric-Drive, Centrifugal Fire Pumps"] [Section 213116 "Diesel-Drive, Centrifugal Fire Pumps"] [Section 213213 "Electric-Drive, Vertical-Turbine Fire Pumps"] [Section 213216 "Diesel-Drive, Vertical-Turbine Fire Pumps"] for fire pumps, pressure-maintenance pumps, and fire-pump controllers.

5. [Section 283111 "Digital, Addressable Fire-Alarm System"] [Section 283112 "Zoned (DC Loop) Fire-Alarm System"] for alarm devices not specified in this Section.

1.2 SYSTEM DESCRIPTIONS

A. Dry-Pipe Sprinkler System: Automatic sprinklers are attached to piping containing compressed air. Opening of sprinklers releases compressed air and permits water pressure to open dry-pipe valve. Water then flows into piping and discharges from sprinklers that are open.

1.3 PERFORMANCE REQUIREMENTS

A. Standard-Pressure Piping System Component: Listed for 175-psig (1200-kPa) minimum working pressure.

Retain first paragraph below if Contractor is required to assume responsibility for design.

B. Delegated Design: Design sprinkler system(s), including comprehensive engineering analysis by a qualified professional engineer, using performance requirements and design criteria indicated.

Retain data in subparagraph below if known and if Owner wants to furnish test data to Contractor.

1. Available fire-hydrant flow test records indicate the following conditions:

a. Date: <Insert test date>.

b. Time: <Insert time> [a.m.] [p.m.]

c. Performed by: <Insert operator's name> of <Insert firm>.

d. Location of Residual Fire Hydrant R: <Insert location>.

e. Location of Flow Fire Hydrant F: <Insert location>.

f. Static Pressure at Residual Fire Hydrant R: <Insert psig (kPa)>.

g. Measured Flow at Flow Fire Hydrant F: <Insert gpm (L/s)>.

h. Residual Pressure at Residual Fire Hydrant R: <Insert psig (kPa)>.

Retain both paragraphs below if system design has not been approved by authorities having jurisdiction.

C. Sprinkler system design shall be approved by authorities having jurisdiction.

Revise or delete first subparagraph below. The margin-of-safety requirement may not be required by authorities having jurisdiction.

1. Margin of Safety for Available Water Flow and Pressure: [10] [20] <Insert number> percent, including losses through water-service piping, valves, and backflow preventers.

2. Sprinkler Occupancy Hazard Classifications:

Revise first 19 subparagraphs below to suit requirements of authorities having jurisdiction. See Appendix A in NFPA 13 for recommended hazard classifications.

a. Automobile Parking Areas: [Ordinary Hazard, Group 1] <Insert classification>.

b. Building Service Areas: [Ordinary Hazard, Group 1] <Insert classification>.

c. Churches: [Light Hazard] <Insert classification>.

d. Electrical Equipment Rooms: [Ordinary Hazard, Group 1] <Insert classification>.

e. Dry Cleaners: [Ordinary Hazard, Group 2] <Insert classification>.

f. General Storage Areas: [Ordinary Hazard, Group 1] <Insert classification>.

g. Laundries: [Ordinary Hazard, Group 1] <Insert classification>.

h. Libraries Except Stack Areas: [Light Hazard] <Insert classification>.

i. Library Stack Areas: [Ordinary Hazard, Group 2] <Insert classification>.

j. Machine Shops: [Ordinary Hazard, Group 2] <Insert classification>.

k. Mechanical Equipment Rooms: [Ordinary Hazard, Group 1] <Insert classification>.

l. Office and Public Areas: [Light Hazard] <Insert classification>.

m. Plastics Processing Areas: [Extra Hazard, Group 2] <Insert classification>.

n. Printing Plants: [Extra Hazard, Group 1] <Insert classification>.

o. Repair Garages: [Ordinary Hazard, Group 2] <Insert classification>.

p. Restaurant Service Areas: [Ordinary Hazard, Group 1] <Insert classification>.

q. Solvent Cleaning Areas: [Extra Hazard, Group 2] <Insert classification>.

r. Upholstering Plants: [Extra Hazard, Group 1] <Insert classification>.

s. <Insert classification>.

3. Minimum Density for Automatic-Sprinkler Piping Design:

Revise first six subparagraphs below to suit requirements of authorities having jurisdiction. Values indicated should provide minimum required total flow for each hazard and group.

a. Light-Hazard Occupancy: [0.10 gpm over 1500-sq. ft. (4.1 mm/min. over 139-sq. m)] <Insert value> area.

b. Ordinary-Hazard, Group 1 Occupancy: [0.15 gpm over 1500-sq. ft. (6.1 mm/min. over 139-sq. m)] <Insert value> area.

c. Ordinary-Hazard, Group 2 Occupancy: [0.20 gpm over 1500-sq. ft. (8.1 mm/min. over 139-sq. m)] <Insert value> area.

d. Extra-Hazard, Group 1 Occupancy: [0.30 gpm over 2500-sq. ft. (12.2 mm/min. over 232-sq. m)] <Insert value> area.

e. Extra-Hazard, Group 2 Occupancy: [0.40 gpm over 2500-sq. ft. (16.3 mm/min. over 232-sq. m)] <Insert value> area.

f. Special Occupancy Hazard: As determined by authorities having jurisdiction.

Retain one of first two subparagraphs below.

4. Maximum Protection Area per Sprinkler: Per UL listing.

5. Maximum Protection Area per Sprinkler:

Revise first five subparagraphs below to suit requirements of authorities having jurisdiction.

a. Office Spaces: [120 sq. ft. (11.1 sq. m)] [225 sq. ft. (20.9 sq. m)] <Insert dimension>.

b. Storage Areas: [130 sq. ft. (12.1 sq. m)] <Insert dimension>.

c. Mechanical Equipment Rooms: [130 sq. ft. (12.1 sq. m)] <Insert dimension>.

d. Electrical Equipment Rooms: [130 sq. ft. (12.1 sq. m)] <Insert dimension>.

e. Other Areas: According to NFPA 13 recommendations unless otherwise indicated.

Revise subparagraph below to suit requirements of authorities having jurisdiction.

6. Total Combined Hose-Stream Demand Requirement: According to NFPA 13 unless otherwise indicated:

a. Light-Hazard Occupancies: [100 gpm (6.3 L/s) for 30 minutes] <Insert requirement>.

b. Ordinary-Hazard Occupancies: [250 gpm (15.75 L/s) for 60 to 90 minutes] <Insert requirement>.

c. Extra-Hazard Occupancies: [500 gpm (31.5 L/s) for 90 to 120 minutes] <Insert requirement>.

d. <Insert requirement>.

D. Seismic Performance: Sprinkler piping shall withstand the effects of earthquake motions determined according to NFPA 13 and [ASCE/SEI 7] <Insert requirement>.

1.4 ACTION SUBMITTALS

A. Product Data: For each type of product indicated.

B. Shop Drawings: For dry-pipe sprinkler systems. Include plans, elevations, sections, details, and attachments to other work.

Retain subparagraph below if equipment includes wiring.

1. Wiring Diagrams: For power, signal, and control wiring.

Paragraph below is defined in Section 013300 "Submittal Procedures" as a "Delegated-Design Submittal." Retain if Work of this Section is required to withstand specific design loads and design responsibilities have been delegated to Contractor or if structural data are required as another way to verify compliance with performance requirements. Professional engineer qualifications are specified in Section 014000 "Quality Requirements."

C. Delegated-Design Submittal: For sprinkler systems indicated to comply with performance requirements and design criteria, including analysis data signed and sealed by the qualified professional engineer responsible for their preparation.

1.5 INFORMATIONAL SUBMITTALS

Coordinate first paragraph below with qualification requirements in Section 014000 "Quality Requirements" and as supplemented in "Quality Assurance" Article.

A. Qualification Data: For qualified Installer[ and professional engineer].

Retain first paragraph below if design by Contractor is specified in "Performance Requirements" Article.

B. Approved Sprinkler Piping Drawings: Working plans, prepared according to NFPA 13, that have been approved by authorities having jurisdiction, including hydraulic calculations if applicable.

C. Field Test Reports and Certificates: Indicate and interpret test results for compliance with performance requirements and as described in NFPA 13. Include "Contractor's Material and Test Certificate for Aboveground Piping."

D. Field quality-control reports.

1.6 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

1.7 QUALITY ASSURANCE

Retain first paragraph below if Contractor is required to assume responsibility for design of fire-suppression systems.

A. Installer Qualifications:

Retain subparagraph below if Contractor is required to assume responsibility for engineering.

1. Installer's responsibilities include designing, fabricating, and installing sprinkler systems and providing professional engineering services needed to assume engineering responsibility. Base calculations on results of fire-hydrant flow test.

Retain subparagraph below if Contractor is required to engage a qualified professional engineer.

a. Engineering Responsibility: Preparation of working plans, calculations, and field test reports by a qualified professional engineer.

B. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

C. NFPA Standards: Sprinkler system equipment, specialties, accessories, installation, and testing shall comply with the following:

1. NFPA 13, "Installation of Sprinkler Systems."

2. NFPA 13R, "Installation of Sprinkler Systems in Residential Occupancies up to and Including Four Stories in Height."

3. NFPA 24, "Installation of Private Fire Service Mains and Their Appurtenances."

PART 2 -  PRODUCTS

2.1 PIPING MATERIALS

See "Writing Guide" Article in the Evaluations for a discussion on this Section's organization and the most efficient way to edit this Section. See "Piping Materials and Standards" Article in Evaluations for a discussion on availability of piping materials covered by referenced standards in corresponding pipe sizes.

A. Comply with requirements in "Piping Schedule" Article for applications of pipe, tube, and fitting materials, and joining methods for specific services, service locations, and pipe sizes.

2.2 STEEL PIPE AND FITTINGS

Pipe in first paragraph below is intended for use with flanged, cut- or roll-grooved, plain-end-pipe, and threaded joints. Pipe is available in NPS 1/8 to NPS 26 (DN 6 to DN 650). Match options for fitting and pipe finish.

A. Standard Weight, Galvanized-Steel Pipe: ASTM A 53/A 53M, [Type E] <Insert type>, [Grade B] <Insert grade>. Pipe ends may be factory or field formed to match joining method.

Pipe in first paragraph below is intended for use with flanged, cut- or roll-grooved, plain-end-pipe, and threaded joints. Pipe is available in NPS 1/2 to NPS 10 (DN 15 to DN 250). Match options for fitting and pipe finish.

B. Schedule 30, Galvanized-Steel Pipe: ASTM A 135; ASTM A 795/A 795M, [Type E] <Insert type>; or ASME B36.10M, wrought steel; with wall thickness not less than Schedule 30 and not more than Schedule 40. Pipe ends may be factory or field formed to match joining method.

Pipe in first paragraph below is intended for use with flanged, roll-grooved, plain-end-pipe, and threaded joints. Pipe is available in NPS 1/2 to NPS 10 (DN 15 to DN 250). Match options for fitting and pipe finish.

C. Thinwall Galvanized-Steel Pipe: ASTM A 135 or ASTM A 795/A 795M, threadable, with wall thickness less than Schedule 30 and equal to or greater than Schedule 10. Pipe ends may be factory or field formed to match joining method.

Nipples in first paragraph below are available in NPS 1/8 to NPS 12 (DN 6 to DN 300).

D. Galvanized-Steel Pipe Nipples: ASTM A 733, made of ASTM A 53/A 53M, standard-weight, seamless steel pipe with threaded ends.

Couplings in first paragraph below are available in NPS 1/8 to NPS 20 (DN 6 to DN 500).

E. Galvanized, Steel Couplings: ASTM A 865, threaded.

Fittings in first paragraph below are available in NPS 1/4 to NPS 12 (DN 8 to DN 300).

F. Galvanized, Gray-Iron Threaded Fittings: ASME B16.4, Class 125, standard pattern.

Unions in first paragraph below are available in NPS 1/4 to NPS 3 (DN 8 to DN 80), but NFPA limits them to NPS 2 (DN 50) and smaller.

G. Malleable- or Ductile-Iron Unions: UL 860.

Flanges in first paragraph below are available in NPS 1 to NPS 96 (DN 25 to DN 2400).

H. Cast-Iron Flanges: ASME B16.1, Class 125.

Fittings in first paragraph below are available in NPS 1 to NPS 2 (DN 25 to DN 50).

I. Plain-End-Pipe Fittings: UL 213, ductile-iron body with retainer lugs that require one-quarter turn or screwed retainer pin to secure pipe in fitting.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Anvil International, Inc.

b. Shurjoint Piping Products.

c. <Insert manufacturer's name>.

J. Grooved-Joint, Steel-Pipe Appurtenances:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Anvil International, Inc.

b. Corcoran Piping System Co.

c. National Fittings, Inc.

d. Shurjoint Piping Products.

e. Tyco Fire & Building Products LP.

f. Victaulic Company.

g. <Insert manufacturer's name>.

2. Pressure Rating: [175 psig (1200 kPa)] [250 psig (1725 kPa)] [300 psig (2070 kPa)] minimum.

3. Galvanized, Grooved-End Fittings for Steel Piping: ASTM A 47/A 47M, malleable-iron casting or ASTM A 536, ductile-iron casting; with dimensions matching steel pipe.

AWWA C606 and UL 213 cover couplings in subparagraph below in NPS 3/4 to at least NPS 12 (DN 20 to at least DN 300).

4. Grooved-End-Pipe Couplings for Steel Piping: AWWA C606 and UL 213, rigid pattern, unless otherwise indicated, for steel-pipe dimensions. Include ferrous housing sections, EPDM-rubber gasket, and bolts and nuts.

2.3 PIPING JOINING MATERIALS

A. Pipe-Flange Gasket Materials: [AWWA C110, rubber, flat face, 1/8 inch (3.2 mm) thick] [or] [ASME B16.21, nonmetallic and asbestos free].

1. Class 125, Cast-Iron Flat-Face Flanges: Full-face gaskets.

B. Metal, Pipe-Flange Bolts and Nuts: ASME B18.2.1, carbon steel unless otherwise indicated.

2.4 LISTED FIRE-PROTECTION VALVES

A. General Requirements:

1. Valves shall be UL listed or FM approved.

2. Minimum Pressure Rating: 175 psig (1200 kPa).

Valves in first paragraph below are available in NPS 2 (DN 50) and larger.

B. Check Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first subparagraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. AFAC Inc.

b. American Cast Iron Pipe Company; Waterous Company Subsidiary.

c. Anvil International, Inc.

d. Clow Valve Company; a division of McWane, Inc.

e. Crane Co.; Crane Valve Group; Crane Valves.

f. Crane Co.; Crane Valve Group; Jenkins Valves.

g. Crane Co.; Crane Valve Group; Stockham Division.

h. Fire-End & Croker Corporation.

i. Fire Protection Products, Inc.

j. Fivalco Inc.

k. Globe Fire Sprinkler Corporation.

l. Groeniger & Company.

m. Kennedy Valve; a division of McWane, Inc.

n. Matco-Norca.

o. Metraflex, Inc.

p. Milwaukee Valve Company.

q. Mueller Co.; Water Products Division.

r. NIBCO INC.

s. Potter Roemer.

t. Reliable Automatic Sprinkler Co., Inc.

u. Shurjoint Piping Products.

v. Tyco Fire & Building Products LP.

w. United Brass Works, Inc.

x. Venus Fire Protection Ltd.

y. Victaulic Company.

z. Viking Corporation.

aa. Watts Water Technologies, Inc.

ab. <Insert manufacturer's name>.

3. Standard: UL 312

4. Pressure Rating: 250 psig (1725 kPa) minimum.

5. Type: Swing check.

6. Body Material: Cast iron.

7. End Connections: Flanged or grooved.

Valves in first paragraph below are available in NPS 2 (DN 50) and smaller.

C. Bronze OS&Y Gate Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first subparagraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Crane Co.; Crane Valve Group; Crane Valves.

b. Crane Co.; Crane Valve Group; Stockham Division.

c. Milwaukee Valve Company.

d. NIBCO INC.

e. United Brass Works, Inc.

f. <Insert manufacturer's name>.

3. Standard: UL 262.

4. Pressure Rating: 175 psig (1200 kPa).

5. Body Material: Bronze.

6. End Connections: Threaded.

Valves in first paragraph below are available in NPS 2 (DN 50) and larger.

D. Iron OS&Y Gate Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first subparagraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. American Cast Iron Pipe Company; Waterous Company Subsidiary.

b. American Valve, Inc.

c. Clow Valve Company; a division of McWane, Inc.

d. Crane Co.; Crane Valve Group; Crane Valves.

e. Crane Co.; Crane Valve Group; Jenkins Valves.

f. Crane Co.; Crane Valve Group; Stockham Division.

g. Hammond Valve.

h. Milwaukee Valve Company.

i. Mueller Co.; Water Products Division.

j. NIBCO INC.

k. Shurjoint Piping Products.

l. Tyco Fire & Building Products LP.

m. United Brass Works, Inc.

n. Watts Water Technologies, Inc.

o. <Insert manufacturer's name>.

3. Standard: UL 262.

4. Pressure Rating: [250 psig (1725 kPa) minimum] [300 psig (2070 kPa)].

5. Body Material: Cast or ductile iron.

6. End Connections: Flanged or grooved.

Valves in paragraph below are available in NPS 2 (DN 50) and larger.

E. Indicating-Type Butterfly Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first subparagraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Anvil International, Inc.

b. Fivalco Inc.

c. Global Safety Products, Inc.

d. Kennedy Valve; a division of McWane, Inc.

e. Milwaukee Valve Company.

f. NIBCO INC.

g. Shurjoint Piping Products.

h. Tyco Fire & Building Products LP.

i. Victaulic Company.

j. <Insert manufacturer's name>.

3. Standard: UL 1091.

4. Pressure Rating: 175 psig (1200 kPa) minimum.

5. Valves NPS 2 (DN 50) and Smaller:

a. Valve Type: Ball or butterfly.

b. Body Material: Bronze.

c. End Connections: Threaded.

6. Valves NPS 2-1/2 (DN 65) and Larger:

a. Valve Type: Butterfly.

b. Body Material: Cast or ductile iron.

c. End Connections: Flanged, grooved, or wafer.

7. Valve Operation: Integral [electrical, 115-V ac, prewired, single-circuit, supervisory switch] [electrical, 115-V ac, prewired, two-circuit, supervisory switch] [visual] indicating device.

2.5 TRIM AND DRAIN VALVES

Trim and drain valves are UL listed, are typically used as part of specialty control valve trim and drain piping, and are NPS 2 (DN 50) and smaller. No UL standard exists for these valves.

A. General Requirements:

1. Standard: UL's "Fire Protection Equipment Directory" listing or "Approval Guide," published by FM Global, listing.

2. Minimum Pressure Rating: 175 psig (1200 kPa).

B. Ball Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Affiliated Distributors.

b. Anvil International, Inc.

c. Barnett.

d. Conbraco Industries, Inc.; Apollo Valves.
e. Fire-End & Croker Corporation.

f. Fire Protection Products, Inc.

g. Flowserve.

h. FNW.

i. Jomar International, Ltd.

j. Kennedy Valve; a division of McWane, Inc.

k. Kitz Corporation.

l. Legend Valve.

m. Metso Automation USA Inc.

n. Milwaukee Valve Company.

o. NIBCO INC.

p. Potter Roemer.

q. Red-White Valve Corporation.

r. Southern Manufacturing Group.

s. Stewart, M. A. and Sons Ltd.

t. Tyco Fire & Building Products LP.

u. Victaulic Company.

v. Watts Water Technologies, Inc.

w. <Insert manufacturer's name>.

2.6 SPECIALTY VALVES

A. General Requirements:

1. Standard: UL's "Fire Protection Equipment Directory" listing or "Approval Guide," published by FM Global, listing.

2. Minimum Pressure Rating: 175 psig (1200 kPa).

3. Body Material: Cast or ductile iron.

4. Size: Same as connected piping.

5. End Connections: Flanged or grooved.

Valves in paragraph below are available in NPS 1-1/2 to NPS 8 (DN 40 to DN 200).

B. Dry-Pipe Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first subparagraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. AFAC Inc.
b. Globe Fire Sprinkler Corporation.

c. Reliable Automatic Sprinkler Co., Inc.

d. Tyco Fire & Building Products LP.

e. Venus Fire Protection Ltd.

f. Victaulic Company.

g. Viking Corporation.

h. <Insert manufacturer's name>.

3. Standard: UL 260

4. Design: Differential-pressure type.

5. Include UL 1486, quick-opening devices, trim sets for air supply, drain, priming level, alarm connections, ball drip valves, pressure gages, priming chamber attachment, and fill-line attachment.

6. Air Compressor:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

a. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first subparagraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

b. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1) Gast Manufacturing Inc.

2) General Air Products, Inc,

3) Viking Corporation.

4) <Insert manufacturer's name>.

c. Standard: UL's "Fire Protection Equipment Directory" listing or "Approval Guide," published by FM Global, listing.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Section 210513 "Common Motor Requirements for Fire Suppression Equipment." If different characteristics are required, insert subparagraphs below to suit Project.

d. Motor Horsepower: Fractional.

e. Power: 120-V ac, 60 Hz, single phase.

2.7 SPRINKLER SPECIALTY PIPE FITTINGS

A. General Requirements for Dry-Pipe-System Fittings: [UL listed] <Insert standard> for dry-pipe service.

Fittings in first paragraph below are available in at least NPS 2 to NPS 8 (DN 50 to DN 200) main sizes with NPS 1/2 to NPS 4 (DN 15 to DN 100) outlets or branches.

B. Branch Outlet Fittings:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Anvil International, Inc.

b. National Fittings, Inc.

c. Shurjoint Piping Products.

d. Tyco Fire & Building Products LP.

e. Victaulic Company.

f. <Insert manufacturer's name>.

2. Standard: UL 213.

3. Pressure Rating: 175 psig (1200 kPa) minimum.

4. Body Material: Ductile-iron housing with EPDM seals and bolts and nuts.

5. Type: Mechanical-T and -cross fittings.

6. Configurations: Snap-on and strapless, ductile-iron housing with branch outlets.

7. Size: Of dimension to fit onto sprinkler main and with outlet connections as required to match connected branch piping.

8. Branch Outlets: Grooved, plain-end pipe, or threaded.

Assemblies in first paragraph below are available in NPS 3/4 to NPS 2 (DN 20 to DN 50).

C. Flow Detection and Test Assemblies:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. AGF Manufacturing Inc.

b. Reliable Automatic Sprinkler Co., Inc.

c. Tyco Fire & Building Products LP.

d. Victaulic Company.

e. <Insert manufacturer's name>.

2. Standard: UL's "Fire Protection Equipment Directory" listing or "Approval Guide," published by FM Global, listing.

3. Pressure Rating: 175 psig (1200 kPa) minimum.

4. Body Material: Cast- or ductile-iron housing with orifice, sight glass, and integral test valve.

5. Size: Same as connected piping.

6. Inlet and Outlet: Threaded.

Testers in first paragraph below are available in NPS sizes required for a single sprinkler.

D. Branch Line Testers:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Elkhart Brass Mfg. Company, Inc.

b. Fire-End & Croker Corporation.

c. Potter Roemer.

d. <Insert manufacturer's name>.

2. Standard: UL 199.

3. Pressure Rating: 175 psig (1200 kPa) minimum.

4. Body Material: Brass.

5. Size: Same as connected piping.

6. Inlet: Threaded.

7. Drain Outlet: Threaded and capped.

8. Branch Outlet: Threaded, for sprinkler.

Fittings in first paragraph below are available in NPS 3/4 to NPS 2 (DN 20 to DN 50).

E. Sprinkler Inspector's Test Fittings:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. AGF Manufacturing Inc.

b. Triple R Specialty.

c. Tyco Fire & Building Products LP.

d. Victaulic Company.

e. Viking Corporation.

f. <Insert manufacturer's name>.

2. Standard: UL's "Fire Protection Equipment Directory" listing or "Approval Guide," published by FM Global, listing.

3. Pressure Rating: 175 psig (1200 kPa) minimum.

4. Body Material: Cast- or ductile-iron housing with sight glass.

5. Size: Same as connected piping.

6. Inlet and Outlet: Threaded.

Nipples in first paragraph below are available in NPS sizes required for a single sprinkler.

F. Adjustable Drop Nipples:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. CECA, LLC.

b. Corcoran Piping System Co.

c. Merit Manufacturing; a division of Anvil International, Inc.

d. <Insert manufacturer's name>.

2. Standard: UL 1474.

3. Pressure Rating: 250 psig (1725 kPa) minimum.

4. Body Material: Steel pipe with EPDM O-ring seals.

5. Size: Same as connected piping.

6. Length: Adjustable.

7. Inlet and Outlet: Threaded.

Fittings in paragraph below are available in NPS sizes required for a single sprinkler.

G. Flexible, Sprinkler Hose Fittings:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Fivalco Inc.

b. FlexHead Industries, Inc.

c. Gateway Tubing, Inc.

d. <Insert manufacturer's name>.

2. Standard: UL 1474.

3. Type: Flexible hose for connection to sprinkler, and with bracket for connection to ceiling grid.

4. Pressure Rating: 175 psig (1200 kPa) minimum.

5. Size: Same as connected piping, for sprinkler.

2.8 SPRINKLERS

Coordinate this article with "Sprinkler Schedule" Article.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1. AFAC Inc.

2. Globe Fire Sprinkler Corporation.

3. Reliable Automatic Sprinkler Co., Inc.

4. Tyco Fire & Building Products LP.

5. Venus Fire Protection Ltd.

6. Victaulic Company.

7. Viking Corporation.

8. <Insert manufacturer's name>.

B. General Requirements:

1. Standard: UL's "Fire Protection Equipment Directory" listing or "Approval Guide," published by FM Global, listing.

2. Pressure Rating for Residential Sprinklers: 175 psig (1200 kPa) maximum.

3. Pressure Rating for Automatic Sprinklers: 175 psig (1200 kPa) minimum.

4. Pressure Rating for High-Pressure Automatic Sprinklers: 250 psig (1725 kPa) minimum.

C. Automatic Sprinklers with Heat-Responsive Element:

1. Nonresidential Applications: [UL 199] <Insert standard>.

2. Residential Applications: [UL 1626] <Insert standard>.

3. Characteristics: Nominal 1/2-inch (12.7-mm) orifice with discharge coefficient K of 5.6, and for "Ordinary" temperature classification rating unless otherwise indicated or required by application.

Retain only sprinkler finishes in first paragraph below that are indicated in "Sprinkler Schedule" Article.

D. Sprinkler Finishes:

1. Chrome plated.

2. Bronze.

3. Painted.

Retain only special coatings in first paragraph below that are indicated in "Sprinkler Schedule" Article.

E. Special Coatings:

1. Wax.

2. Lead.

3. Corrosion-resistant paint.

F. Sprinkler Escutcheons: Materials, types, and finishes for the following sprinkler mounting applications. Escutcheons for concealed, flush, and recessed-type sprinklers are specified with sprinklers.

1. Ceiling Mounting: [Chrome-plated steel, one piece, flat] [Chrome-plated steel, two piece, with 1-inch (25-mm) vertical adjustment] [Plastic, white finish, one piece, flat].

2. Sidewall Mounting: [Chrome-plated steel] [Plastic, white finish], one piece, flat.

G. Sprinkler Guards:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Reliable Automatic Sprinkler Co., Inc.

b. Tyco Fire & Building Products LP.

c. Victaulic Company.

d. Viking Corporation.

e. <Insert manufacturer's name>.

2. Standard: UL 199.

3. Type: Wire cage with fastening device for attaching to sprinkler.

2.9 ALARM DEVICES

A. Alarm-device types shall match piping and equipment connections.

Retain remaining paragraphs if devices are specified in this Section, or delete if devices are specified in Section 283111 "Digital, Addressable Fire-Alarm System" or Section 283112 "Zoned (DC Loop) Fire-Alarm System."

B. Water-Motor-Operated Alarm:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Globe Fire Sprinkler Corporation.

b. Tyco Fire & Building Products LP.

c. Victaulic Company.

d. Viking Corporation.

e. <Insert manufacturer's name>.

2. Standard: UL 753.

3. Type: Mechanically operated, with Pelton wheel.

4. Alarm Gong: Cast aluminum with red-enamel factory finish.

5. Size: 10-inch (250-mm) diameter.

6. Components: Shaft length, bearings, and sleeve to suit wall construction.

7. Inlet: NPS 3/4 (DN 20).

8. Outlet: NPS 1 (DN 25) drain connection.

C. Valve Supervisory Switches:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Fire-Lite Alarms; a Honeywell company.

b. Kennedy Valve; a division of McWane, Inc.

c. Potter Electric Signal Company.

d. System Sensor; a Honeywell company.

e. <Insert manufacturer's name>.

2. Standard: UL 346.

3. Type: Electrically supervised.

4. Components: Single-pole, double-throw switch with normally closed contacts.

5. Design: Signals that controlled valve is in other than fully open position.

2.10 PRESSURE GAGES

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1. AMETEK, Inc.; U.S. Gauge Division.

2. Ashcroft, Inc.

3. Brecco Corporation.

4. WIKA Instrument Corporation.

5. <Insert manufacturer's name>.

B. Standard: UL 393.

C. Dial Size: 3-1/2- to 4-1/2-inch (90- to 115-mm) diameter.

D. Pressure Gage Range: [0 to 250 psig (0 to 1725 kPa) minimum] [0 to 300 psig (0 to 2070 kPa)].

E. Water System Piping Gage: Include "WATER" or "AIR/WATER" label on dial face.

F. Air System Piping Gage: Include[ retard feature and] "AIR" or "AIR/WATER" label on dial face.

PART 3 -  EXECUTION

3.1 SERVICE-ENTRANCE PIPING

Retain this article and delete "Water-Supply Connections" Article below if connection to building's water-service piping is required.

A. Connect sprinkler piping to water-service piping for service entrance to building. Comply with requirements in Section 211100 "Facility Fire-Suppression Water-Service Piping" for exterior piping.

Retain one of two paragraphs below. Backflow preventers are recommended and are usually required by authorities having jurisdiction.

B. Install shutoff valve,[ backflow preventer,] pressure gage, drain, and other accessories indicated at connection to water-service piping.[ Comply with requirements in Section 211100 "Facility Fire-Suppression Water-Service Piping" for backflow preventers.]

C. Install shutoff valve, check valve, pressure gage, and drain at connection to water service.

3.2 WATER-SUPPLY CONNECTIONS

Retain this article and delete "Service-Entrance Piping" Article above if connection to building's water-distribution piping is required.

A. Connect sprinkler piping to building's interior water-distribution piping. Comply with requirements in Section 221116 "Domestic Water Piping" for interior piping.

Retain one of two paragraphs below. Backflow preventers are recommended and are usually required by authorities having jurisdiction.

B. Install shutoff valve,[ backflow preventer,] pressure gage, drain, and other accessories indicated at connection to water-distribution piping.[ Comply with requirements in Section 221119 "Domestic Water Piping Specialties" for backflow preventers.]

C. Install shutoff valve, check valve, pressure gage, and drain at connection to water supply.

3.3 PIPING INSTALLATION

A. Locations and Arrangements: Drawing plans, schematics, and diagrams indicate general location and arrangement of piping. Install piping as indicated, as far as practical.

1. Deviations from approved working plans for piping require written approval from authorities having jurisdiction. File written approval with Architect before deviating from approved working plans.

B. Piping Standard: Comply with requirements in NFPA 13 for installation of sprinkler piping.

Retain first paragraph below if piping is required to withstand seismic design loads.

C. Install seismic restraints on piping. Comply with requirements in NFPA 13 for seismic-restraint device materials and installation.

D. Use listed fittings to make changes in direction, branch takeoffs from mains, and reductions in pipe sizes.

E. Install unions adjacent to each valve in pipes NPS 2 (DN 50) and smaller.

F. Install flanges, flange adapters, or couplings for grooved-end piping on valves, apparatus, and equipment having NPS 2-1/2 (DN 65) and larger end connections.

G. Install "Inspector's Test Connections" in sprinkler system piping, complete with shutoff valve, and sized and located according to NFPA 13.

H. Install sprinkler piping with drains for complete system drainage.

I. Install sprinkler control valves, test assemblies, and drain risers adjacent to standpipes when sprinkler piping is connected to standpipes.

J. Install automatic (ball drip) drain valves to drain piping between fire-department connections and check valves. Drain to floor drain or to outside building.

K. Install alarm devices in piping systems.

See Editing Instruction No. 3 in the Evaluations for cautions about pipe hangers.

L. Install hangers and supports for sprinkler system piping according to NFPA 13. Comply with requirements in NFPA 13 for hanger materials.

M. Install pressure gages on riser or feed main, at each sprinkler test connection, and at top of each standpipe. Include pressure gages with connection not less than NPS 1/4 (DN 8) and with soft metal seated globe valve, arranged for draining pipe between gage and valve. Install gages to permit removal, and install where they will not be subject to freezing.

N. Drain dry-pipe sprinkler piping.

O. Pressurize and check dry-pipe sprinkler system piping and [air-pressure maintenance devices] [air compressors].

P. Install sleeves for piping penetrations of walls, ceilings, and floors. Comply with requirements for sleeves specified in Section 210517 "Sleeves and Sleeve Seals for Fire-Suppression Piping."

Retain first paragraph below for piping that penetrates an exterior concrete wall or concrete slab.

Q. Install sleeve seals for piping penetrations of concrete walls and slabs. Comply with requirements for sleeve seals specified in Section 210517 "Sleeves and Sleeve Seals for Fire-Suppression Piping."

R. Install escutcheons for piping penetrations of walls, ceilings, and floors. Comply with requirements for escutcheons specified in Section 210518 "Escutcheons for Fire-Suppression Piping."

3.4 JOINT CONSTRUCTION

A. Install couplings, flanges, flanged fittings, unions, nipples, and transition and special fittings that have finish and pressure ratings same as or higher than system's pressure rating for aboveground applications unless otherwise indicated.

B. Install unions adjacent to each valve in pipes NPS 2 (DN 50) and smaller.

C. Install flanges, flange adapters, or couplings for grooved-end piping on valves, apparatus, and equipment having NPS 2-1/2 (DN 65) and larger end connections.

D. Ream ends of pipes and tubes and remove burrs. Bevel plain ends of steel pipe.

E. Remove scale, slag, dirt, and debris from inside and outside of pipes, tubes, and fittings before assembly.

F. Flanged Joints: Select appropriate gasket material in size, type, and thickness suitable for water service. Join flanges with gasket and bolts according to ASME B31.9.

G. Threaded Joints: Thread pipe with tapered pipe threads according to ASME B1.20.1. Cut threads full and clean using sharp dies. Ream threaded pipe ends to remove burrs and restore full ID. Join pipe fittings and valves as follows:

1. Apply appropriate tape or thread compound to external pipe threads.

2. Damaged Threads: Do not use pipe or pipe fittings with threads that are corroded or damaged.

H. Twist-Locked Joints: Insert plain end of steel pipe into plain-end-pipe fitting. Rotate retainer lugs one-quarter turn or tighten retainer pin.

I. Steel-Piping, Cut-Grooved Joints: Cut square-edge groove in end of pipe according to AWWA C606. Assemble coupling with housing, gasket, lubricant, and bolts. Join steel pipe and grooved-end fittings according to AWWA C606 for steel-pipe joints.

J. Dissimilar-Material Piping Joints: Make joints using adapters compatible with materials of both piping systems.

3.5 VALVE AND SPECIALTIES INSTALLATION

A. Install listed fire-protection valves, trim and drain valves, specialty valves and trim, controls, and specialties according to NFPA 13 and authorities having jurisdiction.

B. Install listed fire-protection shutoff valves supervised open, located to control sources of water supply except from fire-department connections. Install permanent identification signs indicating portion of system controlled by each valve.

C. Install check valve in each water-supply connection. Install backflow preventers instead of check valves in potable-water-supply sources.

D. Specialty Valves:

1. General Requirements: Install in vertical position for proper direction of flow, in main supply to system.

2. Dry-Pipe Valves: Install trim sets for air supply, drain, priming level, alarm connections, ball drip valves, pressure gages, priming chamber attachment, and fill-line attachment.

a. Install air compressor and compressed-air supply piping.

3.6 SPRINKLER INSTALLATION

Coordinate this article with Drawings.

A. Install sprinklers in suspended ceilings in center of[ narrow dimension of] acoustical ceiling panels.

B. Install dry-type sprinklers with water supply from heated space. Do not install pendent or sidewall, wet-type sprinklers in areas subject to freezing.

C. Install sprinklers into flexible, sprinkler hose fittings and install hose into bracket on ceiling grid.

3.7 IDENTIFICATION

A. Install labeling and pipe markers on equipment and piping according to requirements in NFPA 13.

B. Identify system components, wiring, cabling, and terminals. Comply with requirements for identification specified in Section 260553 "Identification for Electrical Systems."

3.8 FIELD QUALITY CONTROL

Retain first paragraph below to require Contractor to perform tests and inspections.

A. Perform tests and inspections.

Retain first paragraph below to describe tests and inspections to be performed.

B. Tests and Inspections:

1. Leak Test: After installation, charge systems and test for leaks. Repair leaks and retest until no leaks exist.

2. Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.

3. Flush, test, and inspect sprinkler systems according to NFPA 13, "Systems Acceptance" Chapter.

4. Energize circuits to electrical equipment and devices.

5. Start and run air compressors.

6. Coordinate with fire-alarm tests. Operate as required.

7. Coordinate with fire-pump tests. Operate as required.

8. Verify that equipment hose threads are same as local fire-department equipment.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

C. Sprinkler piping system will be considered defective if it does not pass tests and inspections.

D. Prepare test and inspection reports.

3.9 CLEANING

A. Clean dirt and debris from sprinklers.

B. Remove and replace sprinklers with paint other than factory finish.

3.10 PIPING SCHEDULE

See Editing Instruction No. 2 in the Evaluations for available materials.

Retain piping applications in this article. Coordinate with materials specified in Part 2.

A. Piping between Fire-Department Connections and Check Valves: Galvanized, standard-weight steel pipe with [threaded ends; cast-iron threaded fittings; and threaded] [grooved ends; grooved-end fittings; grooved-end-pipe couplings; and grooved] joints.

B. Sprinkler specialty fittings may be used, downstream of control valves, instead of specified fittings.

Retain "one of" option in first paragraph below to allow Contractor to select piping materials from those retained.

C. Dry-pipe sprinkler system, [NPS 2 (DN 50) and smaller] <Insert pipe size range>, shall be[ one of] the following:

Retain one or more of three subparagraphs below. If using more than one type of material and joining method, identify various materials on Drawings and show points of transition from one material to another.

1. [Standard-weight] [or] [Schedule 30], galvanized-steel pipe with threaded ends; galvanized, gray-iron threaded fittings; and threaded joints.

2. [Standard-weight] [Schedule 30] [or] [thinwall], galvanized-steel pipe with plain ends; plain-end-pipe fittings; and twist-locked joints.

3. [Standard-weight] [or] [Schedule 30], galvanized-steel pipe with cut-grooved ends; galvanized, grooved-end fittings for steel piping; grooved-end-pipe couplings for steel piping; and grooved joints.

Retain "one of" option in paragraph below to allow Contractor to select piping materials from those retained.

D. Dry-pipe sprinkler system, [NPS 2-1/2 to NPS 6 (DN 65 to DN 150)] <Insert pipe size range>, shall be[ one of] the following:

Retain one or both subparagraphs below. If using more than one type of material and joining method, identify various materials on Drawings and show points of transition from one material to another.

1. [Standard-weight] [or] [Schedule 30], galvanized-steel pipe with threaded ends; galvanized, gray-iron threaded fittings; and threaded joints.

2. [Standard-weight] [or] [Schedule 30], galvanized-steel pipe with cut-grooved ends; galvanized, grooved-end fittings for steel piping; grooved-end-pipe couplings for steel piping; and grooved joints.

3.11 SPRINKLER SCHEDULE

Retain this article to require selected products to be used in indicated applications; delete to allow Contractor to choose among various products acceptable to authorities having jurisdiction or if delegating sprinkler system design to Contractor. According to NFPA 13, Drawings shall indicate sprinkler make, type, model, and nominal k-factor including sprinkler identification number.

A. Use sprinkler types in subparagraphs below for the following applications:

1. Rooms without Ceilings: [Upright sprinklers] <Insert type>.

2. Rooms with Suspended Ceilings: [Dry pendent sprinklers] [Dry recessed sprinklers] [Dry flush sprinklers] [Dry concealed sprinklers] [Dry pendent, recessed, flush, and concealed sprinklers, as indicated].

3. Wall Mounting: Dry sidewall sprinklers.

4. Spaces Subject to Freezing: [Upright sprinklers] [Dry pendent sprinklers] [Dry sidewall sprinklers] [Upright, dry pendent sprinklers; and dry sidewall sprinklers as indicated] <Insert type>.

5. Special Applications: [Extended-coverage and quick-response sprinklers where indicated] <Insert type>.

B. Provide sprinkler types in subparagraphs below with finishes indicated.

1. Concealed Sprinklers: Rough brass, with factory-painted white cover plate.

2. Flush Sprinklers: Bright chrome, with painted white escutcheon.

3. Recessed Sprinklers: Bright chrome, with bright chrome escutcheon.

4. [Upright,] [Pendent,] [and] [Sidewall] Sprinklers: Chrome plated in finished spaces exposed to view; rough bronze in unfinished spaces not exposed to view; wax coated where exposed to acids, chemicals, or other corrosive fumes.

END OF SECTION 211316

	DRY-PIPE SPRINKLER SYSTEMS
	211316 - 1



