Copyright 2010 AIA
MasterSpec Professional
02/10

Copyright 2010 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 213400 - PRESSURE-MAINTENANCE PUMPS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Regenerative-turbine, pressure-maintenance pumps.

2. Vertical-turbine, pressure-maintenance pumps.

B. Related Section:

Retain Section in subparagraph below that contains requirements Contractor might expect to find in this Section but are specified in another Section.

1. Section 213900 "Controllers for Fire-Pump Drivers" for pressure-maintenance-pump controllers.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product indicated. Include rated capacities, operating characteristics, performance curves, electrical characteristics, and furnished specialties and accessories.

B. Shop Drawings: For pumps, accessories, and specialties. Include plans, elevations, sections, details, and attachments to other work.

1. Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

2. Wiring Diagrams: For power, signal, and control wiring.

1.3 INFORMATIONAL SUBMITTALS

A. Field quality-control reports.

1.4 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

1.5 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

1.6 COORDINATION

A. Coordinate sizes and locations of concrete bases with actual equipment provided.

PART 2 -  PRODUCTS

2.1 REGENERATIVE-TURBINE, PRESSURE-MAINTENANCE PUMPS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. A-C Fire Pump Systems; a business of ITT Industries.

2. Crane Pumps and Systems; a Crane Co. company.

3. MTH Pumps/MTH Tool Company, Inc.

4. PACO Pumps; Grundfos Pumps Corporation U.S.A.

5. Pentair Pump Group; Aurora Pump.

6. <Insert manufacturer's name>.

C. Description: Factory-assembled and -tested, close-coupled, single-stage, regenerative-turbine centrifugal pump as defined in HI 1.1-1.2 and HI 1.3; with pump and motor mounted horizontally.

D. Pump Construction:

1. Casing: Radially split, cast iron, with threaded inlet and outlet.

2. Impeller: Bronze, balanced, and keyed to shaft.

3. Pump Shaft: Stainless steel[ or steel] with deflector.

4. Shaft Sleeve: Bronze.

5. Seal: Mechanical type with spring-loaded rotating head.

E. Motor: Single speed with permanently lubricated ball bearings. Comply with requirements in Section 210513 "Common Motor Requirements for Fire Suppression Equipment."

1. Power Cord: Factory-connected to motor for field connection to controller and at least [10 feet (3 m)] <Insert dimension> long.

F. Nameplate: Permanently attached to pump and indicating capacity and characteristics.

If Project has more than one type or configuration of regenerative-turbine, pressure-maintenance pump, delete paragraph below and schedule pressure-maintenance pumps on Drawings.

G. Capacities and Characteristics:

1. Rated Capacity: <Insert gpm (L/minute)>.

2. Total Dynamic Head: <Insert feet (kPa)>.

3. Working Pressure: [175 psig (1200 kPa)] [300 psig (2070 kPa)] <Insert value>.

4. Inlet Size: Threaded; <Insert NPS (DN)>.

5. Outlet Size: Threaded; <Insert NPS (DN)>.

6. Suction Head Available at Pump: <Insert feet (m)>.

7. Motor Horsepower: <Insert value>.

8. Motor Speed: <Insert rpm>.

9. Electrical Characteristics:

a. Volts: [120] [240] <Insert value>.

b. Phases: [Single] [Three].

c. Hertz: [60] <Insert value>.

d. Full-Load Amperes: <Insert value>.

e. Minimum Circuit Ampacity: <Insert value>.

f. Maximum Overcurrent Protection: <Insert amperage>.

10. Pump-Start, Pressure-Switch Setting: <Insert psig (kPa)>.

11. Pump-Stop, Pressure-Switch Setting: <Insert psig (kPa)>.

2.2 VERTICAL-TURBINE, PRESSURE-MAINTENANCE PUMPS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. A-C Fire Pump Systems; a business of ITT Industries.

2. Patterson Pump Company; a subsidiary of the Gorman-Rupp Company.

3. Peerless Pump, Inc.

4. Pentair Pump Group; Aurora Pump.

5. Pentair Pump Group; Fairbanks Morse.

6. Reddy-Buffaloes Pump Company.

7. Ruhrpumpen, Inc.

8. S.A. Armstrong Limited.

9. Sulzer Pumps Ltd.

10. Weir Floway; a company of Weir Clear Liquid.

11. <Insert manufacturer's name>.

C. Description: Factory-assembled and -tested, vertical, multistage, open-line-shaft turbine pump as defined in HI 2.1-2.2 and HI 2.3; with pump motor mounted above pump head.

D. Pump Construction:

1. Pump Head: Cast iron, for surface discharge, with flange, except connections may be threaded in sizes in which flanges are not available.

2. Pump Head Seal: Stuffing box and stuffing.

Retain first two subparagraphs below for static water levels of 50 feet (15 m) or less and for water-lubricated bearings.

3. Line Shaft: Stainless steel or steel, with corrosion-resistant shaft sleeves.

4. Line Shaft Bearings: Rubber sleeve, water lubricated.

Retain first two subparagraphs below for static water levels between 50 and 200 feet (15 and 61 m) and for oil-lubricated bearings.

5. Line Shaft: Steel.

6. Line Shaft Bearings: Corrosion resistant, oil lubricated.

7. Impeller Shaft: Monel metal or stainless steel.

8. Bowl Section: Multiple cast-iron bowls with closed-type bronze or stainless-steel impellers.

9. Column Pipe: ASTM A 53/A 53M, Schedule 40, galvanized-steel pipe with threaded ends and cast-iron or steel fittings, in sections 10 feet (3 m) or less, with strainer of cast or fabricated bronze or stainless steel at bottom.

E. Motor: Single speed with permanently lubricated ball bearings. Comply with requirements in Section 210513 "Common Motor Requirements for Fire Suppression Equipment."

1. Power Cord: Factory-connected to motor for field connection to controller and at least [10 feet (3 m)] <Insert dimension> long.

F. Base: Cast iron or steel with hole for electrical cable.

G. Nameplate: Permanently attached to pump and indicating capacity and characteristics.

If Project has more than one type or configuration of vertical-turbine, pressure-maintenance pump, delete paragraph below and schedule pressure-maintenance pumps on Drawings.

H. Capacities and Characteristics:

1. Rated Capacity: <Insert gpm (L/minute)>.

2. Total Dynamic Head: <Insert feet (kPa)>.

3. Working Pressure: <Insert psig (kPa)>.

4. Inlet Column Size: <Insert NPS (DN)>.

5. Pump Column Length: <Insert feet (m)>.

6. Outlet Size: <Insert NPS (DN)>.

7. Flange: [Class 125] <Insert class>.

8. Suction Head Available at Pump: <Insert feet (m)>.

9. Motor Horsepower: <Insert value>.

10. Motor Speed: <Insert rpm>.

11. Electrical Characteristics:

a. Volts: [120] [240] <Insert value>.

b. Phases: [Single] [Three].

c. Hertz: [60] <Insert value>.

d. Full-Load Amperes: <Insert value>.

e. Minimum Circuit Ampacity: <Insert value>.

f. Maximum Overcurrent Protection: <Insert amperage>.

12. Pump-Start, Pressure-Switch Setting: <Insert psig (kPa)>.

13. Pump-Stop, Pressure-Switch Setting: <Insert psig (kPa)>.

2.3 MOTORS

Default motor characteristics are specified in Section 210513 "Common Motor Requirements for Fire Suppression Equipment."

A. Comply with NEMA designation, temperature rating, service factor, enclosure type, and efficiency requirements for motors specified in Section 210513 "Common Motor Requirements for Fire Suppression Equipment."

1. Motor Sizes: Minimum size as indicated; if not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

PART 3 -  EXECUTION

3.1 EQUIPMENT INSTALLATION

A. NFPA Standard: Comply with NFPA 20 for installation of pressure-maintenance pumps.

B. Base-Mounted Pump Mounting: Install pumps on concrete bases. Comply with requirements for concrete bases specified in [Section 033000 "Cast-in-Place Concrete."] [Section 033053 "Miscellaneous Cast-in-Place Concrete."]

1. Install dowel rods to connect concrete base to concrete floor. Unless otherwise indicated, install dowel rods on 18-inch (450-mm) centers around the full perimeter of concrete base.

2. For supported equipment, install epoxy-coated anchor bolts that extend through concrete base and anchor into structural concrete floor.

3. Place and secure anchorage devices. Use setting drawings, templates, diagrams, instructions, and directions furnished with items to be embedded.

4. Install anchor bolts to elevations required for proper attachment to supported equipment.

5. Attach pumps to equipment base using anchor bolts.

C. Install regenerative-turbine, pressure-maintenance pumps according to HI 1.4.

D. Install vertical-turbine, pressure-maintenance pumps according to HI 2.4.

3.2 FIELD QUALITY CONTROL

Retain first paragraph below to require a factory-authorized service representative to perform inspections, tests, and adjustments.

A. Manufacturer's Field Service: Engage a factory-authorized service representative to inspect, test, and adjust components, assemblies, and equipment installations, including connections.

Retain first paragraph below to require Contractor to perform tests and inspections.

B. Perform tests and inspections.

Retain subparagraph below to require a factory-authorized service representative to assist Contractor with inspections, tests, and adjustments.

1. Manufacturer's Field Service: Engage a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

Retain first paragraph below to describe tests and inspections to be performed.

C. Tests and Inspections:

1. Operational Test: After electrical circuitry has been energized, start units to confirm proper motor rotation and unit operation.

2. Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

D. Pressure-maintenance pumps will be considered defective if they do not pass tests and inspections.

E. Prepare test and inspection reports.

3.3 ADJUSTING

A. Lubricate pumps as recommended by manufacturer.

B. Set field-adjustable pressure-switch ranges as indicated.

END OF SECTION 213400

	PRESSURE-MAINTENANCE PUMPS
	213400 - 1



