Copyright 2012 AIA
MasterSpec Professional
03/12

Copyright 2012 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 213900 - CONTROLLERS FOR FIRE-PUMP DRIVERS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Full-service, [full] [reduced]-voltage controllers rated 600 V and less.

2. Limited-service controllers rated 600 V and less.

3. Controllers for diesel-drive fire pumps.

4. Controllers for pressure-maintenance pumps.

5. Remote alarm panels.

1.2 DEFINITIONS

Retain definition(s) remaining after this Section has been edited.

A. ATS: Automatic transfer switch(es).

B. ECM: Electronic control module.

C. MCCB: Molded-case circuit breaker.

1.3 PERFORMANCE REQUIREMENTS

Retain paragraph below with "Seismic Qualification Certificates" Paragraph in "Informational Submittals" Article for projects requiring seismic design. Model building codes and ASCE/SEI 7 establish criteria for buildings subject to earthquake motions. Verify requirements of authorities having jurisdiction.

A. Seismic Performance: Fire-pump controllers and alarm panels shall withstand the effects of earthquake motions determined according to [ASCE/SEI 7] <Insert requirement>.

Retain subparagraph below to define the term "withstand" as it applies to this Project. Definition varies with type of building and occupancy and is critical to valid certification. Option is used for essential facilities where equipment must operate immediately after an earthquake.

1. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified[ and the unit will be fully operational after the seismic event]."

1.4 ACTION SUBMITTALS

A. Product Data: For each type of product indicated.

B. Shop Drawings: For each type of product indicated. Include dimensioned plans, elevations, sections, details, and attachments to other work, including required clearances and service spaces around controller enclosures.

1. Detail equipment assemblies and indicate dimensions, weights, loads, method of field assembly, components, and location and size of each field connection.

2. Schematic and Connection Diagrams: For power, signal, alarm, and control wiring and for pressure-sensing tubing.

1.5 INFORMATIONAL SUBMITTALS

Coordinate first paragraph below with qualification requirements in Section 014000 "Quality Requirements" and as supplemented in "Quality Assurance" Article.

A. Qualification Data: For qualified testing agency.

Retain first paragraph below if required by seismic criteria applicable to Project. See ASCE/SEI 7 for certification requirements for equipment and components.

B. Seismic Qualification Certificates: For each type of product indicated, from manufacturer.

NFPA 20 requires that "all controllers shall be completely assembled, wired, and tested by the manufacturer before shipment from the factory." Retain first paragraph below for requesting copies of the test reports.

C. Manufacturer's factory test reports of fully assembled and tested equipment.

D. Source quality-control reports.

E. Field quality-control reports.

1.6 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

1.7 QUALITY ASSURANCE

A. Source Limitations: Obtain fire-pump controllers and all associated equipment from single source or producer.

B. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

C. Comply with standards of authorities having jurisdiction pertaining to materials and installation.

D. Comply with NFPA 20 and NFPA 70.

Retain paragraph below for projects in seismic areas. If retaining, also retain "Seismic Qualification Certificates" Paragraph in "Informational Submittals" Article. Coordinate with Section 260548.16 "Seismic Controls for Electrical Systems."

E. IEEE Compliance: Fabricate and test enclosed controllers according to IEEE 344 to withstand seismic forces defined in Section 260548.16 "Seismic Controls for Electrical Systems."

PART 2 -  PRODUCTS

2.1 FULL-SERVICE CONTROLLERS

Show voltage, size, type, accessories, and enclosure type for each controller on Drawings if not included in the Section Text. See "Specifying Fire-Pump Controllers" Article in the Evaluations for selection considerations.

Standard features vary considerably among manufacturers of full-service, electric-motor-driver, fire-pump controllers; not all features in this article are available for every type and from every listed manufacturer. Features vary according to motor characteristics and the driven-equipment operating criteria. Verify availability and unique characteristics with manufacturers; indicate in the Section Text or show on Drawings those features that apply to each controller. See Editing Instruction No. 2 and "Peculiar Characteristics of Controllers for Electric-Drive Fire Pumps" Article in the Evaluations for additional guidance.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings. If retaining paragraph, ensure that all other related articles retained in the Section Text also include "Basis-of-Design Product" Paragraph and that selected products are from the same manufacturer.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Aquarius Fluid Products, Inc.

2. ASCO Power Technologies, LP; Firetrol Products.

3. Eaton Electrical Inc.; Cutler-Hammer Business Unit.

4. Hubbell Incorporated; Hubbell Industrial Controls.

5. Joslyn Clark Corporation.

6. Master Control Systems, Inc.

7. Metron, Inc.

8. Tornatech.

9. <Insert manufacturer's name>.

See "General Requirements for Fire-Pump Controllers" Article in the Evaluations for restrictions on using nonautomatic controllers.

Some authorities having jurisdiction or the Owner's insurance underwriter may require specific local approvals (e.g., the New York Department of Buildings) or an FM Approvals certification and mark. Insert additional or replacement standards or approvals in first paragraph below.

C. General Requirements for Full-Service Controllers:

1. Comply with NFPA 20 and [UL 218] <Insert standard>.

2. Listed by an NRTL for electric-motor driver for fire-pump service.

3. [Combined automatic and nonautomatic] [Nonautomatic] operation.

4. Factory assembled, wired, and tested; continuous-duty rated.

Retain subparagraph below for controllers used as means of disconnect and overcurrent protection for the service entrance, outside feeder, or separately derived source.

5. Service Equipment Label: NRTL labeled for use as service equipment.

D. Method of Starting:

Retain first subparagraph below for controllers with automatic operation. Retain first option for controllers actuated by water flow in fire-suppression piping; retain second option for other starting means (e.g., fire-protection equipment, sequential starting), and provide details of starting method here or on Drawings.

1. [Pressure] [Nonpressure]-switch actuated.

Retain first two subparagraphs below for automatic operation and pressure-switch actuation.

a. Water-pressure-actuated switch and pressure transducer with independent high- and low-calibrated adjustments responsive to water pressure in fire-suppression piping.

b. System pressure recorder, electric ac driven, with spring backup.

Retain first two subparagraphs below for automatic operation.

c. Programmable minimum-run-time relay to prevent short cycling.

d. Programmable timer for weekly tests.

Retain one of first two subparagraphs below. First option in first subparagraph is full-voltage starting; remaining options are reduced-voltage starting. See "Full-Voltage Controllers" and "Reduced-Voltage Controllers" articles in the Evaluations for additional guidance.

2. Magnetic Controller: [Across-the-line] [Autotransformer] [Part-winding] [Primary-resistor] [Wye-delta (open transition)] [Wye-delta (closed transition)] <Insert type> type.

3. Solid-State Controller: [Reduced-voltage] <Insert type> type.

4. Emergency Start: Mechanically operated start handle that closes and retains the motor RUN contactor independent of all electric or pressure actuators.

NFPA 20 restricts use of automatic shutdown. Retain first option in first paragraph below if allowed and required to suit Project. See ""General Requirements for Fire-Pump Controllers" Article in the Evaluations if retaining first option.

E. Method of Stopping: [Automatic and nonautomatic shutdown after automatic starting] [Nonautomatic].

Show controller short-circuit current (withstand) rating (or available short-circuit currents) on Drawings. Consider conductor size and distance from substation or supply transformers when calculating short-circuit currents at controllers.

F. Capacity: Rated for fire-pump-driver horsepower and short-circuit-current (withstand) rating equal to or greater than short-circuit current available at controller location.

Functions in first two paragraphs below are the minimum required by NFPA 20; however, standard features and optional modifications vary considerably among manufacturers of fire-pump controllers; they must be closely coordinated with "General Requirements for Full-Service Controllers," "Method of Starting," and "Method of Stopping" paragraphs in this article. Verify availability and unique characteristics with manufacturers; include in first two paragraphs below or show on Drawings those features that apply to the controllers.

G. Method of Isolation and Overcurrent Protection: Interlocked isolating switch and nonthermal MCCB; with a common, externally mounted operating handle, and providing locked-rotor protection.

H. Door-Mounted Operator Interface and Controls:

1. Monitor, display, and control the devices, alarms, functions, and operations listed in NFPA 20 as required for drivers and controller types used.

2. Method of Control and Indication:

a. [Microprocessor-based logic] <Insert logic type> controller, with multiline digital readout.

b. [Membrane] <Insert keypad type> keypad.

c. [LED] <Insert lamp type> alarm and status indicating lights.

3. Local[ and Remote] Alarm and Status Indications:

Manufacturers offer numerous alarm and status indications and interfaces. Consult manufacturers for availability and types.

a. Controller power on.

b. Motor running condition.

c. Loss-of-line power.

d. Line-power phase reversal.

e. Line-power single-phase condition.

f. <Insert indication>.

4. Audible alarm, with silence push button.

5. Nonautomatic START and STOP push buttons or switches.

6. <Insert function>.

Retain paragraph below if an ATS ahead of the fire-pump controller is required and the ATS is integral with the controller. See Editing Instruction No. 4 and "Automatic Transfer Switches" Article in the Evaluations for additional guidance.

I. ATS:

1. Complies with NFPA 20, [UL 218] <Insert standard>, and [UL 1008] <Insert standard>.

2. Integral with controller as a listed combination fire-pump controller and power transfer switch.

3. Automatically transfers fire-pump controller from normal power supply to alternate power supply in event of power failure.

4. Allows manual transfer from one source to the other.

Retain one of first two subparagraphs below. Retain first subparagraph if the alternate source is a standby generator with a capacity of less than 225 percent of the motor's full-load current rating. Coordinate with upstream external overcurrent protection.

5. Alternate-Source Isolating and Disconnecting Means: Integral molded-case switch, with an externally mounted operating handle.

NFPA 20 has separate, more stringent, requirements for an integral ATS if the alternate source is a second utility service, an upstream ATS, or an emergency generator with a capacity exceeding 225 percent of the fire-pump motor's full-load current rating. Retain first subparagraph below if any of these situations apply.

6. Alternate-Source Isolating and Disconnecting Means: Mechanically interlocked isolation switch and circuit breaker rated at a minimum of 115 percent of rated motor full-load current, with an externally mounted operating handle; circuit breaker shall be provided with nonthermal sensing, instantaneous-only short-circuit overcurrent protection to comply with available fault currents.

7. Local[ and Remote] Alarm and Status Indications:

Manufacturers offer additional local and remote alarm and status indications and interfaces. Consult manufacturers for availability and types.

a. Normal source available.

b. Alternate source available.

c. In normal position.

d. In alternate position.

e. Isolating means open.

f. <Insert indication>.

8. Audible alarm, with silence push button.

9. Nonautomatic (manual, nonelectric) means of transfer.

Retain first three subparagraphs below if alternate power is from a standby generator.

10. Engine test push button.

11. Start generator output contacts.

12. Timer for weekly generator tests.

13. <Insert function>.

2.2 LIMITED-SERVICE CONTROLLERS

Show voltage, size, type, accessories, and enclosure type for each controller on Drawings if not included in the Section Text. See "Specifying Fire-Pump Controllers" Article in the Evaluations for selection considerations.

Standard features vary considerably among manufacturers of limited-service, electric-motor-driver, fire-pump controllers; not all features in this article are available for every type and from every listed manufacturer. Features depend on motor characteristics and driven-equipment operating criteria. Verify availability and unique characteristics with manufacturers; include in the Section Text or show on Drawings those features that apply to each controller. See Editing Instruction No. 2 and "Peculiar Characteristics of Controllers for Electric-Drive Fire Pumps" and "Limited-Service Controllers" articles in the Evaluations for additional guidance.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings. If retaining paragraph, ensure that all other related articles retained in the Section Text also include "Basis-of-Design Product" Paragraph and that selected products are from the same manufacturer.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Aquarius Fluid Products, Inc.

2. ASCO Power Technologies, LP; Firetrol Products.

3. Eaton Electrical Inc.; Cutler-Hammer Business Unit.

4. Hubbell Incorporated; Hubbell Industrial Controls.

5. Joslyn Clark Corporation.

6. Master Control Systems, Inc.

7. Metron, Inc.

8. Tornatech.

9. <Insert manufacturer's name>.

See "General Requirements for Fire-Pump Controllers" Article in the Evaluations for restrictions on using nonautomatic controllers.

Some authorities having jurisdiction or the Owner's insurance underwriter may require specific local approvals (e.g., the New York Department of Buildings) or an FM Approvals certification and mark. Insert additional or replacement standards or approvals in first paragraph below.

C. General Requirements for Limited-Service Controllers:

1. Comply with NFPA 20 and [UL 218] <Insert standard>.

2. Listed by an NRTL for electric-motor driver for fire-pump service.

3. [Combined automatic and nonautomatic] [Nonautomatic] operation.

4. Factory assembled, wired, and tested; continuous-duty rated.

Retain subparagraph below for controllers used as means of disconnect and overcurrent protection for the service entrance, outside feeder, or separately derived source.

5. Service Equipment Label: NRTL labeled for use as service equipment.

D. Method of Starting:

Retain first subparagraph below for controllers with automatic operation. Retain first option for controllers actuated by water flow in fire-suppression piping; retain second option for other starting means (e.g., fire-protection equipment, sequential starting), and provide details of starting method here or on Drawings.

1. [Pressure] [Nonpressure]-switch actuated.

Retain first two subparagraphs below for automatic operation and pressure-switch actuation.

a. Water-pressure-actuated switch and pressure transducer with independent high- and low-calibrated adjustments responsive to water pressure in fire-suppression piping.

b. System pressure recorder, electric ac driven, with spring backup.

Retain first two subparagraphs below for automatic operation.

c. Programmable minimum-run-time relay to prevent short cycling.

d. Programmable timer for weekly tests.

Full-voltage, across-the-line starting is the only starting method allowed by NFPA 20 for limited-service controllers.

2. Across-the-line magnetic controller.

3. Emergency Start: Mechanically operated start handle that closes and retains the motor RUN contactor independent of all electric or pressure actuators.

NFPA 20 restricts use of automatic shutdown. Retain first option in first paragraph below if allowed and required to suit Project. See "General Requirements for Fire-Pump Controllers" Article in the Evaluations if retaining first option.

E. Method of Stopping: [Automatic and nonautomatic shutdown after automatic starting] [Nonautomatic].

Show controller short-circuit current (withstand) rating (or available short-circuit currents) on Drawings. Consider conductor size and distance from substation or supply transformers when calculating short-circuit currents at controllers.

F. Capacity: Rated for fire-pump-driver horsepower and short-circuit-current (withstand) rating equal to or greater than short-circuit current available at controller location.

Functions in first two paragraphs below are the minimum required by NFPA 20; however, standard features and optional modifications vary considerably among manufacturers of fire-pump controllers; they must be closely coordinated with "General Requirements for Limited-Service Controllers," "Method of Starting," and "Method of Stopping" paragraphs in this article. Verify availability and unique characteristics with manufacturers; include in first two paragraphs below or show on Drawings those features that apply to the controllers.

G. Method of Isolation and Overcurrent Protection: Inverse-time, nonadjustable MCCB, with an externally mounted operating handle.

H. Door-Mounted Operator Interface and Controls:

1. Monitor, display, and control the devices, alarms, functions, and operations listed in NFPA 20 as required for drivers and controller types used.

2. Method of Control and Indication:

a. [Microprocessor-based logic] <Insert logic type> controller, with multiline [LCD] <Insert display type> digital readout.

b. [Membrane] <Insert keypad type> keypad.

c. [LED] <Insert lamp type> alarm and status indicating lights.

3. Local[ and Remote] Alarm and Status Indications:

Manufacturers offer numerous alarm and status indications and interfaces. Consult manufacturers for availability and types.

a. Controller power on.

b. Motor running condition.

c. Loss-of-line power.

d. Line-power phase reversal.

e. Line-power single-phase condition.

f. <Insert indication>.

4. Audible alarm, with silence push button.

5. Nonautomatic START and STOP push buttons.

6. <Insert function>.

Retain paragraph below if an ATS ahead of the fire-pump controller is required and the ATS is integral with the controller. See Editing Instruction No. 4 and "Automatic Transfer Switches" Article in the Evaluations for additional guidance.

I. ATS:

1. Complies with NFPA 20, [UL 218] <Insert standard>, and [UL 1008] <Insert standard>.

2. Integral with controller as a listed combination fire-pump controller and power transfer switch.

3. Automatically transfers fire-pump controller from normal power supply to alternate power supply in event of power failure.

4. Allows manual transfer from one source to the other.

Retain one of first two subparagraphs below. Retain first subparagraph if the alternate source is a standby generator with a capacity of less than 225 percent of the motor's full-load current rating. Coordinate with upstream external overcurrent protection.

5. Alternate-Source Isolating and Disconnecting Means: Integral molded-case switch, with an externally mounted operating handle.

NFPA 20 has separate, more stringent, requirements for an integral ATS if the alternate source is a second utility service, an upstream ATS, or an emergency generator with a capacity exceeding 225 percent of the fire-pump motor's full-load current rating. Retain first subparagraph below if any of these situations apply.

6. Alternate-Source Isolating and Disconnecting Means: Mechanically interlocked isolation switch and circuit breaker rated at a minimum of 115 percent of rated motor full-load current, with an externally mounted operating handle; circuit breaker shall be provided with nonthermal sensing, instantaneous-only short-circuit overcurrent protection to comply with available fault currents.

7. Local[ and Remote] Alarm and Status Indications:

Manufacturers offer additional local and remote alarm and status indications and interfaces. Consult manufacturers for availability and types.

a. Normal source available.

b. Alternate source available.

c. In normal position.

d. In alternate position.

e. Isolating means open.

f. <Insert indication>.

8. Audible alarm, with silence push button.

9. Nonautomatic (manual, nonelectric) means of transfer.

Retain one of first three subparagraphs below if alternate power is from a standby generator.

10. Engine test push button.

11. Start generator output contacts.

12. Timer for weekly generator tests.

13. <Insert function>.

2.3 CONTROLLERS FOR DIESEL-DRIVE FIRE PUMPS

Show voltage, size, type, accessories, and enclosure type for each controller on Drawings if not included in the Section Text. See "Specifying Fire-Pump Controllers" Article in the Evaluations for selection considerations.

Standard features vary considerably among manufacturers of diesel-engine-driver, fire-pump controllers; not all features in this article are available for every type and from every listed manufacturer. Features depend on motor characteristics and driven-equipment operating criteria. Verify availability and unique characteristics with manufacturer; include in the Section Text or show on Drawings those features that apply to each controller. See Editing Instruction No. 2 and "Peculiar Characteristics of Controllers for Diesel-Drive Fire Pumps" Article in the Evaluations for additional guidance.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings. If retaining paragraph, ensure that all other related articles retained in the Section Text also include "Basis-of-Design Product" Paragraph and that selected products are from the same manufacturer.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Aquarius Fluid Products, Inc.

2. ASCO Power Technologies, LP; Firetrol Products.

3. Eaton Electrical Inc.; Cutler-Hammer Business Unit.

4. Hubbell Incorporated; Hubbell Industrial Controls.

5. Joslyn Clark Corporation.

6. Master Control Systems, Inc.

7. Metron, Inc.

8. Tornatech.

9. <Insert manufacturer's name>.

Some authorities having jurisdiction or the Owner's insurance underwriter may require specific local approvals (e.g., the New York Department of Buildings) or an FM Approvals certification and mark. Insert additional or replacement standards or approvals in first paragraph below.

C. General Requirements for Controllers:

1. Comply with NFPA 20 and [UL 218] <Insert standard>.

2. Listed by an NRTL for diesel-engine driver for fire-pump service.

3. [Combined automatic and nonautomatic] [Nonautomatic] operation.

4. Factory assembled, wired, and tested.

D. Method of Starting:

Retain first subparagraph below for controllers with automatic operation. Retain first option for controllers actuated by water flow in fire-suppression piping; retain second option for other starting means (e.g., fire-protection equipment, sequential starting), and provide details of starting method here or on Drawings.

1. [Pressure] [Nonpressure]-switch actuated.

Retain first two subparagraphs below for automatic operation and pressure-switch actuation.

a. Water-pressure-actuated switch and pressure transducer with independent high- and low-calibrated adjustments responsive to water pressure in fire-suppression piping.

b. System pressure recorder, electric ac driven, with spring backup.

Retain first two subparagraphs below for automatic operation.

c. Programmable minimum-run-time relay to prevent short cycling.

d. Programmable timer for weekly tests.

Only a battery-powered starting method is allowed by NFPA 20 for diesel-engine controllers.

2. Dual, redundant dc-voltage battery units, with automatic changeover.

3. Emergency Control: Bypasses all automatic control circuits during manual starting and running.

4. Automatic engine start on loss of ac power to the controller.

NFPA 20 restricts use of automatic shutdown. Retain first option in first paragraph below if allowed and required to suit Project. See "General Requirements for Fire-Pump Controllers" Article in the Evaluations if retaining first option.

E. Method of Stopping: [Automatic and nonautomatic shutdown after automatic starting] [Nonautomatic].

Functions in first paragraph below are the minimum required by NFPA 20; however, standard features and optional modifications vary considerably among manufacturers of fire-pump controllers; they must be closely coordinated with "General Requirements for Controllers," "Method of Starting," and "Method of Stopping" paragraphs in this article. Verify availability and unique characteristics with manufacturers; include in first paragraph or show on Drawings those features that apply to the controllers.

F. Door-Mounted Operator Interface and Controls:

1. Monitor, display, and control devices, alarms, functions, and operations listed in NFPA 20 as required for drivers and controller types used.

2. Method of Control and Indication:

a. [Microprocessor-based logic] <Insert logic type> controller, with multiline [LCD] <Insert display type> readout.

b. [Membrane] <Insert keypad type> keypad.

c. [LED] <Insert lamp type> alarm and status indicating lights.

3. Local[ and Remote] Alarm and Status Indications:

Manufacturers offer numerous local and remote alarm and status indications and interfaces. Consult manufacturers for availability and types.

a. Controller power on.

b. Engine-lubrication-system critically low oil pressure.

c. Engine-jacket coolant high temperature.

d. Engine fail-to-start.

e. Engine overspeed shutdown.

f. Low fuel level.

g. Missing or failed battery.

h. Battery charger failure.

Retain first subparagraph below for engines equipped with pressure-limiting controls.

i. System overpressure.

Retain first two subparagraphs below for engines equipped with ECM controls.

j. ECM selector switch in alternate ECM position.

k. Fuel injector malfunction.

l. <Insert indication>.

NFPA 20 does not allow a silence switch or push button for alarms listed in this article.

4. Audible alarm.

5. Nonautomatic START and STOP push buttons or switches.

6. <Insert function>.

G. Battery Charger System:

1. Built-in, independent, dual battery chargers with automatic changeover; [12-V dc] [24-V dc] for [lead-acid] [nickel-cadmium] batteries.

2. Standard: [UL 1236] <Insert standard>.

2.4 CONTROLLERS FOR PRESSURE-MAINTENANCE PUMPS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings. If retaining paragraph, ensure that all other related articles retained in the Section Text also include "Basis-of-Design Product" Paragraph and that selected products are from the same manufacturer.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Aquarius Fluid Products, Inc.

2. ASCO Power Technologies, LP; Firetrol Products.

3. Eaton Electrical Inc.; Cutler-Hammer Business Unit.

4. Hubbell Incorporated; Hubbell Industrial Controls.

5. Joslyn Clark Corporation.

6. Master Control Systems, Inc.

7. Metron, Inc.

8. Tornatech.

9. <Insert manufacturer's name>.

C. General Requirements for Pressure-Maintenance-Pump Controllers:

1. Type: UL 508 factory assembled, -wired, and tested, across-the-line; for combined automatic and manual operation.

2. Enclosure: UL 508 and NEMA 250, Type 2 for wall-mounting.

3. Factory assembled, wired, and tested.

4. Finish: Manufacturer's standard color paint.

D. Rate controller for scheduled horsepower and include the following:

1. Fusible disconnect switch.

2. Pressure switch.

3. Hand-off-auto selector switch.

4. Pilot light.

5. Running period timer.

2.5 REMOTE ALARM PANELS

NFPA 20 requires use of a remote alarm panel located in an area that is constantly attended if the fire-pump controller is in a location that is not constantly attended or supervised. See Editing Instruction No. 2 and "Remote Alarm Panels" Article in the Evaluations for additional guidance.

A. General Requirements for Remote Alarm Panels: Comply with NFPA 20 and [UL 218] <Insert standard>; listed by an NRTL for fire-pump service.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

B. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings. If retaining paragraph, ensure that all other related articles retained in the Section Text also include "Basis-of-Design Product" Paragraph and that selected products are from the same manufacturer.

C. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Aquarius Fluid Products, Inc.

2. ASCO Power Technologies, LP; Firetrol Products.

3. Eaton Electrical Inc.; Cutler-Hammer Business Unit.

4. Hubbell Incorporated; Hubbell Industrial Controls.

5. Joslyn Clark Corporation.

6. Master Control Systems, Inc.

7. Metron, Inc.

8. Tornatech.

9. <Insert manufacturer's name>.

Not all features, accessories, and options in this article are available from every listed manufacturer. Verify availability and unique characteristics with manufacturers.

D. General Requirements for Remote Alarm Panels: Factory assembled, wired, and tested.

Retain first and last options in first paragraph below if a separate and redundant normal power source is provided to the panel. Not all listed manufacturers offer dual voltage sources.

E. Supervisory[ and Normal] Control Voltage: [120-V ac] [240-V ac] <Insert voltage>; [single] [dual] source.

Alarms and status indications in first two paragraphs below are the minimum required by NFPA 20; however, standard and optional features vary considerably among manufacturers of remote alarm panels. Verify availability and unique characteristics with manufacturer; include in first paragraph below or show on Drawings those features that apply to each alarm panel. Retain first paragraph for electric controllers; retain second paragraph for diesel-engine controllers.

F. Audible and Visual Alarm and Status Indications:

1. Driver running.

2. Loss of phase.

3. Phase reversal.

4. Supervised power on.

5. [Common] [Separate] trouble on the controller.

If retaining second option in subparagraph above, insert list of required alarms in first subparagraph below.

a. <Insert alarm>.

Retain first subparagraph below if power is supplied from multiple sources.

6. Controller connected to alternate power source.

7. <Insert indication>.

G. Audible and Visual Alarm and Status Indications: Manufacturer's standard indicating lights; [push-to-test] [non-push-to-test, with separate test push button].

1. Engine running.

2. Controller main switch turned to the off or manual position.

3. Supervised power on.

4. [Common] [Separate] trouble on the controller or engine.

If retaining second option in subparagraph above, insert list of required alarms in first subparagraph below.

a. <Insert alarm>.

5. Common pump room trouble.

Retain first subparagraph below if power is supplied from multiple sources.

6. Controller connected to alternate power source.

7. <Insert indication>.

H. Audible alarm, with silence push button.

2.6 ENCLOSURES

A. Fire-Pump Controllers, ATS, and Remote Alarm Panels: NEMA 250, to comply with environmental conditions at installed locations and NFPA 20.

See "Enclosures" Article in the Evaluations for discussion of enclosure types. Coordinate subparagraphs below with Drawings by identifying the designated areas on plans or by including the required enclosure types. Enclosure materials and finishes may be added to the Section Text. NFPA 20 requires NEMA 250, Type 2 as the minimum allowable enclosure type for indoor controllers and ATS; NEMA 250, Type 1 is allowed for alarm panels. Consult manufacturers for availability of, and limitations on, other than NEMA 250, Type 2 enclosures, especially if retaining "Basis-of-Design Product" Paragraph in other articles.

Retain first subparagraph below only if retaining remote alarm panels.

1. Indoor, Dry and Clean Locations: [Type 1 (IEC IP10)] <Insert type>.

2. Indoor Locations Subject to Dripping Noncorrosive Liquids: [Type 2 (IEC IP11)] <Insert type>.

3. Outdoor Locations: [Type 3R (IEC IP14)] [Type 4 (IEC IP56)] [Type 4X (IEC IP56)] <Insert type>.

4. Other Wet or Damp, Indoor Locations: [Type 4 (IEC IP56)] [Type 4X (IEC IP56)] <Insert type>.

5. Indoor Locations Subject to Dust, Falling Dirt, and Dripping Noncorrosive Liquids: Type 12 (IEC IP12).

B. Enclosure Color: [Manufacturer's standard "fire-pump-controller red"] <Insert color>.

C. Nameplates: Comply with NFPA 20; complete with capacity, characteristics, approvals, listings, and other pertinent data.

D. Floor stands, 12 inches (305 mm) high, for floor-mounted controllers.

2.7 SOURCE QUALITY CONTROL

A. Testing: Test and inspect fire-pump controllers according to requirements in NFPA 20 and [UL 218] <Insert standard>.

1. Verification of Performance: Rate controllers according to operation of functions and features specified.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

B. Fire-pump controllers will be considered defective if they do not pass tests and inspections.

C. Prepare test and inspection reports.

PART 3 -  EXECUTION

3.1 CONTROLLER INSTALLATION

NFPA 20 and NFPA 70 define specific installation requirements for fire-pump controllers. See "General Installation Requirements for Fire-Pump Controllers" Article in the Evaluations for additional information.

A. Install controllers within sight of their respective drivers.

Retain first paragraph below for controllers actuated by water flow in fire-suppression piping.

B. Connect controllers to their dedicated pressure-sensing lines.

Limited-service controllers and small-to-medium-sized, full-service controllers are readily suited for wall mounting. Retain first paragraph below for equipment supported by walls or freestanding racks.

C. Wall-Mounting Controllers: Install controllers on walls with disconnect operating handles not higher than 79 inches (2006 mm) above finished floor, and bottom of enclosure not less than 12 inches (305 mm) above finished floor unless otherwise indicated. Bolt units to wall or mount on lightweight structural-steel channels bolted to wall. For controllers not on walls, provide freestanding racks complying with Section 260529 "Hangers and Supports for Electrical Systems."

Full- and limited-service controllers are available with standard or optional floor stands. Retain first paragraph below for controllers supported on slabs-on-grade.

D. Floor-Mounting Controllers: Install controllers on 4-inch (100-mm) nominal-thickness concrete bases, using floor stands high enough so that the bottom of enclosure cabinet is not less than 12 inches (305 mm) above finished floor. Comply with requirements for concrete bases specified in [Section 033000 "Cast-in-Place Concrete."] [Section 033053 "Miscellaneous Cast-in-Place Concrete."]

1. Install dowel rods to connect concrete base to concrete floor. Unless otherwise indicated, install dowel rods on 18-inch (450-mm) centers around the full perimeter of concrete base.

2. For supported equipment, install epoxy-coated anchor bolts that extend through concrete base, and anchor into structural concrete floor.

3. Place and secure anchorage devices. Use setting drawings, templates, diagrams, instructions, and directions furnished with items to be embedded.

4. Install anchor bolts to elevations required for proper attachment to supported equipment.

Retain first paragraph below if seismic controls are Project requirement. Coordinate with Drawings.

E. Seismic Bracing: Comply with requirements specified in Section 260548.16 "Seismic Controls for Electrical Systems."

F. Temporary Lifting Provisions: Remove temporary lifting eyes, channels, and brackets and temporary blocking of moving parts from enclosures and components.

Retain paragraph below if retaining full- or limited-service, electric-drive controllers in Part 2.

G. Comply with NEMA ICS 15.

3.2 REMOTE ALARM PANEL INSTALLATION

Retain this article if retaining "Remote Alarm Panels" Article in Part 2.

A. Install panels on walls with tops not higher than [72 inches (1829 mm)] <Insert height> above finished floor unless otherwise indicated. Bolt units to wall or mount on lightweight structural-steel channels bolted to wall. For panels not on walls, provide freestanding racks complying with Section 260529 "Hangers and Supports for Electrical Systems."

3.3 POWER WIRING INSTALLATION

Retain this article if retaining electric-drive controllers in Part 2. NFPA 20 and NFPA 70 have specific requirements and restrictions on wiring for electric-drive controllers; review these standards before revising this article. See "General Installation Requirements for Fire-Pump Controllers" Article in the Evaluations for restrictions on other wiring systems routed through controllers.

A. Install power wiring between controllers and their services or sources, and between controllers and their drivers. Comply with requirements in NFPA 20, NFPA 70, and Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

B. Comply with NECA 1.

3.4 CONTROL AND ALARM WIRING INSTALLATION

Retain this article if remote control or remote status indication is required. NFPA 20 and NFPA 70 have specific requirements and restrictions on control and alarm wiring for all fire-pump controllers and associated remote panels; review these standards before revising this article. See "General Installation Requirements for Fire-Pump Controllers" Article in the Evaluations for restrictions on other wiring systems routed through controllers.

A. Install wiring between controllers and remote devices[ and facility's central monitoring system]. Comply with requirements in NFPA 20, NFPA 70, and Section 260523 "Control-Voltage Electrical Power Cables."

Retain first paragraph below if retaining remote alarm panels in Part 2. Retain second paragraph if remote indication at the fire-alarm system is required.

B. Install wiring between remote alarm panels and controllers. Comply with requirements in NFPA 20, NFPA 70, and Section 260523 "Control-Voltage Electrical Power Cables."

C. Install wiring between controllers and the building's fire-alarm system. Comply with requirements specified in Section 283111 "Digital, Addressable Fire-Alarm System."

D. Bundle, train, and support wiring in enclosures.

E. Connect remote manual and automatic activation devices where applicable.

3.5 IDENTIFICATION

A. Comply with requirements in NFPA 20 for marking fire-pump controllers.

B. Identify system components, wiring, cabling, and terminals. Comply with requirements for identification in NFPA 20 and as specified in Section 260553 "Identification for Electrical Systems."

3.6 FIELD QUALITY CONTROL

NFPA 20 requires manufacturers of fire-pump controllers to be present during field acceptance testing. Retain first paragraph below to require Contractor to perform tests and inspections.

A. Perform tests and inspections.

Retain first two paragraphs below to describe tests and inspections to be performed.

Field acceptance tests are part of the formal process to verify compliance with NFPA 20; therefore, all pre-acceptance testing preparation should be complete before scheduling the tests for witnessing by authorities having jurisdiction.

B. Acceptance Testing Preparation:

1. Inspect and Test Each Component:

a. Inspect wiring, components, connections, and equipment installations. Test and adjust components and equipment.

b. Test insulation resistance for each element, component, connecting supply, feeder, and control circuits.

c. Test continuity of each circuit.

2. Verify and Test Each Electric-Driver Controller:

a. Verify that voltages at controller locations are within plus 10 or minus 1 percent of motor nameplate rated voltages, with motors off. If outside this range for any motor, notify [Architect] [Construction Manager] [Owner] before starting the motor(s).

b. Test each motor for proper phase rotation.

3. Operational Test: After electrical circuitry has been energized, start units to confirm proper unit operation.

4. Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.

C. Field Acceptance Tests:

1. Do not begin field acceptance testing until suction piping has been flushed and hydrostatically tested and the certificate for flushing and testing has been submitted to [Architect] [Construction Manager] [Owner] and authorities having jurisdiction.

2. Prior to starting, notify authorities having jurisdiction of the time and place of the acceptance testing.

3. Engage manufacturer's factory-authorized service representative to be present during the testing.

4. Perform field acceptance tests as outlined in NFPA 20.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

D. Controllers will be considered defective if they do not pass tests and inspections.

E. Prepare test and inspection reports.

F. Perform startup service.

G. Complete installation and startup checks according to manufacturer's written instructions.

3.7 ADJUSTING

Retain applicable paragraphs in this article. Coordinate with selections made in Part 2.

A. Adjust controllers to function smoothly and as recommended by manufacturer.

B. Set field-adjustable switches, auxiliary relays, time-delay relays, and timers.

C. Program microprocessors for required operational sequences, status indications, alarms, event recording, and display features. Clear events memory after final acceptance testing and prior to Substantial Completion.

D. Set field-adjustable pressure switches.

3.8 DEMONSTRATION

Retain applicable options in paragraph below. Coordinate with selections made in Part 2.

A. [Engage a factory-authorized service representative to train] [Train] Owner's maintenance personnel to adjust, operate, and maintain controllers[ and remote alarm panels] [, and to use and reprogram microprocessor-based controls within this equipment].

END OF SECTION 213900

	CONTROLLERS FOR FIRE-PUMP DRIVERS
	213900 - 1



