Copyright 2010 AIA
MasterSpec Professional
03/10

Copyright 2010 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 220517 - SLEEVES AND SLEEVE SEALS FOR PLUMBING PIPING
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Sleeves.

2. Sleeve-seal systems.

3. Grout.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product indicated.

PART 2 -  PRODUCTS

2.1 SLEEVES

A. Cast-Iron Wall Pipes: Cast or fabricated of cast or ductile iron and equivalent to ductile-iron pressure pipe, with plain ends and integral waterstop unless otherwise indicated.

B. Galvanized-Steel Wall Pipes: ASTM A 53/A 53M, Schedule 40, with plain ends and welded steel collar; zinc coated.

C. Galvanized-Steel-Pipe Sleeves: ASTM A 53/A 53M, Type E, Grade B, Schedule 40, zinc coated, with plain ends.

PVC sleeves in first paragraph below may be prohibited by fire authorities having jurisdiction.

D. PVC-Pipe Sleeves: ASTM D 1785, Schedule 40.

E. Galvanized-Steel-Sheet Sleeves: 0.0239-inch (0.6-mm) minimum thickness; round tube closed with welded longitudinal joint.

2.2 SLEEVE-SEAL SYSTEMS

Sleeve-seal systems in this article are used for piping penetrations in slabs-on-grade and below grade in exterior walls. These systems are available for NPS 1/2 to NPS 48 (DN 15 to DN 1200) piping.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Advance Products & Systems, Inc.

2. CALPICO, Inc.

3. Metraflex Company (The).

4. Pipeline Seal and Insulator, Inc.

5. Proco Products, Inc.

6. <Insert manufacturer's name>.

C. Description: Modular sealing-element unit, designed for field assembly, for filling annular space between piping and sleeve.

Retain first option in first subparagraph below unless NBR gasket material is required because hydrocarbons are present in the soil.

1. Sealing Elements: [EPDM-rubber] [NBR] interlocking links shaped to fit surface of pipe. Include type and number required for pipe material and size of pipe.

2. Pressure Plates: [Carbon steel] [Plastic] [Stainless steel].

3. Connecting Bolts and Nuts: [Carbon steel, with corrosion-resistant coating,] [Stainless steel] of length required to secure pressure plates to sealing elements.

2.3 GROUT

A. Standard: ASTM C 1107/C 1107M, Grade B, post-hardening and volume-adjusting, dry, hydraulic-cement grout.

B. Characteristics: Nonshrink; recommended for interior and exterior applications.

C. Design Mix: 5000-psi (34.5-MPa), 28-day compressive strength.

D. Packaging: Premixed and factory packaged.

PART 3 -  EXECUTION

3.1 SLEEVE INSTALLATION

A. Install sleeves for piping passing through penetrations in floors, partitions, roofs, and walls.

B. For sleeves that will have sleeve-seal system installed, select sleeves of size large enough to provide [1-inch (25-mm)] <Insert dimension> annular clear space between piping and concrete slabs and walls.

Retain subparagraph below if applicable.

1. Sleeves are not required for core-drilled holes.

C. Install sleeves in concrete floors, concrete roof slabs, and concrete walls as new slabs and walls are constructed.

1. Cut sleeves to length for mounting flush with both surfaces.

a. Exception: Extend sleeves installed in floors of mechanical equipment areas or other wet areas [2 inches (50 mm)] <Insert dimension> above finished floor level.

2. Using grout, seal the space outside of sleeves in slabs and walls without sleeve-seal system.

D. Install sleeves for pipes passing through interior partitions.

1. Cut sleeves to length for mounting flush with both surfaces.

Revise first subparagraph below as required for seismic design conditions. Coordinate sleeve requirements with Section 220719 "Plumbing Piping Insulation."

2. Install sleeves that are large enough to provide 1/4-inch (6.4-mm) annular clear space between sleeve and pipe or pipe insulation.

3. Seal annular space between sleeve and piping or piping insulation; use joint sealants appropriate for size, depth, and location of joint. Comply with requirements for sealants specified in Section 079200 "Joint Sealants."

Revise paragraph below to suit Project and insert description of firestopping sealant.

E. Fire-Barrier Penetrations: Maintain indicated fire rating of walls, partitions, ceilings, and floors at pipe penetrations. Seal pipe penetrations with firestop materials. Comply with requirements for firestopping specified in Section 078413 "Penetration Firestopping."

3.2 SLEEVE-SEAL-SYSTEM INSTALLATION

Sleeve-seal systems in this article are used, in slabs-on-grade and below grade in exterior concrete walls, for a watertight seal around service piping entries into the building. These systems typically require installation in a sleeve for proper operation.

A. Install sleeve-seal systems in sleeves in exterior concrete walls and slabs-on-grade at service piping entries into building.

B. Select type, size, and number of sealing elements required for piping material and size and for sleeve ID or hole size. Position piping in center of sleeve. Center piping in penetration, assemble sleeve-seal system components, and install in annular space between piping and sleeve. Tighten bolts against pressure plates that cause sealing elements to expand and make a watertight seal.

3.3 SLEEVE AND SLEEVE-SEAL SCHEDULE

A. Use sleeves and sleeve seals for the following piping-penetration applications:

1. Exterior Concrete Walls above Grade:

a. Piping Smaller Than [NPS 6 (DN 150)] <Insert pipe size>: [Cast-iron wall sleeves] [Galvanized-steel wall sleeves] [Galvanized-steel-pipe sleeves] <Insert material>.

b. Piping [NPS 6 (DN 150)] <Insert pipe size> and Larger: [Cast-iron wall sleeves] [Galvanized-steel wall sleeves] [Galvanized-steel-pipe sleeves] <Insert material>.

2. Exterior Concrete Walls below Grade:

a. Piping Smaller Than [NPS 6 (DN 150)] <Insert pipe size>: [Cast-iron wall sleeves with sleeve-seal system] [Galvanized-steel wall sleeves with sleeve-seal system] [Galvanized-steel-pipe sleeves with sleeve-seal system] <Insert material>.

1) Select sleeve size to allow for 1-inch (25-mm) annular clear space between piping and sleeve for installing sleeve-seal system.

b. Piping [NPS 6 (DN 150)] <Insert pipe size> and Larger: [Cast-iron wall sleeves with sleeve-seal system] [Galvanized-steel wall sleeves with sleeve-seal system] [Galvanized-steel-pipe sleeves with sleeve-seal system] <Insert material>.

1) Select sleeve size to allow for 1-inch (25-mm) annular clear space between piping and sleeve for installing sleeve-seal system.

3. Concrete Slabs-on-Grade:

a. Piping Smaller Than [NPS 6 (DN 150)] <Insert pipe size>: [Cast-iron wall sleeves with sleeve-seal system] [Galvanized-steel wall sleeves with sleeve-seal system] [Galvanized-steel-pipe sleeves with sleeve-seal system] <Insert material>.

1) Select sleeve size to allow for 1-inch (25-mm) annular clear space between piping and sleeve for installing sleeve-seal system.

b. Piping [NPS 6 (DN 150)] <Insert pipe size> and Larger: [Cast-iron wall sleeves with sleeve-seal system] [Galvanized-steel wall sleeves with sleeve-seal system] [Galvanized-steel-pipe sleeves with sleeve-seal system] [Galvanized-steel-pipe sleeves] <Insert material>.

Retain first subparagraph below if using sleeve-seal systems; delete if using only galvanized-steel-pipe sleeves.

1) Select sleeve size to allow for 1-inch (25-mm) annular clear space between piping and sleeve for installing sleeve-seal system.

4. Concrete Slabs above Grade:

a. Piping Smaller Than [NPS 6 (DN 150)] <Insert pipe size>: [Galvanized-steel-pipe sleeves] [PVC-pipe sleeves] <Insert material>.

b. Piping [NPS 6 (DN 150)] <Insert pipe size> and Larger: [Galvanized-steel-pipe sleeves] [PVC-pipe sleeves] <Insert material>.

5. Interior Partitions:

Verify, with fire authorities having jurisdiction, that PVC materials are allowed for sleeves.

a. Piping Smaller Than [NPS 6 (DN 150)] <Insert pipe size>: [Galvanized-steel-pipe sleeves] [PVC-pipe sleeves] <Insert material>.

b. Piping [NPS 6 (DN 150)] <Insert pipe size> and Larger: [Galvanized-steel-sheet sleeves] <Insert material>.

END OF SECTION 220517

	SLEEVES AND SLEEVE SEALS FOR PLUMBING PIPING
	220517 - 1



