Copyright 2010 AIA
MasterSpec Professional
03/10

Copyright 2010 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 220519 - METERS AND GAGES FOR PLUMBING PIPING
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Bimetallic-actuated thermometers.

2. Liquid-in-glass thermometers.

3. Thermowells.

4. Dial-type pressure gages.

5. Gage attachments.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product indicated.

1.3 INFORMATIONAL SUBMITTALS

A. Product certificates.

1.4 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

PART 2 -  PRODUCTS

2.1 BIMETALLIC-ACTUATED THERMOMETERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Ashcroft Inc.

2. Ernst Flow Industries.

3. Marsh Bellofram.

4. Miljoco Corporation.

5. Nanmac Corporation.

6. Noshok.

7. Palmer Wahl Instrumentation Group.

8. REOTEMP Instrument Corporation.

9. Tel-Tru Manufacturing Company.

10. Trerice, H. O. Co.

11. Watts Regulator Co.; a div. of Watts Water Technologies, Inc.

12. Weiss Instruments, Inc.

13. WIKA Instrument Corporation - USA.

14. Winters Instruments - U.S.

15. <Insert manufacturer's name>.

C. Standard: ASME B40.200.

Case in first paragraph below will typically be the sealed (dry) type. Hermetically sealed cases are available.

D. Case: [Liquid-filled] [and] [sealed] type(s); stainless steel with [3-inch (76-mm)] [5-inch (127-mm)] <Insert dimension> nominal diameter.

E. Dial: [Nonreflective aluminum] <Insert material> with permanently etched scale markings and scales in [deg F (deg C)] [deg F and deg C].

F. Connector Type(s): Union joint, [adjustable angle] [rigid, back] [and] [rigid, bottom] <Insert type>, with unified-inch screw threads.

G. Connector Size: [1/2 inch (13 mm)] <Insert dimension>, with ASME B1.1 screw threads.

H. Stem: 0.25 or 0.375 inch (6.4 or 9.4 mm) in diameter; stainless steel.

I. Window: [Plain glass] [or] [plastic] <Insert material>.

J. Ring: Stainless steel.

K. Element: Bimetal coil.

L. Pointer: Dark-colored metal.

M. Accuracy: Plus or minus [1] [1.5] <Insert number> percent of scale range.

2.2 LIQUID-IN-GLASS THERMOMETERS

A. Metal-Case, Industrial-Style, Liquid-in-Glass Thermometers:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Flo Fab Inc.

b. Miljoco Corporation.

c. Palmer Wahl Instrumentation Group.

d. Tel-Tru Manufacturing Company.

e. Trerice, H. O. Co.

f. Weiss Instruments, Inc.

g. Winters Instruments - U.S.

h. <Insert manufacturer's name>.

3. Standard: ASME B40.200.

4. Case: [Cast aluminum] <Insert material>; [7-inch (178-mm)] [9-inch (229-mm)] nominal size unless otherwise indicated.

5. Case Form: [Adjustable angle] [Back angle] [Straight] <Insert form> unless otherwise indicated.

6. Tube: Glass with magnifying lens and blue[ or red] organic liquid.

7. Tube Background: Nonreflective aluminum with permanently etched scale markings graduated in [deg F (deg C)] [deg F and deg C].

8. Window: [Glass] [or] [plastic] <Insert material>.

9. Stem: [Aluminum] <Insert material> and of length to suit installation.

a. Design for Thermowell Installation: Bare stem.

10. Connector: 1-1/4 inches (32 mm), with ASME B1.1 screw threads.

11. Accuracy: Plus or minus 1 percent of scale range or one scale division, to a maximum of 1.5 percent of scale range.

B. Plastic-Case, Industrial-Style, Liquid-in-Glass Thermometers:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Ernst Flow Industries.

b. Marsh Bellofram.

c. Miljoco Corporation.

d. Palmer Wahl Instrumentation Group.

e. REOTEMP Instrument Corporation.

f. Watts Regulator Co.; a div. of Watts Water Technologies, Inc.

g. Weiss Instruments, Inc.

h. WIKA Instrument Corporation - USA.

i. <Insert manufacturer's name>.

3. Standard: ASME B40.200.

4. Case: [Plastic] <Insert material>; [7-inch (178-mm)] [9-inch (229-mm)] nominal size unless otherwise indicated.

5. Case Form: [Adjustable angle] [Back angle] [Straight] <Insert form> unless otherwise indicated.

6. Tube: Glass with magnifying lens and blue[ or red] organic liquid.

7. Tube Background: Nonreflective aluminum with permanently etched scale markings graduated in [deg F (deg C)] [deg F and deg C].

8. Window: [Glass] [or] [plastic] <Insert material>.

9. Stem: [Aluminum] [Brass] [Stainless steel] [Aluminum, brass, or stainless steel] <Insert material> and of length to suit installation.

a. Design for Thermowell Installation: Bare stem.

10. Connector: 1-1/4 inches (32 mm), with ASME B1.1 screw threads.

11. Accuracy: Plus or minus 1 percent of scale range or one scale division, to a maximum of 1.5 percent of scale range.

2.3 THERMOWELLS

ASME B40.200 uses the following symbols for thermowell materials: "CNR" for copper nickel (90-10), "CUNI" for copper nickel (70-30), "CRES" for corrosion-resistant steel, "NICU" for nickel copper, "ALBR" for aluminum bronze, and "CSA" for steel. Other materials are allowed.

A. Thermowells:

1. Standard: ASME B40.200.

2. Description: Pressure-tight, socket-type fitting made for insertion into piping tee fitting.

3. Material for Use with Copper Tubing: [CNR] [or] [CUNI] <Insert material>.

4. Material for Use with Steel Piping: [CRES] [CSA] <Insert material>.

5. Type: Stepped shank unless straight or tapered shank is indicated.

6. External Threads: NPS 1/2, NPS 3/4, or NPS 1, (DN 15, DN 20, or NPS 25,) ASME B1.20.1 pipe threads.

7. Internal Threads: 1/2, 3/4, and 1 inch (13, 19, and 25 mm), with ASME B1.1 screw threads.

8. Bore: Diameter required to match thermometer bulb or stem.

9. Insertion Length: Length required to match thermometer bulb or stem.

10. Lagging Extension: Include on thermowells for insulated piping and tubing.

11. Bushings: For converting size of thermowell's internal screw thread to size of thermometer connection.

B. Heat-Transfer Medium: [Mixture of graphite and glycerin] <Insert material>.

2.4 PRESSURE GAGES

A. Direct-Mounted, Metal-Case, Dial-Type Pressure Gages:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. AMETEK, Inc.; U.S. Gauge.

b. Ashcroft Inc.

c. Ernst Flow Industries.

d. Flo Fab Inc.

e. Marsh Bellofram.

f. Miljoco Corporation.

g. Noshok.

h. Palmer Wahl Instrumentation Group.

i. REOTEMP Instrument Corporation.

j. Tel-Tru Manufacturing Company.

k. Trerice, H. O. Co.

l. Watts Regulator Co.; a div. of Watts Water Technologies, Inc.

m. Weiss Instruments, Inc.

n. WIKA Instrument Corporation - USA.

o. Winters Instruments - U.S.

p. <Insert manufacturer's name>.

3. Standard: ASME B40.100.

4. Case: [Liquid-filled] [Sealed] [Open-front, pressure relief] [Solid-front, pressure relief] <Insert type> type(s); [cast aluminum or drawn steel] <Insert material>; [4-1/2-inch (114-mm)] [6-inch (152-mm)] <Insert dimension> nominal diameter.

5. Pressure-Element Assembly: Bourdon tube unless otherwise indicated.

Match pressure connection size in first subparagraph below with gage attachment size.

6. Pressure Connection: Brass, with [NPS 1/4 (DN 8)] [NPS 1/4 or NPS 1/2 (DN 8 or DN 15)] [NPS 1/2 (DN 15)], ASME B1.20.1 pipe threads and bottom-outlet type unless back-outlet type is indicated.

7. Movement: Mechanical, with link to pressure element and connection to pointer.

8. Dial: Nonreflective aluminum with permanently etched scale markings graduated in [psi (kPa)] [psi and kPa].

9. Pointer: Dark-colored metal.

10. Window: [Glass] [or] [plastic] <Insert material>.

11. Ring: [Metal] [Brass] [Stainless steel].

12. Accuracy: [Grade A, plus or minus 1 percent of middle half of] [Grade B, plus or minus 2 percent of middle half of] [Grade C, plus or minus 3 percent of middle half of] [Grade D, plus or minus 5 percent of whole] scale range.

B. Direct-Mounted, Plastic-Case, Dial-Type Pressure Gages:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. AMETEK, Inc.; U.S. Gauge.

b. Ashcroft Inc.

c. Flo Fab Inc.

d. Marsh Bellofram.

e. Miljoco Corporation.

f. Noshok.

g. Palmer Wahl Instrumentation Group.

h. REOTEMP Instrument Corporation.

i. Tel-Tru Manufacturing Company.

j. Trerice, H. O. Co.

k. Weiss Instruments, Inc.

l. WIKA Instrument Corporation - USA.

m. Winters Instruments - U.S.

n. <Insert manufacturer's name>.

3. Standard: ASME B40.100.

4. Case: [Sealed] <Insert type> type; [plastic] <Insert material>; [4-1/2-inch (114-mm)] [6-inch (152-mm)] <Insert dimension> nominal diameter.

5. Pressure-Element Assembly: Bourdon tube unless otherwise indicated.

Match pressure connection size in first subparagraph below with gage attachment size.

6. Pressure Connection: Brass, with [NPS 1/4 (DN 8)] [NPS 1/4 or NPS 1/2 (DN 8 or DN 15)] [NPS 1/2 (DN 15)], ASME B1.20.1 pipe threads and bottom-outlet type unless back-outlet type is indicated.

7. Movement: Mechanical, with link to pressure element and connection to pointer.

8. Dial: Nonreflective aluminum with permanently etched scale markings graduated in [psi (kPa)] [psi and kPa].

9. Pointer: Dark-colored metal.

10. Window: [Glass] [or] [plastic] <Insert material>.

11. Accuracy: [Grade A, plus or minus 1 percent of middle half of] [Grade B, plus or minus 2 percent of middle half of] [Grade C, plus or minus 3 percent of middle half of] [Grade D, plus or minus 5 percent of whole] scale range.

C. Remote-Mounted, Metal-Case, Dial-Type Pressure Gages:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. AMETEK, Inc.; U.S. Gauge.

b. Ashcroft Inc.

c. Ernst Flow Industries.

d. Flo Fab Inc.

e. Marsh Bellofram.

f. Miljoco Corporation.

g. Noshok.

h. Palmer Wahl Instrumentation Group.

i. REOTEMP Instrument Corporation.

j. Tel-Tru Manufacturing Company.

k. Trerice, H. O. Co.

l. Watts Regulator Co.; a div. of Watts Water Technologies, Inc.

m. Weiss Instruments, Inc.

n. WIKA Instrument Corporation - USA.

o. Winters Instruments - U.S.

p. <Insert manufacturer's name>.

3. Standard: ASME B40.100.

4. Case: [Liquid-filled] [Sealed] <Insert type> type; [cast aluminum or drawn steel] [metal] <Insert material>; [4-1/2-inch (114-mm)] [6-inch (152-mm)] <Insert dimension> nominal diameter with [back] [front] flange and holes for panel mounting.

5. Pressure-Element Assembly: Bourdon tube unless otherwise indicated.

Match pressure connection size in first subparagraph below with gage attachment size.

6. Pressure Connection: Brass, with [NPS 1/4 (DN 8)] [NPS 1/4 or NPS 1/2 (DN 8 or DN 15)] [NPS 1/2 (DN 15)], ASME B1.20.1 pipe threads and bottom-outlet type unless back-outlet type is indicated.

7. Movement: Mechanical, with link to pressure element and connection to pointer.

8. Dial: Nonreflective aluminum with permanently etched scale markings graduated in [psi (kPa)] [psi and kPa].

9. Pointer: Dark-colored metal.

10. Window: [Glass] [or] [plastic] <Insert material>.

11. Ring: [Metal] [Stainless steel] <Insert material>.

12. Accuracy: [Grade A, plus or minus 1 percent of middle half of] [Grade B, plus or minus 2 percent of middle half of] [Grade C, plus or minus 3 percent of middle half of] [Grade D, plus or minus 5 percent of whole] scale range.

D. Remote-Mounted, Plastic-Case, Dial-Type Pressure Gages:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. AMETEK, Inc.; U.S. Gauge.

b. Ashcroft Inc.

c. Miljoco Corporation.

d. Noshok.

e. Palmer Wahl Instrumentation Group.

f. REOTEMP Instrument Corporation.

g. Tel-Tru Manufacturing Company.

h. Trerice, H. O. Co.

i. Weiss Instruments, Inc.

j. WIKA Instrument Corporation - USA.

k. Winters Instruments - U.S.

l. <Insert manufacturer's name>.

3. Standard: ASME B40.100.

4. Case: [Sealed] <Insert type> type; [plastic] <Insert material>; [4-1/2-inch (114-mm)] [6-inch (152-mm)] <Insert dimension> nominal diameter with [back] [front] flange and holes for panel mounting.

5. Pressure-Element Assembly: Bourdon tube unless otherwise indicated.

Match pressure connection size in first subparagraph below with gage attachment size.

6. Pressure Connection: Brass, with [NPS 1/4 (DN 8)] [NPS 1/4 or NPS 1/2 (DN 8 or DN 15)] [NPS 1/2 (DN 15)], ASME B1.20.1 pipe threads and bottom-outlet type unless back-outlet type is indicated.

7. Movement: Mechanical, with link to pressure element and connection to pointer.

8. Dial: Nonreflective aluminum with permanently etched scale markings graduated in [psi (kPa)] [psi and kPa].

9. Pointer: Dark-colored metal.

10. Window: [Glass] [or] [plastic] <Insert material>.

11. Accuracy: [Grade A, plus or minus 1 percent of middle half of] [Grade B, plus or minus 2 percent of middle half of] [Grade C, plus or minus 3 percent of middle half of] [Grade D, plus or minus 5 percent of whole] scale range.

2.5 GAGE ATTACHMENTS

Match attachment size in two paragraphs below with pressure-gage-connection size.

A. Snubbers: ASME B40.100, brass; with [NPS 1/4 (DN 8)] [NPS 1/4 or NPS 1/2 (DN 8 or DN 15)] [NPS 1/2 (DN 15)], ASME B1.20.1 pipe threads and [piston] [porous-metal]-type surge-dampening device. Include extension for use on insulated piping.

B. Valves: [Brass ball] [Brass or stainless-steel needle], with [NPS 1/4 (DN 8)] [NPS 1/4 or NPS 1/2 (DN 8 or DN 15)] [NPS 1/2 (DN 15)], ASME B1.20.1 pipe threads.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Install thermowells with socket extending [a minimum of 2 inches (51 mm) into fluid] [one-third of pipe diameter] [to center of pipe] and in vertical position in piping tees.

B. Install thermowells of sizes required to match thermometer connectors. Include bushings if required to match sizes.

C. Install thermowells with extension on insulated piping.

D. Fill thermowells with heat-transfer medium.

E. Install direct-mounted thermometers in thermowells and adjust vertical and tilted positions.

F. Install remote-mounted thermometer bulbs in thermowells and install cases on panels; connect cases with tubing and support tubing to prevent kinks. Use minimum tubing length.

G. Install direct-mounted pressure gages in piping tees with pressure gage located on pipe at the most readable position.

H. Install remote-mounted pressure gages on panel.

I. Install valve and snubber in piping for each pressure gage for fluids.

J. Install thermometers in the following locations:

1. Inlet and outlet of each water heater.

2. Inlets and outlets of each domestic water heat exchanger.

3. Inlet and outlet of each domestic hot-water storage tank.

4. Inlet and outlet of each remote domestic water chiller.

5. <Insert location>.

K. Install pressure gages in the following locations:

1. Building water service entrance into building.

2. Inlet and outlet of each pressure-reducing valve.

3. Suction and discharge of each domestic water pump.

4. <Insert location>.

L. Install meters and gages adjacent to machines and equipment to allow service and maintenance of meters, gages, machines, and equipment.

M. Adjust faces of meters and gages to proper angle for best visibility.

3.2 THERMOMETER SCHEDULE

Retain this article if more than one type of thermometer is required; delete if all thermometers are the same type.

Retain and revise applicable thermometer applications. Coordinate with materials specified in Part 2.

Retain "one of" option in first paragraph below to allow Contractor to select thermometer materials from those retained.

A. Thermometers at inlet and outlet of each domestic water heater shall be[ one of] the following:

Retain one or both subparagraphs below. If retaining more than one type of thermometer, indicate location of each on Drawings.

1. [Liquid-filled] [Sealed], bimetallic-actuated type.

2. Industrial-style, liquid-in-glass type.

Retain "one of" option in first paragraph below to allow Contractor to select thermometer materials from those retained.

B. Thermometers at inlets and outlets of each domestic water heat exchanger shall be[ one of] the following:

Retain one or both subparagraphs below. If retaining more than one type of thermometer, indicate location of each on Drawings.

1. [Liquid-filled] [Sealed], bimetallic-actuated type.

2. Industrial-style, liquid-in-glass type.

Retain "one of" option in first paragraph below to allow Contractor to select thermometer materials from those retained.

C. Thermometers at inlet and outlet of each domestic hot-water storage tank shall be[ one of] the following:

Retain one or both subparagraphs below. If retaining more than one type of thermometer, indicate location of each on Drawings.

1. [Liquid-filled] [Sealed], bimetallic-actuated type.

2. Industrial-style, liquid-in-glass type.

Retain "one of" option in first paragraph below to allow Contractor to select thermometer materials from those retained.

D. Thermometers at inlet and outlet of each remote domestic water chiller shall be[ one of] the following:

Retain one or both subparagraphs below. If retaining more than one type of thermometer, indicate location of each on Drawings.

1. [Liquid-filled] [Sealed], bimetallic-actuated type.

2. Industrial-style, liquid-in-glass type.

Insert additional paragraphs for thermometer applications here.

E. Thermometer stems shall be of length to match thermowell insertion length.

3.3 THERMOMETER SCALE-RANGE SCHEDULE

The IP and SI temperature values for the scale ranges presented in this article are not mathematical, rounded, conversions from IP to SI; rather they are the temperature ranges within each specific unit of measure that are available from most manufacturers.

Retain the first option in each paragraph for thermometers with a single scale in either deg F or deg C; retain the second option for thermometers with dual scales.

Scale ranges vary among types of thermometers and among manufacturers. Retain a scale range that covers more than service-fluid temperature range. Exact ranges listed are not mandatory.

Retain one or more of first three paragraphs below. If retaining more than one scale range, indicate location of each on Drawings.

A. Scale Range for Domestic Cold-Water Piping: [0 to 100 deg F (Minus 20 to plus 50 deg C)] [0 to 100 deg F and minus 20 to plus 50 deg C].

B. Scale Range for Domestic Cold-Water Piping: [0 to 150 deg F (Minus 20 to plus 70 deg C)] [0 to 150 deg F and minus 20 to plus 70 deg C].

C. Scale Range for Domestic Cold-Water Piping: [30 to 240 deg F (0 to plus 115 deg C)] [30 to 240 deg F and 0 to plus 115 deg C].

Retain one or both of first two paragraphs below. If retaining more than one scale range, indicate location of each on Drawings.

D. Scale Range for Domestic Hot-Water Piping: [0 to 250 deg F (0 to 150 deg C)] [0 to 250 deg F and 0 to 150 deg C].

E. Scale Range for Domestic Hot-Water Piping: [20 to 240 deg F (0 to 150 deg C)] [20 to 240 deg F and 0 to 150 deg C].

Retain one or both paragraphs below. If retaining more than one scale range, indicate location of each on Drawings.

F. Scale Range for Domestic Cooled-Water Piping: [0 to 100 deg F (Minus 20 to plus 50 deg C)] [0 to 100 deg F and minus 20 to plus 50 deg C].

G. Scale Range for Domestic Cooled-Water Piping: [0 to 150 deg F (Minus 20 to plus 70 deg C)] [0 to 150 deg F and minus 20 to plus 70 deg C].

Insert additional paragraphs for thermometer scale ranges and applications here.

3.4 PRESSURE-GAGE SCHEDULE

Retain this article if more than one type of pressure gage is required; delete if all pressure gages are the same type.

Retain and revise applicable pressure-gage applications. Coordinate with materials specified in Part 2.

Retain "one of" option in first paragraph below to allow Contractor to select pressure-gage materials from those retained.

A. Pressure gages at discharge of each water service into building shall be[ one of] the following:

Retain one or both subparagraphs below. If retaining more than one type of pressure gage, indicate location of each on Drawings.

1. [Liquid-filled] [Sealed] [Open-front, pressure-relief] [Solid-front, pressure-relief] <Insert type>, [direct] [remote]-mounted, metal case.

2. [Sealed] <Insert type>, [direct] [remote]-mounted, plastic case.

Retain "one of" option in first paragraph below to allow Contractor to select pressure-gage materials from those retained.

B. Pressure gages at inlet and outlet of each water pressure-reducing valve shall be[ one of] the following:

Retain one or both subparagraphs below. If retaining more than one type of pressure gage, indicate location of each on Drawings.

1. [Liquid-filled] [Sealed] [Open-front, pressure-relief] [Solid-front, pressure-relief] <Insert type>, [direct] [remote]-mounted, metal case.

2. [Sealed] <Insert type>, [direct] [remote]-mounted, plastic case.

Retain "one of" option in paragraph below to allow Contractor to select pressure-gage materials from those retained.

C. Pressure gages at suction and discharge of each domestic water pump shall be[ one of] the following:

Retain one or both subparagraphs below. If retaining more than one type of pressure gage, indicate location of each on Drawings.

1. [Liquid-filled] [Sealed] [Open-front, pressure-relief] [Solid-front, pressure-relief] <Insert type>, [direct] [remote]-mounted, metal case.

2. [Sealed] <Insert type>, [direct] [remote]-mounted, plastic case.

Insert additional paragraphs for pressure-gage applications here.

3.5 PRESSURE-GAGE SCALE-RANGE SCHEDULE

The IP and SI pressure values for the scale ranges presented in this article are not mathematical, rounded, conversions from IP to SI; rather they are the pressure ranges within each specific unit of measure that are available from most manufacturers.

Retain the first option in each paragraph for pressure gages with a single scale in either psi or kPa; retain the second option for pressure gages with dual scales.

Scale ranges vary among types of pressure gages and among manufacturers. Retain a scale range that covers more than service-fluid pressure range. Exact ranges listed are not mandatory.

Retain one or more of first three paragraphs below. If retaining more than one scale range, indicate location of each on Drawings.

A. Scale Range for Water Service Piping: [0 to 100 psi (0 to 600 kPa)] [0 to 100 psi and 0 to 600 kPa].

B. Scale Range for Water Service Piping: [0 to 160 psi (0 to 1100 kPa)] [0 to 160 psi and 0 to 1100 kPa].

C. Scale Range for Water Service Piping: [0 to 200 psi (0 to 1400 kPa)] [0 to 200 psi and 0 to 1400 kPa].

Retain one or more of three paragraphs below. If retaining more than one scale range, indicate location of each on Drawings.

D. Scale Range for Domestic Water Piping: [0 to 100 psi (0 to 600 kPa)] [0 to 100 psi and 0 to 600 kPa].

E. Scale Range for Domestic Water Piping: [0 to 160 psi (0 to 1100 kPa)] [0 to 160 psi and 0 to 1100 kPa].

F. Scale Range for Domestic Water Piping: [0 to 200 psi (0 to 1400 kPa)] [0 to 200 psi and 0 to 1400 kPa].

Insert additional paragraphs for pressure-gage scale ranges and applications here.

END OF SECTION 220519

	METERS AND GAGES FOR PLUMBING PIPING
	220519 - 1



