Copyright 2010 AIA
MasterSpec Professional
03/10

Copyright 2010 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 220523 - GENERAL-DUTY VALVES FOR PLUMBING PIPING
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Brass ball valves.

2. Bronze ball valves.

3. Iron, single-flange butterfly valves.

4. Bronze swing check valves.

5. Iron swing check valves.

6. Iron swing check valves with closure control.

7. Bronze gate valves.

8. Iron gate valves.

9. Bronze globe valves.

10. Iron globe valves.

11. Chainwheels.

B. Related Sections:

Retain Sections in subparagraphs below that contain requirements Contractor might expect to find in this Section but are specified in other Sections.

1. Section 220553 "Identification for Plumbing Piping and Equipment" for valve tags and schedules.

2. Section 221113 "Facility Water Distribution Piping" for valves applicable only to this piping.

3. Section 221116 "Domestic Water Piping" for valves applicable only to this piping.

4. Section 221319 "Sanitary Waste Piping Specialties" for valves applicable only to this piping.

5. Section 221423 "Storm Drainage Piping Specialties" for valves applicable only to this piping.

6. Section 221513 "General-Service Compressed-Air Piping" for valves applicable only to this piping.

7. Section 226113 "Compressed-Air Piping for Laboratory and Healthcare Facilities" for valves applicable only to this piping.

8. Section 226213 "Vacuum Piping for Laboratory and Healthcare Facilities" for valves applicable only to this piping.

9. Section 226313 "Gas Piping for Laboratory and Healthcare Facilities" for valves applicable only to this piping.

10. Section 334100 "Storm Utility Drainage Piping" for valves applicable only to this piping.

11. Section 334600 "Subdrainage" for valves applicable only to this piping.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of valve indicated.

1.3 QUALITY ASSURANCE

A. ASME Compliance: ASME B16.10 and ASME B16.34 for ferrous valve dimensions and design criteria.

B. NSF Compliance: NSF 61 for valve materials for potable-water service.

PART 2 -  PRODUCTS

2.1 GENERAL REQUIREMENTS FOR VALVES

Plumbing valve applications specified in this Section are limited to NPS 12 (DN 300).

A. Refer to valve schedule articles for applications of valves.

Caution: Revise pressure ratings and insert temperature ratings in valve articles if valves with higher ratings are required.

B. Valve Pressure and Temperature Ratings: Not less than indicated and as required for system pressures and temperatures.

C. Valve Sizes: Same as upstream piping unless otherwise indicated.

D. Valve Actuator Types:

1. Gear Actuator: For quarter-turn valves NPS 8 (DN 200) and larger.

2. Handwheel: For valves other than quarter-turn types.

3. Handlever: For quarter-turn valves NPS 6 (DN 150) and smaller[ except plug valves].

4. Chainwheel: Device for attachment to valve handwheel, stem, or other actuator; of size and with chain for mounting height, as indicated in the "Valve Installation" Article.

E. Valves in Insulated Piping: With 2-inch (50-mm) stem extensions and the following features:

1. Gate Valves: With rising stem.

2. Ball Valves: With extended operating handle of non-thermal-conductive material, and protective sleeve that allows operation of valve without breaking the vapor seal or disturbing insulation.

3. Butterfly Valves: With extended neck.

F. Valve-End Connections:

1. Flanged: With flanges according to ASME B16.1 for iron valves.

2. Solder Joint: With sockets according to ASME B16.18.

3. Threaded: With threads according to ASME B1.20.1.

2.2 BRASS BALL VALVES

Retain one or more of three paragraphs in this article if brass ball valves are required. MSS SP-110 covers both brass and bronze, copper-alloy ball valves NPS 1/4 to NPS 4 (DN 8 to DN 100). See the Evaluations and manufacturers' catalogs before selecting either brass or bronze ball valves or including both.

A. One-Piece, Reduced-Port, Brass Ball Valves with Brass Trim:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Kitz Corporation.

b. <Insert manufacturer's name>.

2. Description:

a. Standard: MSS SP-110.

b. CWP Rating: 400 psig (2760 kPa).

c. Body Design: One piece.

d. Body Material: Forged brass.

e. Ends: Threaded.

f. Seats: PTFE or TFE.

g. Stem: Brass.

h. Ball: Chrome-plated brass.

i. Port: Reduced.

B. Two-Piece, Full-Port, Brass Ball Valves with Brass Trim:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Crane Co.; Crane Valve Group; Crane Valves.

b. Crane Co.; Crane Valve Group; Jenkins Valves.

c. DynaQuip Controls.

d. Flow-Tek, Inc.; a subsidiary of Bray International, Inc.

e. Hammond Valve.

f. Jamesbury; a subsidiary of Metso Automation.

g. Jomar International, LTD.

h. Kitz Corporation.

i. Legend Valve.

j. Marwin Valve; a division of Richards Industries.

k. Milwaukee Valve Company.

l. NIBCO INC.

m. Red-White Valve Corporation.

n. RuB Inc.

o. <Insert manufacturer's name>.

2. Description:

a. Standard: MSS SP-110.

b. SWP Rating: 150 psig (1035 kPa).

c. CWP Rating: 600 psig (4140 kPa).

d. Body Design: Two piece.

e. Body Material: Forged brass.

f. Ends: Threaded.

g. Seats: PTFE or TFE.

h. Stem: Brass.

i. Ball: Chrome-plated brass.

j. Port: Full.

C. Two-Piece, Regular-Port, Brass Ball Valves with Brass Trim:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Hammond Valve.

b. Jamesbury; a subsidiary of Metso Automation.

c. Legend Valve.

d. Marwin Valve; a division of Richards Industries.

e. Milwaukee Valve Company.

f. <Insert manufacturer's name>.

2. Description:

a. Standard: MSS SP-110.

b. SWP Rating: 150 psig (1035 kPa).

c. CWP Rating: 600 psig (4140 kPa).

d. Body Design: Two piece.

e. Body Material: Forged brass.

f. Ends: Threaded.

g. Seats: PTFE or TFE.

h. Stem: Brass.

i. Ball: Chrome-plated brass.

j. Port: Regular.

2.3 BRONZE BALL VALVES

Retain one or more of three paragraphs in this article if bronze ball valves are required. MSS SP-110 covers both brass and bronze, copper-alloy ball valves NPS 1/4 to NPS 4 (DN 8 to DN 100). See the Evaluations and manufacturers' catalogs before selecting either brass or bronze ball valves or including both.

A. One-Piece, Reduced-Port, Bronze Ball Valves with Bronze Trim:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. American Valve, Inc.

b. Conbraco Industries, Inc.; Apollo Valves.

c. NIBCO INC.

d. <Insert manufacturer's name>.

2. Description:

a. Standard: MSS SP-110.

b. CWP Rating: 400 psig (2760 kPa).

c. Body Design: One piece.

d. Body Material: Bronze.

e. Ends: Threaded.

f. Seats: PTFE or TFE.

g. Stem: Bronze.

h. Ball: Chrome-plated brass.

i. Port: Reduced.

B. Two-Piece, Full-Port, Bronze Ball Valves with Bronze Trim:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. American Valve, Inc.

b. Conbraco Industries, Inc.; Apollo Valves.

c. Crane Co.; Crane Valve Group; Crane Valves.

d. Hammond Valve.

e. Lance Valves; a division of Advanced Thermal Systems, Inc.

f. Legend Valve.

g. Milwaukee Valve Company.

h. NIBCO INC.

i. Red-White Valve Corporation.

j. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

k. <Insert manufacturer's name>.

2. Description:

a. Standard: MSS SP-110.

b. SWP Rating: 150 psig (1035 kPa).

c. CWP Rating: 600 psig (4140 kPa).

d. Body Design: Two piece.

e. Body Material: Bronze.

f. Ends: Threaded.

g. Seats: PTFE or TFE.

h. Stem: Bronze.

i. Ball: Chrome-plated brass.

j. Port: Full.

C. Two-Piece, Regular-Port, Bronze Ball Valves with Bronze Trim:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. American Valve, Inc.

b. Conbraco Industries, Inc.; Apollo Valves.

c. Crane Co.; Crane Valve Group; Jenkins Valves.

d. Crane Co.; Crane Valve Group; Stockham Division.

e. DynaQuip Controls.

f. Hammond Valve.

g. Lance Valves; a division of Advanced Thermal Systems, Inc.

h. Milwaukee Valve Company.

i. NIBCO INC.

j. <Insert manufacturer's name>.

2. Description:

a. Standard: MSS SP-110.

b. SWP Rating: 150 psig (1035 kPa).

c. CWP Rating: 600 psig (4140 kPa).

d. Body Design: Two piece.

e. Body Material: Bronze.

f. Ends: Threaded.

g. Seats: PTFE or TFE.

h. Stem: Bronze.

i. Ball: Chrome-plated brass.

j. Port: Regular.

2.4 IRON, SINGLE-FLANGE BUTTERFLY VALVES

Retain one or more of four paragraphs in this article if iron, single-flange butterfly valves are required. MSS SP-67 covers iron, single-flange butterfly valves NPS 1-1/2 to NPS 72 (DN 40 to DN 1800).

A. 200 CWP, Iron, Single-Flange Butterfly Valves with EPDM Seat and Aluminum-Bronze Disc:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. ABZ Valve and Controls; a division of ABZ Manufacturing, Inc.

b. Conbraco Industries, Inc.; Apollo Valves.

c. Cooper Cameron Valves; a division of Cooper Cameron Corporation.

d. Crane Co.; Crane Valve Group; Jenkins Valves.

e. Crane Co.; Crane Valve Group; Stockham Division.

f. DeZurik Water Controls.

g. Flo Fab Inc.

h. Hammond Valve.

i. Kitz Corporation.

j. Legend Valve.

k. Milwaukee Valve Company.

l. NIBCO INC.

m. Norriseal; a Dover Corporation company.

n. Red-White Valve Corporation.

o. Spence Strainers International; a division of CIRCOR International, Inc.

p. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

q. <Insert manufacturer's name>.

2. Description:

a. Standard: MSS SP-67, Type I.

b. CWP Rating: 200 psig (1380 kPa).

c. Body Design: Lug type; suitable for bidirectional dead-end service at rated pressure without use of downstream flange.

d. Body Material: ASTM A 126, cast iron or ASTM A 536, ductile iron.

e. Seat: EPDM.

f. Stem: One- or two-piece stainless steel.

g. Disc: Aluminum bronze.

B. 200 CWP, Iron, Single-Flange Butterfly Valves with NBR Seat and Aluminum-Bronze Disc:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. ABZ Valve and Controls; a division of ABZ Manufacturing, Inc.

b. Conbraco Industries, Inc.; Apollo Valves.

c. Cooper Cameron Valves; a division of Cooper Cameron Corporation.

d. Crane Co.; Crane Valve Group; Jenkins Valves.

e. Crane Co.; Crane Valve Group; Stockham Division.

f. DeZurik Water Controls.

g. Flo Fab Inc.

h. Hammond Valve.

i. Kitz Corporation.

j. Legend Valve.

k. Milwaukee Valve Company.

l. NIBCO INC.

m. Norriseal; a Dover Corporation company.

n. Red-White Valve Corporation.

o. Spence Strainers International; a division of CIRCOR International, Inc.

p. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

q. <Insert manufacturer's name>.

2. Description:

a. Standard: MSS SP-67, Type I.

b. CWP Rating: 200 psig (1380 kPa).

c. Body Design: Lug type; suitable for bidirectional dead-end service at rated pressure without use of downstream flange.

d. Body Material: ASTM A 126, cast iron or ASTM A 536, ductile iron.

e. Seat: NBR.

f. Stem: One- or two-piece stainless steel.

g. Disc: Aluminum bronze.

C. 200 CWP, Iron, Single-Flange Butterfly Valves with EPDM Seat and Ductile-Iron Disc:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. ABZ Valve and Controls; a division of ABZ Manufacturing, Inc.

b. American Valve, Inc.

c. Conbraco Industries, Inc.; Apollo Valves.

d. Cooper Cameron Valves; a division of Cooper Cameron Corporation.

e. Crane Co.; Crane Valve Group; Center Line.

f. Crane Co.; Crane Valve Group; Stockham Division.

g. DeZurik Water Controls.

h. Flo Fab Inc.

i. Hammond Valve.

j. Kitz Corporation.

k. Legend Valve.

l. Milwaukee Valve Company.

m. Mueller Steam Specialty; a division of SPX Corporation.

n. NIBCO INC.

o. Norriseal; a Dover Corporation company.

p. Spence Strainers International; a division of CIRCOR International, Inc.

q. Sure Flow Equipment Inc.

r. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

s. <Insert manufacturer's name>.

2. Description:

a. Standard: MSS SP-67, Type I.

b. CWP Rating: 200 psig (1380 kPa).

c. Body Design: Lug type; suitable for bidirectional dead-end service at rated pressure without use of downstream flange.

d. Body Material: ASTM A 126, cast iron or ASTM A 536, ductile iron.

e. Seat: EPDM.

f. Stem: One- or two-piece stainless steel.

g. Disc: Nickel-plated[ or -coated] ductile iron.

D. 200 CWP, Iron, Single-Flange Butterfly Valves with NBR Seat and Ductile-Iron Disc:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. ABZ Valve and Controls; a division of ABZ Manufacturing, Inc.

b. American Valve, Inc.

c. Conbraco Industries, Inc.; Apollo Valves.

d. Cooper Cameron Valves; a division of Cooper Cameron Corporation.

e. Crane Co.; Crane Valve Group; Center Line.

f. Crane Co.; Crane Valve Group; Stockham Division.

g. DeZurik Water Controls.

h. Flo Fab Inc.

i. Hammond Valve.

j. Kitz Corporation.

k. Legend Valve.

l. Milwaukee Valve Company.

m. Mueller Steam Specialty; a division of SPX Corporation.

n. NIBCO INC.

o. Norriseal; a Dover Corporation company.

p. Spence Strainers International; a division of CIRCOR International, Inc.

q. Sure Flow Equipment Inc.

r. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

s. <Insert manufacturer's name>.

2. Description:

a. Standard: MSS SP-67, Type I.

b. CWP Rating: 200 psig (1380 kPa).

c. Body Design: Lug type; suitable for bidirectional dead-end service at rated pressure without use of downstream flange.

d. Body Material: ASTM A 126, cast iron or ASTM A 536, ductile iron.

e. Seat: NBR.

f. Stem: One- or two-piece stainless steel.

g. Disc: Nickel-plated[ or -coated] ductile iron.

2.5 BRONZE SWING CHECK VALVES

Retain one or both paragraphs in this article if bronze swing check valves are required. MSS SP-80 covers bronze swing check valves NPS 1/4 to NPS 3 (DN 8 to DN 80).

A. Class 125, Bronze Swing Check Valves with Bronze Disc:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. American Valve, Inc.

b. Crane Co.; Crane Valve Group; Crane Valves.

c. Crane Co.; Crane Valve Group; Jenkins Valves.

d. Crane Co.; Crane Valve Group; Stockham Division.

e. Hammond Valve.

f. Kitz Corporation.

g. Milwaukee Valve Company.

h. NIBCO INC.

i. Powell Valves.

j. Red-White Valve Corporation.

k. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

l. Zy-Tech Global Industries, Inc.

m. <Insert manufacturer's name>.

2. Description:

a. Standard: MSS SP-80, Type 3.

b. CWP Rating: 200 psig (1380 kPa).

c. Body Design: Horizontal flow.

d. Body Material: ASTM B 62, bronze.

e. Ends: Threaded.

f. Disc: Bronze.

B. Class 125, Bronze Swing Check Valves with Nonmetallic Disc:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Crane Co.; Crane Valve Group; Crane Valves.

b. Crane Co.; Crane Valve Group; Jenkins Valves.

c. Crane Co.; Crane Valve Group; Stockham Division.

d. Hammond Valve.

e. Kitz Corporation.

f. Milwaukee Valve Company.

g. NIBCO INC.

h. Red-White Valve Corporation.

i. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

j. <Insert manufacturer's name>.

2. Description:

a. Standard: MSS SP-80, Type 4.

b. CWP Rating: 200 psig (1380 kPa).

c. Body Design: Horizontal flow.

d. Body Material: ASTM B 62, bronze.

e. Ends: Threaded.

f. Disc: PTFE or TFE.

2.6 IRON SWING CHECK VALVES

Retain one or both paragraphs in this article if iron swing check valves are required. MSS SP-71 covers iron swing check valves NPS 2 to NPS 24 (DN 50 to DN 600).

A. Class 125, Iron Swing Check Valves with Metal Seats:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Crane Co.; Crane Valve Group; Crane Valves.

b. Crane Co.; Crane Valve Group; Jenkins Valves.

c. Crane Co.; Crane Valve Group; Stockham Division.

d. Hammond Valve.

e. Kitz Corporation.

f. Legend Valve.

g. Milwaukee Valve Company.

h. NIBCO INC.

i. Powell Valves.

j. Red-White Valve Corporation.

k. Sure Flow Equipment Inc.

l. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

m. Zy-Tech Global Industries, Inc.

n. <Insert manufacturer's name>.

2. Description:

a. Standard: MSS SP-71, Type I.

b. CWP Rating: 200 psig (1380 kPa).

c. Body Design: Clear or full waterway.

d. Body Material: ASTM A 126, gray iron with bolted bonnet.

e. Ends: Flanged.

f. Trim: Bronze.

g. Gasket: Asbestos free.

B. Class 125, Iron Swing Check Valves with Nonmetallic-to-Metal Seats:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Crane Co.; Crane Valve Group; Crane Valves.

b. Crane Co.; Crane Valve Group; Stockham Division.

c. <Insert manufacturer's name>.

2. Description:

a. Standard: MSS SP-71, Type I.

b. CWP Rating: 200 psig (1380 kPa).

c. Body Design: Clear or full waterway.

d. Body Material: ASTM A 126, gray iron with bolted bonnet.

e. Ends: Flanged.

f. Trim: Composition.

g. Seat Ring: Bronze.

h. Disc Holder: Bronze.

i. Disc: PTFE or TFE.

j. Gasket: Asbestos free.

2.7 IRON SWING CHECK VALVES WITH CLOSURE CONTROL

A. Class 125, Iron Swing Check Valves with Lever- and Spring-Closure Control:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. NIBCO INC.

b. <Insert manufacturer's name>.

2. Description:

a. Standard: MSS SP-71, Type I.

b. CWP Rating: 200 psig (1380 kPa).

c. Body Design: Clear or full waterway.

d. Body Material: ASTM A 126, gray iron with bolted bonnet.

e. Ends: Flanged.

f. Trim: Bronze.

g. Gasket: Asbestos free.

h. Closure Control: Factory-installed, exterior lever and spring.

B. Class 125, Iron Swing Check Valves with Lever- and Weight-Closure Control:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Crane Co.; Crane Valve Group; Crane Valves.

b. Crane Co.; Crane Valve Group; Jenkins Valves.

c. Crane Co.; Crane Valve Group; Stockham Division.

d. Hammond Valve.

e. Milwaukee Valve Company.

f. NIBCO INC.

g. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

h. <Insert manufacturer's name>.

2. Description:

a. Standard: MSS SP-71, Type I.

b. CWP Rating: 200 psig (1380 kPa).

c. Body Design: Clear or full waterway.

d. Body Material: ASTM A 126, gray iron with bolted bonnet.

e. Ends: Flanged.

f. Trim: Bronze.

g. Gasket: Asbestos free.

h. Closure Control: Factory-installed, exterior lever and weight.

2.8 BRONZE GATE VALVES

Retain one or both paragraphs in this article if bronze gate valves are required. MSS SP-80 covers bronze gate valves NPS 1/4 to NPS 3 (DN 8 to DN 80).

A. Class 125, NRS Bronze Gate Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. American Valve, Inc.

b. Crane Co.; Crane Valve Group; Crane Valves.

c. Crane Co.; Crane Valve Group; Jenkins Valves.

d. Crane Co.; Crane Valve Group; Stockham Division.

e. Hammond Valve.

f. Kitz Corporation.

g. Milwaukee Valve Company.

h. NIBCO INC.

i. Powell Valves.

j. Red-White Valve Corporation.

k. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

l. Zy-Tech Global Industries, Inc.

m. <Insert manufacturer's name>.

2. Description:

a. Standard: MSS SP-80, Type 1.

b. CWP Rating: 200 psig (1380 kPa).

c. Body Material: ASTM B 62, bronze with integral seat and screw-in bonnet.

d. Ends: Threaded[ or solder joint].

e. Stem: Bronze.

f. Disc: Solid wedge; bronze.

g. Packing: Asbestos free.

h. Handwheel: Malleable iron[, bronze, or aluminum].

B. Class 125, RS Bronze Gate Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. American Valve, Inc.

b. Crane Co.; Crane Valve Group; Crane Valves.

c. Crane Co.; Crane Valve Group; Jenkins Valves.

d. Crane Co.; Crane Valve Group; Stockham Division.

e. Hammond Valve.

f. Kitz Corporation.

g. Milwaukee Valve Company.

h. NIBCO INC.

i. Powell Valves.

j. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

k. Zy-Tech Global Industries, Inc.

l. <Insert manufacturer's name>.

2. Description:

a. Standard: MSS SP-80, Type 2.

b. CWP Rating: 200 psig (1380 kPa).

c. Body Material: ASTM B 62, bronze with integral seat and screw-in bonnet.

d. Ends: Threaded[ or solder joint].

e. Stem: Bronze.

f. Disc: Solid wedge; bronze.

g. Packing: Asbestos free.

h. Handwheel: Malleable iron[, bronze, or aluminum].

2.9 IRON GATE VALVES

Retain one or both paragraphs in this article if iron gate valves are required. MSS SP-70 covers iron gate valves NPS 2 to NPS 48 (DN 50 to DN 1200).

A. Class 125, NRS, Iron Gate Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Crane Co.; Crane Valve Group; Crane Valves.

b. Crane Co.; Crane Valve Group; Jenkins Valves.

c. Crane Co.; Crane Valve Group; Stockham Division.

d. Flo Fab Inc.

e. Hammond Valve.

f. Kitz Corporation.

g. Legend Valve.

h. Milwaukee Valve Company.

i. NIBCO INC.

j. Powell Valves.

k. Red-White Valve Corporation.

l. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

m. Zy-Tech Global Industries, Inc.

n. <Insert manufacturer's name>.

2. Description:

a. Standard: MSS SP-70, Type I.

b. CWP Rating: 200 psig (1380 kPa).

c. Body Material: ASTM A 126, gray iron with bolted bonnet.

d. Ends: Flanged.

e. Trim: Bronze.

f. Disc: Solid wedge.

g. Packing and Gasket: Asbestos free.

B. Class 125, OS&Y, Iron Gate Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Crane Co.; Crane Valve Group; Crane Valves.

b. Crane Co.; Crane Valve Group; Jenkins Valves.

c. Crane Co.; Crane Valve Group; Stockham Division.

d. Flo Fab Inc.

e. Hammond Valve.

f. Kitz Corporation.

g. Legend Valve.

h. Milwaukee Valve Company.

i. NIBCO INC.

j. Powell Valves.

k. Red-White Valve Corporation.

l. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

m. Zy-Tech Global Industries, Inc.

n. <Insert manufacturer's name>.

2. Description:

a. Standard: MSS SP-70, Type I.

b. CWP Rating: 200 psig (1380 kPa).

c. Body Material: ASTM A 126, gray iron with bolted bonnet.

d. Ends: Flanged.

e. Trim: Bronze.

f. Disc: Solid wedge.

g. Packing and Gasket: Asbestos free.

2.10 BRONZE GLOBE VALVES

Retain one or both paragraphs in this article if bronze globe valves are required. MSS SP-80 covers bronze globe valves NPS 1/4 to NPS 3 (DN 8 to DN 80).

A. Class 125, Bronze Globe Valves with Bronze Disc:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Crane Co.; Crane Valve Group; Crane Valves.

b. Crane Co.; Crane Valve Group; Stockham Division.

c. Hammond Valve.

d. Kitz Corporation.

e. Milwaukee Valve Company.

f. NIBCO INC.

g. Powell Valves.

h. Red-White Valve Corporation.

i. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

j. Zy-Tech Global Industries, Inc.

k. <Insert manufacturer's name>.

2. Description:

a. Standard: MSS SP-80, Type 1.

b. CWP Rating: 200 psig (1380 kPa).

c. Body Material: ASTM B 62, bronze with integral seat and screw-in bonnet.

d. Ends: Threaded[ or solder joint].

e. Stem and Disc: Bronze.

f. Packing: Asbestos free.

g. Handwheel: Malleable iron[, bronze, or aluminum].

B. Class 125, Bronze Globe Valves with Nonmetallic Disc:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Crane Co.; Crane Valve Group; Crane Valves.

b. Crane Co.; Crane Valve Group; Stockham Division.

c. NIBCO INC.

d. Red-White Valve Corporation.

e. <Insert manufacturer's name>.

2. Description:

a. Standard: MSS SP-80, Type 2.

b. CWP Rating: 200 psig (1380 kPa).

c. Body Material: ASTM B 62, bronze with integral seat and screw-in bonnet.

d. Ends: Threaded[ or solder joint].

e. Stem: Bronze.

f. Disc: PTFE or TFE.

g. Packing: Asbestos free.

h. Handwheel: Malleable iron[, bronze, or aluminum].

2.11 IRON GLOBE VALVES

Retain this article if iron globe valves are required. MSS SP-85 covers iron globe valves NPS 2 to NPS 12 (DN 50 to DN 300).

A. Class 125, Iron Globe Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Crane Co.; Crane Valve Group; Crane Valves.

b. Crane Co.; Crane Valve Group; Jenkins Valves.

c. Crane Co.; Crane Valve Group; Stockham Division.

d. Hammond Valve.

e. Kitz Corporation.

f. Milwaukee Valve Company.

g. NIBCO INC.

h. Powell Valves.

i. Red-White Valve Corporation.

j. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

k. Zy-Tech Global Industries, Inc.

l. <Insert manufacturer's name>.

2. Description:

a. Standard: MSS SP-85, Type I.

b. CWP Rating: 200 psig (1380 kPa).

c. Body Material: ASTM A 126, gray iron with bolted bonnet.

d. Ends: Flanged.

e. Trim: Bronze.

f. Packing and Gasket: Asbestos free.

2.12 CHAINWHEELS

A. Description: Valve actuation assembly with sprocket rim, brackets, and chain.

1. Brackets: Type, number, size, and fasteners required to mount actuator on valve.

Retain first subparagraph below for ball, butterfly, and plug valves.

2. Attachment: For connection to butterfly valve stems.

3. Sprocket Rim with Chain Guides: Ductile iron, of type and size required for valve.[ Include zinc coating.]

4. Chain: Hot-dip, galvanized steel, of size required to fit sprocket rim.

PART 3 -  EXECUTION

3.1 VALVE INSTALLATION

A. Install valves with unions or flanges at each piece of equipment arranged to allow service, maintenance, and equipment removal without system shutdown.

B. Locate valves for easy access and provide separate support where necessary.

C. Install valves in horizontal piping with stem at or above center of pipe.

D. Install valves in position to allow full stem movement.

E. Install chainwheels on operators for [butterfly] [gate] [and] [globe] valves [NPS 4 (DN 100)] <Insert size> and larger and more than [96 inches (2400 mm)] <Insert dimension> above floor. Extend chains to [60 inches (1520 mm)] <Insert dimension> above finished floor.

1. Install swing check valves for proper direction of flow and in horizontal position with hinge pin level.

3.2 ADJUSTING

A. Adjust or replace valve packing after piping systems have been tested and put into service but before final adjusting and balancing. Replace valves if persistent leaking occurs.

3.3 GENERAL REQUIREMENTS FOR VALVE APPLICATIONS

The Section Text is arranged to provide bronze or brass valves in NPS 2 (DN 50) and smaller and iron valves in NPS 2-1/2 to NPS 12 (DN 65 to DN 300).

Retain and revise valve applications in paragraphs and schedules below. Coordinate with valves specified in Part 2.

A. If valve applications are not indicated, use the following:

1. Shutoff Service: Ball, butterfly[, or gate] valves.

2. Throttling Service: [Globe] [or ball] [or butterfly] [, ball, or butterfly] valves.

3. Pump-Discharge Check Valves:

a. NPS 2 (DN 50) and Smaller: Bronze swing check valves with [bronze] [or] [nonmetallic] disc.

b. NPS 2-1/2 (DN 65) and Larger for Domestic Water: Iron swing check valves with lever and weight or with spring.

c. NPS 2-1/2 (DN 65) and Larger for Sanitary Waste and Storm Drainage: Iron swing check valves with lever and weight or spring.

B. If valves with specified SWP classes or CWP ratings are not available, the same types of valves with higher SWP class or CWP ratings may be substituted.

C. Select valves, except wafer types, with the following end connections:

1. For Copper Tubing, NPS 2 (DN 50) and Smaller: Threaded ends except where solder-joint valve-end option is indicated in valve schedules below.

2. For Copper Tubing, NPS 2-1/2 to NPS 4 (DN 65 to DN 100): Flanged ends except where threaded valve-end option is indicated in valve schedules below.

3. For Copper Tubing, NPS 5 (DN 125) and Larger: Flanged ends.

4. For Steel Piping, NPS 2 (DN 50) and Smaller: Threaded ends.

5. For Steel Piping, NPS 2-1/2 to NPS 4 (DN 65 to DN 100): Flanged ends except where threaded valve-end option is indicated in valve schedules below.

6. For Steel Piping, NPS 5 (DN 125) and Larger: Flanged ends.

3.4 LOW-PRESSURE, COMPRESSED-AIR VALVE SCHEDULE (150 PSIG (1035 kPa) OR LESS)

A. Pipe NPS 2 (DN 50) and Smaller:

Retain first subparagraph below if solder-joint valve ends are permitted for this application.

1. Bronze[ and Brass] Valves: May be provided with solder-joint ends instead of threaded ends.

Retain only valve types, in subparagraphs below, required for Project.

2. Ball Valves: [One] [Two] piece, [full] [regular] [reduced] port, [brass] [or] [bronze] with [brass] [bronze] trim.

3. Bronze Swing Check Valves: Class 125, [bronze] [nonmetallic] disc.

4. Bronze Gate Valves: Class 125, [NRS] [RS].

B. Pipe NPS 2-1/2 (DN 65) and Larger:

Retain first subparagraph below if threaded valve ends are permitted for this application.

1. Iron Valves, NPS 2-1/2 to NPS 4 (DN 65 to NPS 100): May be provided with threaded ends instead of flanged ends.

Retain only valve types, in subparagraphs below, required for Project.

2. Iron, Single-Flange Butterfly Valves: 200 CWP, NBR seat, [aluminum-bronze] [ductile-iron] disc.

3. Iron Swing Check Valves: Class 125, [metal] [nonmetallic-to-metal] seats.

4. Iron Gate Valves: Class 125, [NRS] [OS&Y].

3.5 HIGH-PRESSURE, COMPRESSED-AIR VALVE SCHEDULE (150 TO 200 PSIG (1035 TO 1380 kPa))

A. Pipe NPS 2 (DN 50) and Smaller:

Retain first subparagraph below if solder-joint valve ends are permitted for this application.

1. Bronze[ and Brass] Valves: May be provided with solder-joint ends instead of threaded ends.

2. Ball Valves: [One] [Two] piece, [full] [regular] [reduced] port, [brass] [or] [bronze] with [brass] [bronze] trim.

3. Bronze Swing Check Valves: Class 125, [bronze] [nonmetallic] disc.

4. Bronze Gate Valves: Class 125, [NRS] [RS].

B. Pipe NPS 2-1/2 (DN 65) and Larger:

Retain first subparagraph below if threaded valve ends are permitted for this application.

1. Iron Valves, NPS 2-1/2 to NPS 4 (DN 65 to NPS 100): May be provided with threaded ends instead of flanged ends.

Retain only valve types, in subparagraphs below, required for Project.

2. Iron, Single-Flange Butterfly Valves: 200 CWP, NBR seat, [aluminum-bronze] [ductile-iron] disc.

3. Iron Swing Check Valves: Class 125, [metal] [nonmetallic-to-metal] seats.

4. Iron Gate Valves: Class 125, [NRS] [OS&Y].

3.6 DOMESTIC, HOT- AND COLD-WATER VALVE SCHEDULE

A. Pipe NPS 2 (DN 50) and Smaller:

Retain first subparagraph below if solder-joint valve ends are permitted for this application.

1. Bronze[ and Brass] Valves: May be provided with solder-joint ends instead of threaded ends.

Retain only valve types, in subparagraphs below, required for Project.

2. Bronze Angle Valves: Class 125, [bronze] [nonmetallic] disc.

3. Ball Valves: [One] [Two] piece, [full] [regular] [reduced] port, [brass] [or] [bronze] with [brass] [bronze] trim.

4. Bronze Swing Check Valves: [Class 125], [bronze] [nonmetallic] disc.

5. Bronze Gate Valves: Class 125, [NRS] [RS].

6. Bronze Globe Valves: Class 125, [bronze] [nonmetallic] disc.

B. Pipe NPS 2-1/2 (DN 65) and Larger:

Retain first subparagraph below if threaded valve ends are permitted for this application.

1. Iron Valves, NPS 2-1/2 to NPS 4 (DN 65 to NPS 100): May be provided with threaded ends instead of flanged ends.

Retain only valve types, in subparagraphs below, required for Project.

2. Iron, Single-Flange Butterfly Valves: 200 CWP, [EPDM] [NBR] seat, [aluminum-bronze] [ductile-iron] disc.

Retain one or more of first two subparagraphs below and indicate location of each type on Drawings.

3. Iron Swing Check Valves: Class 125, [metal] [nonmetallic-to-metal] seats.

4. Iron Swing Check Valves with Closure Control: Class 125, lever and [spring] [weight].

5. Iron Gate Valves: [Class 125], [NRS] [OS&Y].

6. Iron Globe Valves: Class 125.

3.7 [SANITARY-WASTE] [AND] [STORM-DRAINAGE] VALVE SCHEDULE

A. Pipe NPS 2 (DN 50) and Smaller:

Retain first subparagraph below if solder-joint valve ends are permitted for this application.

1. Bronze[ and Brass] Valves: May be provided with solder-joint ends instead of threaded ends.

Retain only valve types, in subparagraphs below, required for Project.

2. Ball Valves: [One] [Two] piece, [full] [regular] [reduced] port, [brass] [or] [bronze] with [brass] [bronze] trim.

3. Bronze Swing Check Valves: Class 125, [bronze] [nonmetallic] disc.

4. Bronze Gate Valves: Class 125, [NRS] [RS].

5. Bronze Globe Valves: Class 125, [bronze] [nonmetallic] disc.

B. Pipe NPS 2-1/2 (DN 65) and Larger:

Retain first subparagraph below if threaded valve ends are permitted for this application.

1. Iron Valves, NPS 2-1/2 to NPS 4 (DN 65 to NPS 100): May be provided with threaded ends instead of flanged ends.

Retain one or more of first two subparagraphs below and indicate location of each type on Drawings.

2. Iron Swing Check Valves: Class 125, [metal] [nonmetallic-to-metal] seats.

3. Iron Swing Check Valves with Closure Control: Class 125, lever and [spring] [weight].

4. Iron Gate Valves: Class 125, [NRS] [OS&Y].

5. Iron Globe Valves: Class 125.

END OF SECTION 220523

	GENERAL-DUTY VALVES FOR PLUMBING PIPING
	220523 - 1



