Copyright 2011 AIA
MasterSpec Professional
09/11

Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 220548 - VIBRATION AND SEISMIC CONTROLS FOR PLUMBING PIPING AND EQUIPMENT
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Elastomeric isolation pads.

2. Elastomeric isolation mounts.

3. Restrained elastomeric isolation mounts.

4. Open-spring isolators.

5. Housed-spring isolators.

6. Restrained-spring isolators.

7. Housed-restrained-spring isolators.

8. Pipe-riser resilient supports.

9. Resilient pipe guides.

10. Elastomeric hangers.

11. Spring hangers.

12. Snubbers.

13. Restraint channel bracings.

14. Restraint cables.

15. Seismic-restraint accessories.

16. Mechanical anchor bolts.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product.

B. Delegated-Design Submittal: For each vibration isolation and seismic-restraint device.

1. Include design calculations and details for selecting vibration isolators and seismic restraints complying with performance requirements, design criteria, and analysis data signed and sealed by the qualified professional engineer responsible for their preparation.

1.3 INFORMATIONAL SUBMITTALS

Coordinate "Qualification Data" Paragraph below with qualification requirements in Section 014000 "Quality Requirements" and as may be supplemented in "Quality Assurance" Article.

A. Qualification Data: For professional engineer.

Retain "Welding certificates" Paragraph below if retaining "Welding Qualifications" Paragraph in "Quality Assurance" Article.

B. Welding certificates.

C. Field quality-control reports.

1.4 QUALITY ASSURANCE

A. Comply with seismic-restraint requirements in the IBC unless requirements in this Section are more stringent.

Retain "Welding Qualifications" Paragraph below if shop or field welding is required. If retaining, also retain "Welding certificates" Paragraph in "Informational Submittals" Article.

B. Welding Qualifications: Qualify procedures and personnel according to AWS D1.1/D1.1M, "Structural Welding Code - Steel."

C. Seismic-restraint devices shall have horizontal and vertical load testing and analysis and shall bear anchorage preapproval OPA number from OSHPD, preapproval by ICC-ES, or preapproval by another agency acceptable to authorities having jurisdiction, showing maximum seismic-restraint ratings. Ratings based on independent testing are preferred to ratings based on calculations. If preapproved ratings are unavailable, submittals based on independent testing are preferred. Calculations (including combining shear and tensile loads) to support seismic-restraint designs must be signed and sealed by a qualified professional engineer.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

2.1 PERFORMANCE REQUIREMENTS

A. Seismic-Restraint Loading:

Obtain values for items in subparagraphs below from Project structural engineer or from ASCE/SEI 7. If the code at Project site is other than the IBC or NFPA 5000, revise parameters to comply with applicable code.

Specify design spectral response acceleration at short periods (0.2 second) and at 1.0 second based on site class in "Site Class as Defined in the IBC" Subparagraph below. Typical values range from 2 to 200 percent. Design spectral response acceleration is required for seismic force calculations to size seismic restraints. For each seismic restraint, include component importance factor, component response modification factor, and component amplification factor in the Plumbing Vibration-Control and Seismic-Restraint Device Schedule on Drawings.

1. Site Class as Defined in the IBC: [A] [B] [C] [D] [E] [F].

In "Assigned Seismic Use Group or Building Category as Defined in the IBC" Subparagraph below, retain Seismic Use Group or Building Category for Project structure from three classifications defined in the IBC.

2. Assigned Seismic Use Group or Building Category as Defined in the IBC: [I] [II] [III].

Retain "Component Importance Factor," "Component Response Modification Factor," and "Component Amplification Factor" subparagraphs below if these values are not included in the Plumbing Vibration-Control and Seismic-Restraint Device Schedule on Drawings. Factors below often vary among supported equipment. However, it is possible to specify maximum values for these factors for various classes of equipment or for all equipment instead of scheduling each piece of equipment.

a. Component Importance Factor: [1.0] [1.5] <Insert value>.

b. Component Response Modification Factor: [1.5] [2.5] [3.5] [5.0] <Insert value>.

c. Component Amplification Factor: [1.0] [2.5] <Insert value>.

3. Design Spectral Response Acceleration at Short Periods (0.2 Second): <Insert number>.

4. Design Spectral Response Acceleration at 1.0-Second Period: <Insert number>.

2.2 ELASTOMERIC ISOLATION PADS

Copy "Elastomeric Isolation Pads" Paragraph below and re-edit for each product.

The configuration and materials of elastomeric isolation pads depend on the equipment being supported. It is possible to have more than one type of elastomeric isolation pad on the same Project. Insert Drawing designation for each elastomeric isolation pad type required. Use these designations on Drawings to identify each product.

A. Elastomeric Isolation Pads: <Insert drawing designation>.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Ace Mountings Co., Inc.

b. California Dynamics Corporation.

c. Isolation Technology, Inc.

d. Kinetics Noise Control, Inc.

e. Mason Industries, Inc.

f. Vibration Eliminator Co., Inc.

g. Vibration Isolation.

h. Vibration Mountings & Controls, Inc.

i. <Insert manufacturer's name>.

3. Fabrication: Single or multiple layers of sufficient durometer stiffness for uniform loading over pad area.

4. Size: Factory or field cut to match requirements of supported equipment.

Verify availability of various pad materials and their properties with manufacturers.

5. Pad Material: Oil and water resistant with elastomeric properties.

6. Surface Pattern: [Smooth] [Ribbed] [Waffle] pattern.

Retain first subparagraph below if pad is infused with synthetic fibers.

7. Infused nonwoven cotton or synthetic fibers.

Retain subparagraph below if galvanized-steel baseplates are adhered to the isolation pad to facilitate load distribution.

8. Load-bearing metal plates adhered to pads.

2.3 ELASTOMERIC ISOLATION MOUNTS

Copy "Double-Deflection, Elastomeric Isolation Mounts" Paragraph below and re-edit for each product.

The configuration and materials of elastomeric isolation mounts depend on the equipment being supported. It is possible to have more than one type of elastomeric isolation mount on the same Project. Insert drawing designation for each elastomeric isolation mount type required. Use these designations on Drawings to identify each product.

A. Double-Deflection, Elastomeric Isolation Mounts: <Insert drawing designation>.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Ace Mountings Co., Inc.

b. California Dynamics Corporation.

c. Isolation Technology, Inc.

d. Kinetics Noise Control, Inc.

e. Mason Industries, Inc.

f. Vibration Eliminator Co., Inc.

g. Vibration Isolation.

h. Vibration Mountings & Controls, Inc.

i. <Insert manufacturer's name>.

3. Mounting Plates:

a. Top Plate: Encapsulated steel load transfer top plates, factory drilled and threaded[ with threaded studs or bolts].

Retain "Baseplate" Subparagraph below if the elastomeric mount being specified has a baseplate.

b. Baseplate: Encapsulated steel bottom plates with holes provided for anchoring to support structure.

4. Elastomeric Material: Molded, oil-resistant rubber, neoprene, or other elastomeric material.

2.4 RESTRAINED ELASTOMERIC ISOLATION MOUNTS

Copy "Restrained Elastomeric Isolation Mounts" Paragraph below and re-edit for each product.

The configuration and materials of restrained elastomeric isolation mounts depend on the equipment being supported. It is possible to have more than one type of restrained elastomeric isolation mount on the same Project. Insert drawing designation for each restrained elastomeric isolation mount type required. Use these designations on Drawings to identify each product.

A. Restrained Elastomeric Isolation Mounts: <Insert drawing designation>.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Ace Mountings Co., Inc.

b. California Dynamics Corporation.

c. Isolation Technology, Inc.

d. Kinetics Noise Control, Inc.

e. Mason Industries, Inc.

f. Vibration Eliminator Co., Inc.

g. Vibration Isolation.

h. Vibration Mountings & Controls, Inc.

i. <Insert manufacturer's name>.

3. Description: All-directional isolator with seismic restraints containing two separate and opposing elastomeric elements that prevent central threaded element and attachment hardware from contacting the housing during normal operation.

a. Housing: Cast-ductile iron or welded steel.

b. Elastomeric Material: Molded, oil-resistant rubber, neoprene, or other elastomeric material.

2.5 OPEN-SPRING ISOLATORS

Copy "Freestanding, Laterally Stable, Open-Spring Isolators" Paragraph below and re-edit for each product.

The configuration and materials of open-spring isolators depend on the equipment being supported. It is possible to have more than one type of open-spring isolator on the same Project. Insert drawing designation for each open-spring isolator type required. Use these designations on Drawings to identify each product.

A. Freestanding, Laterally Stable, Open-Spring Isolators: <Insert drawing designation>.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Ace Mountings Co., Inc.

b. California Dynamics Corporation.

c. Isolation Technology, Inc.

d. Kinetics Noise Control, Inc.

e. Mason Industries, Inc.

f. Vibration Eliminator Co., Inc.

g. Vibration Isolation.

h. Vibration Mountings & Controls, Inc.

i. <Insert manufacturer's name>.

3. Outside Spring Diameter: Not less than 80 percent of the compressed height of the spring at rated load.

4. Minimum Additional Travel: 50 percent of the required deflection at rated load.

5. Lateral Stiffness: More than 80 percent of rated vertical stiffness.

6. Overload Capacity: Support 200 percent of rated load, fully compressed, without deformation or failure.

7. Baseplates: Factory-drilled steel plate for bolting to structure with an elastomeric isolator pad attached to the underside. Baseplates shall limit floor load to 500 psig (3447 kPa).

8. Top Plate and Adjustment Bolt: Threaded top plate with adjustment bolt and cap screw to fasten and level equipment.

2.6 HOUSED-SPRING ISOLATORS

Copy "Freestanding, Laterally Stable, Open-Spring Isolators in Two-Part Telescoping Housing" Paragraph below and re-edit for each product.

The configuration and materials of housed-spring isolators depend on the equipment being supported. It is possible to have more than one type of housed-spring isolator on the same Project. Insert drawing designation for each housed-spring isolator type required. Use these designations on Drawings to identify each product.

A. Freestanding, Laterally Stable, Open-Spring Isolators in Two-Part Telescoping Housing: <Insert drawing designation>.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Ace Mountings Co., Inc.

b. California Dynamics Corporation.

c. Isolation Technology, Inc.

d. Kinetics Noise Control, Inc.

e. Mason Industries, Inc.

f. Vibration Eliminator Co., Inc.

g. Vibration Isolation.

h. Vibration Mountings & Controls, Inc.

i. <Insert manufacturer's name>.

3. Outside Spring Diameter: Not less than 80 percent of the compressed height of the spring at rated load.

4. Minimum Additional Travel: 50 percent of the required deflection at rated load.

5. Lateral Stiffness: More than 80 percent of rated vertical stiffness.

6. Overload Capacity: Support 200 percent of rated load, fully compressed, without deformation or failure.

7. Two-Part Telescoping Housing: A steel top and bottom frame separated by an elastomeric material and enclosing the spring isolators.

a. Drilled base housing for bolting to structure with an elastomeric isolator pad attached to the underside. Bases shall limit floor load to 500 psig (3447 kPa).

b. Top housing with [attachment and leveling bolt] [threaded mounting holes and internal leveling device] [elastomeric pad].

2.7 RESTRAINED-SPRING ISOLATORS

Copy "Freestanding, Laterally Stable, Open-Spring Isolators with Vertical-Limit Stop Restraint" Paragraph below and re-edit for each product.

The configuration and materials of restrained-spring isolators depend on the equipment being supported. It is possible to have more than one type of restrained-spring isolator on the same Project. Insert drawing designation for each restrained-spring isolator type required. Use these designations on Drawings to identify each product.

A. Freestanding, Laterally Stable, Open-Spring Isolators with Vertical-Limit Stop Restraint: <Insert drawing designation>.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Ace Mountings Co., Inc.

b. California Dynamics Corporation.

c. Isolation Technology, Inc.

d. Kinetics Noise Control, Inc.

e. Mason Industries, Inc.

f. Vibration Eliminator Co., Inc.

g. Vibration Isolation.

h. Vibration Mountings & Controls, Inc.

i. <Insert manufacturer's name>.

3. Housing: Steel housing with vertical-limit stops to prevent spring extension due to weight being removed.

a. Base with holes for bolting to structure with an elastomeric isolator pad attached to the underside. Bases shall limit floor load to 500 psig (3447 kPa).

b. Top plate with [threaded mounting holes] [elastomeric pad].

c. Internal leveling bolt that acts as blocking during installation.

4. Restraint: Limit stop as required for equipment and authorities having jurisdiction.

5. Outside Spring Diameter: Not less than 80 percent of the compressed height of the spring at rated load.

6. Minimum Additional Travel: 50 percent of the required deflection at rated load.

7. Lateral Stiffness: More than 80 percent of rated vertical stiffness.

8. Overload Capacity: Support 200 percent of rated load, fully compressed, without deformation or failure.

2.8 HOUSED-RESTRAINED-SPRING ISOLATORS

Copy "Freestanding, Steel, Open-Spring Isolators with Vertical-Limit Stop Restraint in Two-Part Telescoping Housing" Paragraph below and re-edit for each product.

The configuration and materials of housed-restrained-spring isolators depend on the equipment being supported. It is possible to have more than one type of housed-restrained-spring isolator on the same Project. Insert drawing designation for each housed-restrained-spring isolator type required. Use these designations on Drawings to identify each product.

A. Freestanding, Steel, Open-Spring Isolators with Vertical-Limit Stop Restraint in Two-Part Telescoping Housing: <Insert drawing designation>.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Ace Mountings Co., Inc.

b. California Dynamics Corporation.

c. Isolation Technology, Inc.

d. Kinetics Noise Control, Inc.

e. Mason Industries, Inc.

f. Vibration Eliminator Co., Inc.

g. Vibration Isolation.

h. Vibration Mountings & Controls, Inc.

i. <Insert manufacturer's name>.

3. Two-Part Telescoping Housing: A steel top and bottom frame separated by an elastomeric material and enclosing the spring isolators. Housings are equipped with [adjustable] [non-adjustable] snubbers to limit vertical movement.

a. Drilled base housing for bolting to structure with an elastomeric isolator pad attached to the underside. Bases shall limit floor load to 500 psig (3447 kPa).

b. Threaded top housing with adjustment bolt and cap screw to fasten and level equipment.

4. Outside Spring Diameter: Not less than 80 percent of the compressed height of the spring at rated load.

5. Minimum Additional Travel: 50 percent of the required deflection at rated load.

6. Lateral Stiffness: More than 80 percent of rated vertical stiffness.

7. Overload Capacity: Support 200 percent of rated load, fully compressed, without deformation or failure.

2.9 PIPE-RISER RESILIENT SUPPORT

Copy "Description" Paragraph below and re-edit for each product.

The configuration and materials of pipe-riser resilient supports depend on the equipment being supported. It is possible to have more than one type of pipe-riser resilient support on the same Project. Insert drawing designation for each pipe-riser resilient support type required. Use these designations on Drawings to identify each product.

A. Description: All-directional, acoustical pipe anchor consisting of two steel tubes separated by a minimum 1/2-inch- (13-mm-) thick neoprene <Insert drawing designation>.

1. Vertical-Limit Stops: Steel and neoprene vertical-limit stops arranged to prevent vertical travel in both directions.

2. Maximum Load Per Support: 500 psig (3.45 MPa)on isolation material providing equal isolation in all directions.

2.10 RESILIENT PIPE GUIDES

Copy "Description" Paragraph below and re-edit for each product.

The configuration and materials of resilient pipe guides depend on the equipment being supported. It is possible to have more than one type of resilient pipe guide on the same Project. Insert drawing designation for each resilient pipe guide type required. Use these designations on Drawings to identify each product.

A. Description: Telescopic arrangement of two steel tubes or post and sleeve arrangement separated by a minimum 1/2-inch- (13-mm-) thick neoprene <Insert drawing designation>.

Retain "Factory-Set Height Guide with Shear Pin" Subparagraph below where vertical motion due to pipe expansion and contraction is required and clearances are not readily visible.

1. Factory-Set Height Guide with Shear Pin: Shear pin shall be removable and reinsertable to allow for selection of pipe movement. Guides shall be capable of motion to meet location requirements.

2.11 ELASTOMERIC HANGERS

Copy "Elastomeric Mount in a Steel Frame with Upper and Lower Steel Hanger Rods" Paragraph below and re-edit for each product.

The configuration and materials of elastomeric hangers depend on the equipment being supported. It is possible to have more than one type of elastomeric hanger on the same Project. Insert drawing designation for each elastomeric hanger type required. Use these designations on Drawings to identify each product.

A. Elastomeric Mount in a Steel Frame with Upper and Lower Steel Hanger Rods: <Insert drawing designation>.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Ace Mountings Co., Inc.

b. California Dynamics Corporation.

c. Isolation Technology, Inc.

d. Kinetics Noise Control, Inc.

e. Mason Industries, Inc.

f. Vibration Eliminator Co., Inc.

g. Vibration Mountings & Controls, Inc.

h. <Insert manufacturer's name>.

3. Frame: Steel, fabricated with a connection for an upper threaded hanger rod and an opening on the underside to allow for a maximum of 30 degrees of angular lower hanger-rod misalignment without binding or reducing isolation efficiency.

4. Dampening Element: Molded, oil-resistant rubber, neoprene, or other elastomeric material with a projecting bushing for the underside opening preventing steel to steel contact.

2.12 SPRING HANGERS

Copy "Combination Coil-Spring and Elastomeric-Insert Hanger with Spring and Insert in Compression" Paragraph below and re-edit for each product.

The configuration and materials of spring hangers depend on the equipment being supported. It is possible to have more than one type of spring hanger on the same Project. Insert drawing designation for each spring hanger type required. Use these designations on Drawings to identify each product.

A. Combination Coil-Spring and Elastomeric-Insert Hanger with Spring and Insert in Compression: <Insert drawing designation>.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Ace Mountings Co., Inc.

b. California Dynamics Corporation.

c. Kinetics Noise Control, Inc.

d. Mason Industries, Inc.

e. Vibration Eliminator Co., Inc.

f. Vibration Isolation.

g. Vibration Mountings & Controls, Inc.

h. <Insert manufacturer's name>.

3. Frame: Steel, fabricated for connection to threaded hanger rods and to allow for a maximum of 30 degrees of angular hanger-rod misalignment without binding or reducing isolation efficiency.

4. Outside Spring Diameter: Not less than 80 percent of the compressed height of the spring at rated load.

5. Minimum Additional Travel: 50 percent of the required deflection at rated load.

6. Lateral Stiffness: More than 80 percent of rated vertical stiffness.

7. Overload Capacity: Support 200 percent of rated load, fully compressed, without deformation or failure.

8. Elastomeric Element: Molded, oil-resistant rubber or neoprene. Steel-washer-reinforced cup to support spring and bushing projecting through bottom of frame.

Retain "Adjustable Vertical Stop" Subparagraph below if a vertical-limit stop is required.

9. Adjustable Vertical Stop: Steel washer with neoprene washer "up-stop" on lower threaded rod.

10. Self-centering hanger-rod cap to ensure concentricity between hanger rod and support spring coil.

2.13 SNUBBERS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Kinetics Noise Control, Inc.

2. Mason Industries, Inc.

3. Vibration Mountings & Controls, Inc.

4. <Insert manufacturer's name>.

C. Description: Factory fabricated using welded structural-steel shapes and plates, anchor bolts, and replaceable resilient isolation washers and bushings.

1. Anchor bolts for attaching to concrete shall be seismic-rated, drill-in, and stud-wedge or female-wedge type.

2. Resilient Isolation Washers and Bushings: Oil- and water-resistant neoprene.

3. Maximum 1/4-inch (6-mm) air gap, and minimum 1/4-inch- (6-mm-) thick resilient cushion.

Metal framing systems are specified in Section 220529 "Hangers and Supports for Plumbing Piping and Equipment."

2.14 RESTRAINT CHANNEL BRACINGS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Cooper B-Line, Inc.

2. Hilti, Inc.

3. Mason Industries, Inc.

4. Unistrut.

5. <Insert manufacturer's name>.

C. Description: MFMA-4, shop- or field-fabricated bracing assembly made of slotted steel channels with accessories for attachment to braced component at one end and to building structure at the other end and other matching components and with corrosion-resistant coating; rated in tension, compression, and torsion forces.

2.15 RESTRAINT CABLES

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Kinetics Noise Control, Inc.

2. Loos & Co., Inc.

3. Vibration Mountings & Controls, Inc.

4. <Insert manufacturer's name>.

C. Restraint Cables: [ASTM A 603 galvanized] [ASTM A 492 stainless]-steel cables. End connections made of steel assemblies with thimbles, brackets, swivel, and bolts designed for restraining cable service; with a minimum of two clamping bolts for cable engagement.

2.16 SEISMIC-RESTRAINT ACCESSORIES

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Cooper B-Line, Inc.

2. Kinetics Noise Control, Inc.

3. Mason Industries, Inc.

4. TOLCO.

5. <Insert manufacturer's name>.

Retain "Hanger-Rod Stiffener" Paragraph below for strengthening resistance of hanger rods against seismic forces that may cause buckling of rods; delete if detailed on Drawings. Use with either channel- or cable-type bracing assemblies when required to counter seismic forces. Detail fabrication and indicate locations on Drawings.

C. Hanger-Rod Stiffener: [Steel tube or steel slotted-support-system sleeve with internally bolted connections] [Reinforcing steel angle clamped] to hanger rod.

D. Bushings for Floor-Mounted Equipment Anchor Bolts: Neoprene bushings designed for rigid equipment mountings, and matched to type and size of anchor bolts and studs.

E. Bushing Assemblies for Wall-Mounted Equipment Anchorage: Assemblies of neoprene elements and steel sleeves designed for rigid equipment mountings, and matched to type and size of attachment devices used.

F. Resilient Isolation Washers and Bushings: One-piece, molded, oil- and water-resistant neoprene, with a flat washer face.

G. Mechanical Anchor Bolts: Drilled-in and stud-wedge or female-wedge type in zinc-coated steel for interior applications and stainless steel for exterior applications. Select anchor bolts with strength required for anchor and as tested according to ASTM E 488.

PART 3 -  EXECUTION

3.1 APPLICATIONS

A. Multiple Pipe Supports: Secure pipes to trapeze member with clamps approved for application by [an evaluation service member of ICC-ES] [OSHPD] [an agency acceptable to authorities having jurisdiction].

Indicate on Drawings, by details, schedules, or a combination of both, the locations where hanger rods for individual pipes and hanger rods for trapeze hangers require hanger-rod stiffeners.

B. Hanger-Rod Stiffeners: Install hanger-rod stiffeners where indicated or scheduled on Drawings to receive them and where required to prevent buckling of hanger rods due to seismic forces.

C. Strength of Support and Seismic-Restraint Assemblies: Where not indicated, select sizes of components so strength is adequate to carry present and future static and seismic loads within specified loading limits.

3.2 VIBRATION CONTROL AND SEISMIC-RESTRAINT DEVICE INSTALLATION

A. Coordinate the location of embedded connection hardware with supported equipment attachment and mounting points and with requirements for concrete reinforcement and formwork specified in [Section 033000 "Cast-in-Place Concrete."] [Section 033053 "Miscellaneous Cast-in-Place Concrete."]

B. Installation of vibration isolators must not cause any change of position of equipment, piping, or ductwork resulting in stresses or misalignment.

C. Comply with requirements in Section 077200 "Roof Accessories" for installation of roof curbs, equipment supports, and roof penetrations.

D. Equipment Restraints:

Indicate type and quantity of snubbers described in first subparagraph below on Drawings or in the Plumbing Vibration-Control and Seismic-Restraint Device Schedule on Drawings.

1. Install seismic snubbers on plumbing equipment mounted on vibration isolators. Locate snubbers as close as possible to vibration isolators and bolt to equipment base and supporting structure.

2. Install resilient bolt isolation washers on equipment anchor bolts where clearance between anchor and adjacent surface exceeds 0.125 inch (3.2 mm).

3. Install seismic-restraint devices using methods approved by [an evaluation service member of ICC-ES] [OSHPD] [an agency acceptable to authorities having jurisdiction] that provides required submittals for component.

E. Piping Restraints:

1. Comply with requirements in MSS SP-127.

In first subparagraph below, options for 40 and 80 feet (12 and 24 m) are recommended by MSS SP-127. Revise these dimensions based on the configuration of piping.

2. Space lateral supports a maximum of [40 feet (12 m)] <Insert dimension> o.c., and longitudinal supports a maximum of [80 feet (24 m)] <Insert dimension> o.c.

3. Brace a change of direction longer than 12 feet (3.7 m).

F. Install cables so they do not bend across edges of adjacent equipment or building structure.

G. Install seismic-restraint devices using methods approved by [an evaluation service member of ICC-ES] [OSHPD] [an agency acceptable to authorities having jurisdiction] that provides required submittals for component.

H. Install bushing assemblies for anchor bolts for floor-mounted equipment, arranged to provide resilient media between anchor bolt and mounting hole in concrete base.

I. Install bushing assemblies for mounting bolts for wall-mounted equipment, arranged to provide resilient media where equipment or equipment-mounting channels are attached to wall.

J. Attachment to Structure: If specific attachment is not indicated, anchor bracing to structure at flanges of beams, at upper truss chords of bar joists, or at concrete members.

K. Drilled-in Anchors:

1. Identify position of reinforcing steel and other embedded items prior to drilling holes for anchors. Do not damage existing reinforcing or embedded items during coring or drilling. Notify the structural engineer if reinforcing steel or other embedded items are encountered during drilling. Locate and avoid prestressed tendons, electrical and telecommunications conduit, and gas lines.

2. Do not drill holes in concrete or masonry until concrete, mortar, or grout has achieved full design strength.

3. Wedge Anchors: Protect threads from damage during anchor installation. Heavy-duty sleeve anchors shall be installed with sleeve fully engaged in the structural element to which anchor is to be fastened.

4. Set anchors to manufacturer's recommended torque, using a torque wrench.

5. Install zinc-coated steel anchors for interior and stainless-steel anchors for exterior applications.

3.3 ACCOMMODATION OF DIFFERENTIAL SEISMIC MOTION

Coordinate this article with Drawings.

A. Install flexible connections in piping where they cross seismic joints, where adjacent sections or branches are supported by different structural elements, and where the connections terminate with connection to equipment that is anchored to a different structural element from the one supporting the connections as they approach equipment. Comply with requirements in Section 221116 "Domestic Water Piping" for piping flexible connections.

3.4 FIELD QUALITY CONTROL

Retain "Testing Agency" and "Perform tests and inspections" paragraphs below to identify who shall perform tests and inspections. If retaining second option in "Testing Agency" Paragraph, or if retaining "Perform tests and inspections" Paragraph, retain "Field quality-control reports" Paragraph in "Informational Submittals" Article.

A. Testing Agency: [Owner will engage] [Engage] a qualified testing agency to perform tests and inspections.

Retain "Perform tests and inspections" Paragraph below to require Contractor to perform tests and inspections.

B. Perform tests and inspections.

C. Tests and Inspections:

1. Provide evidence of recent calibration of test equipment by a testing agency acceptable to authorities having jurisdiction.

2. Schedule test with Owner, through Architect, before connecting anchorage device to restrained component (unless postconnection testing has been approved), and with at least seven days' advance notice.

3. Obtain Architect's approval before transmitting test loads to structure. Provide temporary load-spreading members.

4. Test at least [four] <Insert number> of each type and size of installed anchors and fasteners selected by Architect.

5. Test to 90 percent of rated proof load of device.

6. Measure isolator restraint clearance.

7. Measure isolator deflection.

8. Verify snubber minimum clearances.

D. Remove and replace malfunctioning units and retest as specified above.

E. Prepare test and inspection reports.

3.5 ADJUSTING

A. Adjust isolators after piping system is at operating weight.

B. Adjust limit stops on restrained-spring isolators to mount equipment at normal operating height. After equipment installation is complete, adjust limit stops so they are out of contact during normal operation.

END OF SECTION 220548

	VIBRATION AND SEISMIC CONTROLS FOR PLUMBING PIPING AND EQUIPMENT
	220548 - 1



