Copyright 2011 AIA
MasterSpec Professional
09/11

Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 220548.13 - VIBRATION CONTROLS FOR PLUMBING PIPING AND EQUIPMENT
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Elastomeric isolation pads.

2. Elastomeric isolation mounts.

3. Restrained elastomeric isolation mounts.

4. Open-spring isolators.

5. Housed-spring isolators.

6. Restrained-spring isolators.

7. Housed-restrained-spring isolators.

8. Pipe-riser resilient supports.

9. Resilient pipe guides.

10. Elastomeric hangers.

11. Spring hangers.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product.

B. Delegated-Design Submittal: For each vibration isolation device.

1. Include design calculations for selecting vibration isolators.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

See Evaluations for more detailed information about controlling vibration, additional information on products listed in Part 2, illustrations, selection guides, and supplements to equipment schedules.

2.1 ELASTOMERIC ISOLATION PADS

Copy "Elastomeric Isolation Pads" Paragraph below and re-edit for each product.

The configuration and materials of elastomeric isolation pads depend on the equipment being supported. It is possible to have more than one type of elastomeric isolation pad on the same Project. Insert drawing designation for each elastomeric isolation pad type required. Use these designations on Drawings to identify each product.

A. Elastomeric Isolation Pads: <Insert drawing designation>.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Ace Mountings Co., Inc.

b. California Dynamics Corporation.

c. Isolation Technology, Inc.

d. Kinetics Noise Control, Inc.

e. Mason Industries, Inc.

f. Vibration Eliminator Co., Inc.

g. Vibration Isolation.

h. Vibration Mountings & Controls, Inc.

i. <Insert manufacturer's name>.

3. Fabrication: Single or multiple layers of sufficient durometer stiffness for uniform loading over pad area.

4. Size: Factory or field cut to match requirements of supported equipment.

Verify availability of various pad materials and their properties with manufacturers.

5. Pad Material: Oil and water resistant with elastomeric properties.

6. Surface Pattern: [Smooth] [Ribbed] [Waffle] pattern.

Retain first subparagraph below if pad is infused with synthetic fibers.

7. Infused nonwoven cotton or synthetic fibers.

Retain subparagraph below if galvanized-steel baseplates are adhered to the isolation pad to facilitate load distribution.

8. Load-bearing metal plates adhered to pads.

2.2 ELASTOMERIC ISOLATION MOUNTS

Copy "Double-Deflection, Elastomeric Isolation Mounts" Paragraph below and re-edit for each product.

The configuration and materials of elastomeric isolation mounts depend on the equipment being supported. It is possible to have more than one type of elastomeric isolation mount on the same Project. Insert drawing designation for each elastomeric isolation mount type required. Use these designations on Drawings to identify each product.

A. Double-Deflection, Elastomeric Isolation Mounts: <Insert drawing designation>.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Ace Mountings Co., Inc.

b. California Dynamics Corporation.

c. Isolation Technology, Inc.

d. Kinetics Noise Control, Inc.

e. Mason Industries, Inc.

f. Vibration Eliminator Co., Inc.

g. Vibration Isolation.

h. Vibration Mountings & Controls, Inc.

i. <Insert manufacturer's name>.

3. Mounting Plates:

a. Top Plate: Encapsulated steel load transfer top plates, factory drilled and threaded[ with threaded studs or bolts].

Retain "Baseplate" Subparagraph below if the elastomeric mount being specified has a baseplate.

b. Baseplate: Encapsulated steel bottom plates with holes provided for anchoring to support structure.

4. Elastomeric Material: Molded, oil-resistant rubber, neoprene, or other elastomeric material.

2.3 RESTRAINED ELASTOMERIC ISOLATION MOUNTS

Copy "Restrained Elastomeric Isolation Mounts" Paragraph below and re-edit for each product.

The configuration and materials of restrained elastomeric isolation mounts depend on the equipment being supported. It is possible to have more than one type of restrained elastomeric isolation mount on the same Project. Insert drawing designation for each mount type required. Use these designations on Drawings to identify each product.

A. Restrained Elastomeric Isolation Mounts: <Insert drawing designation>.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Ace Mountings Co., Inc.

b. California Dynamics Corporation.

c. Isolation Technology, Inc.

d. Kinetics Noise Control, Inc.

e. Mason Industries, Inc.

f. Vibration Eliminator Co., Inc.

g. Vibration Isolation.

h. Vibration Mountings & Controls, Inc.

i. <Insert manufacturer's name>.

3. Description: All-directional isolator with restraints containing two separate and opposing elastomeric elements that prevent central threaded element and attachment hardware from contacting the housing during normal operation.

a. Housing: Cast-ductile iron or welded steel.

b. Elastomeric Material: Molded, oil-resistant rubber, neoprene, or other elastomeric material.

2.4 OPEN-SPRING ISOLATORS

Copy "Freestanding, Laterally Stable, Open-Spring Isolators" Paragraph below and re-edit for each product.

The configuration and materials of open-spring isolators depend on the equipment being supported. It is possible to have more than one type of open-spring isolator on the same Project. Insert drawing designation for each open-spring isolator type required. Use these designations on Drawings to identify each product.

A. Freestanding, Laterally Stable, Open-Spring Isolators: <Insert drawing designation>.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Ace Mountings Co., Inc.

b. California Dynamics Corporation.

c. Isolation Technology, Inc.

d. Kinetics Noise Control, Inc.

e. Mason Industries, Inc.

f. Vibration Eliminator Co., Inc.

g. Vibration Isolation.

h. Vibration Mountings & Controls, Inc.

i. <Insert manufacturer's name>.

3. Outside Spring Diameter: Not less than 80 percent of the compressed height of the spring at rated load.

4. Minimum Additional Travel: 50 percent of the required deflection at rated load.

5. Lateral Stiffness: More than 80 percent of rated vertical stiffness.

6. Overload Capacity: Support 200 percent of rated load, fully compressed, without deformation or failure.

7. Baseplates: Factory-drilled steel plate for bolting to structure with an elastomeric isolator pad attached to the underside. Baseplates shall limit floor load to 500 psig (3447 kPa).

8. Top Plate and Adjustment Bolt: Threaded top plate with adjustment bolt and cap screw to fasten and level equipment.

2.5 HOUSED-SPRING ISOLATORS

Copy "Freestanding, Laterally Stable, Open-Spring Isolators in Two-Part Telescoping Housing" Paragraph below and re-edit for each product.

The configuration and materials of housed-spring isolators depend on the equipment being supported. It is possible to have more than one type of housed-spring isolator on the same Project. Insert drawing designation for each housed-spring isolator type required. Use these designations on Drawings to identify each product.

A. Freestanding, Laterally Stable, Open-Spring Isolators in Two-Part Telescoping Housing: <Insert drawing designation>.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Ace Mountings Co., Inc.

b. California Dynamics Corporation.

c. Isolation Technology, Inc.

d. Kinetics Noise Control, Inc.

e. Mason Industries, Inc.

f. Vibration Eliminator Co., Inc.

g. Vibration Isolation.

h. Vibration Mountings & Controls, Inc.

i. <Insert manufacturer's name>.

3. Outside Spring Diameter: Not less than 80 percent of the compressed height of the spring at rated load.

4. Minimum Additional Travel: 50 percent of the required deflection at rated load.

5. Lateral Stiffness: More than 80 percent of rated vertical stiffness.

6. Overload Capacity: Support 200 percent of rated load, fully compressed, without deformation or failure.

7. Two-Part Telescoping Housing: A steel top and bottom frame separated by an elastomeric material and enclosing the spring isolators.

a. Drilled base housing for bolting to structure with an elastomeric isolator pad attached to the underside. Bases shall limit floor load to 500 psig (3447 kPa).

b. Top housing with [attachment and leveling bolt] [threaded mounting holes and internal leveling device] [elastomeric pad].

2.6 RESTRAINED-SPRING ISOLATORS

Copy "Freestanding, Laterally Stable, Open-Spring Isolators with Vertical-Limit Stop Restraint" Paragraph below and re-edit for each product.

The configuration and materials of restrained-spring isolators depend on the equipment being supported. It is possible to have more than one type of restrained-spring isolator on the same Project. Insert drawing designation for each restrained-spring isolator type required. Use these designations on Drawings to identify each product.

A. Freestanding, Laterally Stable, Open-Spring Isolators with Vertical-Limit Stop Restraint: <Insert drawing designation>.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Ace Mountings Co., Inc.

b. California Dynamics Corporation.

c. Isolation Technology, Inc.

d. Kinetics Noise Control, Inc.

e. Mason Industries, Inc.

f. Vibration Eliminator Co., Inc.

g. Vibration Isolation.

h. Vibration Mountings & Controls, Inc.

i. <Insert manufacturer's name>.

3. Housing: Steel housing with vertical-limit stops to prevent spring extension due to weight being removed.

a. Base with holes for bolting to structure with an elastomeric isolator pad attached to the underside. Bases shall limit floor load to 500 psig (3447 kPa).

b. Top plate with [threaded mounting holes] [elastomeric pad].

c. Internal leveling bolt that acts as blocking during installation.

4. Restraint: Limit stop as required for equipment and authorities having jurisdiction.

5. Outside Spring Diameter: Not less than 80 percent of the compressed height of the spring at rated load.

6. Minimum Additional Travel: 50 percent of the required deflection at rated load.

7. Lateral Stiffness: More than 80 percent of rated vertical stiffness.

8. Overload Capacity: Support 200 percent of rated load, fully compressed, without deformation or failure.

2.7 HOUSED-RESTRAINED-SPRING ISOLATORS

Copy "Freestanding, Steel, Open-Spring Isolators with Vertical-Limit Stop Restraint in Two-Part Telescoping Housing" Paragraph below and re-edit for each product.

The configuration and materials of housed-restrained-spring isolators depend on the equipment being supported. It is possible to have more than one type of housed-restrained-spring isolator on the same Project. Insert drawing designation for each housed-restrained-spring isolator type required. Use these designations on Drawings to identify each product.

A. Freestanding, Steel, Open-Spring Isolators with Vertical-Limit Stop Restraint in Two-Part Telescoping Housing: <Insert drawing designation>.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Ace Mountings Co., Inc.

b. California Dynamics Corporation.

c. Isolation Technology, Inc.

d. Kinetics Noise Control, Inc.

e. Mason Industries, Inc.

f. Vibration Eliminator Co., Inc.

g. Vibration Isolation.

h. Vibration Mountings & Controls, Inc.

i. <Insert manufacturer's name>.

3. Two-Part Telescoping Housing: A steel top and bottom frame separated by an elastomeric material and enclosing the spring isolators. Housings are equipped with [adjustable] [non-adjustable] snubbers to limit vertical movement.

a. Drilled base housing for bolting to structure with an elastomeric isolator pad attached to the underside. Bases shall limit floor load to 500 psig (3447 kPa).

b. Threaded top housing with adjustment bolt and cap screw to fasten and level equipment.

4. Outside Spring Diameter: Not less than 80 percent of the compressed height of the spring at rated load.

5. Minimum Additional Travel: 50 percent of the required deflection at rated load.

6. Lateral Stiffness: More than 80 percent of rated vertical stiffness.

7. Overload Capacity: Support 200 percent of rated load, fully compressed, without deformation or failure.

2.8 PIPE-RISER RESILIENT SUPPORT

Copy "Description" Paragraph below and re-edit for each product.

The configuration and materials of pipe-riser resilient supports depend on the equipment being supported. It is possible to have more than one type of pipe-riser resilient support on the same Project. Insert drawing designation for each pipe-riser resilient support type required. Use these designations on Drawings to identify each product.

A. Description: All-directional, acoustical pipe anchor consisting of two steel tubes separated by a minimum 1/2-inch- (13-mm-) thick neoprene <Insert drawing designation>.

1. Vertical-Limit Stops: Steel and neoprene vertical-limit stops arranged to prevent vertical travel in both directions.

2. Maximum Load Per Support: 500 psig (3.45 MPa)on isolation material providing equal isolation in all directions.

2.9 RESILIENT PIPE GUIDES

Copy "Description" Paragraph below and re-edit for each product.

The configuration and materials of resilient pipe guides depend on the equipment being supported. It is possible to have more than one type of resilient pipe guide on the same Project. Insert drawing designation for each resilient pipe guide type required. Use these designations on Drawings to identify each product.

A. Description: Telescopic arrangement of two steel tubes or post and sleeve arrangement separated by a minimum 1/2-inch- (13-mm-) thick neoprene <Insert drawing designation>.

Retain "Factory-Set Height Guide with Shear Pin" Subparagraph below where vertical motion due to pipe expansion and contraction is required and clearances are not readily visible.

1. Factory-Set Height Guide with Shear Pin: Shear pin shall be removable and reinsertable to allow for selection of pipe movement. Guides shall be capable of motion to meet location requirements.

2.10 ELASTOMERIC HANGERS

Copy "Elastomeric Mount in a Steel Frame with Upper and Lower Steel Hanger Rods" Paragraph below and re-edit for each product.

The configuration and materials of elastomeric hangers depend on the equipment being supported. It is possible to have more than one type of elastomeric hanger on the same Project. Insert drawing designation for each elastomeric hanger type required. Use these designations on Drawings to identify each product.

A. Elastomeric Mount in a Steel Frame with Upper and Lower Steel Hanger Rods: <Insert drawing designation>.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Ace Mountings Co., Inc.

b. California Dynamics Corporation.

c. Isolation Technology, Inc.

d. Kinetics Noise Control, Inc.

e. Mason Industries, Inc.

f. Vibration Eliminator Co., Inc.

g. Vibration Mountings & Controls, Inc.

h. <Insert manufacturer's name>.

3. Frame: Steel, fabricated with a connection for an upper threaded hanger rod and an opening on the underside to allow for a maximum of 30 degrees of angular lower hanger-rod misalignment without binding or reducing isolation efficiency.

4. Dampening Element: Molded, oil-resistant rubber, neoprene, or other elastomeric material with a projecting bushing for the underside opening preventing steel to steel contact.

2.11 SPRING HANGERS

Copy "Combination Coil-Spring and Elastomeric-Insert Hanger with Spring and Insert in Compression" Paragraph below and re-edit for each product.

The configuration and materials of spring hangers depend on the equipment being supported. It is possible to have more than one type of spring hanger on the same Project. Insert drawing designation for each spring hanger type required. Use these designations on Drawings to identify each product.

A. Combination Coil-Spring and Elastomeric-Insert Hanger with Spring and Insert in Compression: <Insert drawing designation>.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Ace Mountings Co., Inc.

b. California Dynamics Corporation.

c. Kinetics Noise Control, Inc.

d. Mason Industries, Inc.

e. Vibration Eliminator Co., Inc.

f. Vibration Isolation.

g. Vibration Mountings & Controls, Inc.

h. <Insert manufacturer's name>.

3. Frame: Steel, fabricated for connection to threaded hanger rods and to allow for a maximum of 30 degrees of angular hanger-rod misalignment without binding or reducing isolation efficiency.

4. Outside Spring Diameter: Not less than 80 percent of the compressed height of the spring at rated load.

5. Minimum Additional Travel: 50 percent of the required deflection at rated load.

6. Lateral Stiffness: More than 80 percent of rated vertical stiffness.

7. Overload Capacity: Support 200 percent of rated load, fully compressed, without deformation or failure.

8. Elastomeric Element: Molded, oil-resistant rubber or neoprene. Steel-washer-reinforced cup to support spring and bushing projecting through bottom of frame.

Retain "Adjustable Vertical Stop" Subparagraph below if a vertical-limit stop is required.

9. Adjustable Vertical Stop: Steel washer with neoprene washer "up-stop" on lower threaded rod.

10. Self-centering hanger rod cap to ensure concentricity between hanger rod and support spring coil.

PART 3 -  EXECUTION

3.1 VIBRATION CONTROL DEVICE INSTALLATION

A. Coordinate the location of embedded connection hardware with supported equipment attachment and mounting points and with requirements for concrete reinforcement and formwork specified in [Section 033000 "Cast-in-Place Concrete."] [Section 033053 "Miscellaneous Cast-in-Place Concrete."]

B. Installation of vibration isolators must not cause any change of position of equipment, piping, or ductwork resulting in stresses or misalignment.

END OF SECTION 220548.13

	VIBRATION CONTROLS FOR PLUMBING PIPING AND EQUIPMENT
	220548.13 - 1



