Copyright 2010 AIA
MasterSpec Professional
03/10

Copyright 2010 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 221113 - FACILITY WATER DISTRIBUTION PIPING
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. This Section includes water-distribution piping and related components outside the building for [water service] [fire-service mains] [combined water service and fire-service mains].

Utility companies usually provide water meters. Delete paragraph below if water meters are provided by utility company or Contractor. If utility company furnishes water meters, identify the company here and specify what it will do; then edit text to suit Project.

B. Utility-furnished products include water meters that will be furnished to the site, ready for installation.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product indicated.

B. Shop Drawings: Detail precast concrete vault assemblies and indicate dimensions, method of field assembly, and components.

1.3 INFORMATIONAL SUBMITTALS

A. Field quality-control test reports.

1.4 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

1.5 QUALITY ASSURANCE

Retain and edit first paragraph and subparagraphs below to suit Project or delete if not applicable.

A. Regulatory Requirements:

1. Comply with requirements of utility company supplying water. Include tapping of water mains and backflow prevention.

2. Comply with standards of authorities having jurisdiction for potable-water-service piping, including materials, installation, testing, and disinfection.

3. Comply with standards of authorities having jurisdiction for fire-suppression water-service piping, including materials, hose threads, installation, and testing.

B. Piping materials shall bear label, stamp, or other markings of specified testing agency.

C. Comply with ASTM F 645 for selection, design, and installation of thermoplastic water piping.

D. Comply with FMG's "Approval Guide" or UL's "Fire Protection Equipment Directory" for fire-service-main products.

E. NFPA Compliance: Comply with NFPA 24 for materials, installations, tests, flushing, and valve and hydrant supervision for fire-service-main piping for fire suppression.

F. NSF Compliance:

Delete first subparagraph below if NSF 14 is not applicable.

1. Comply with NSF 14 for plastic potable-water-service piping.[ Include marking "NSF-pw" on piping.]

2. Comply with NSF 61 for materials for water-service piping and specialties for domestic water.

1.6 PROJECT CONDITIONS

Retain this Article if interruption of existing water-distribution service is required.

A. Interruption of Existing Water-Distribution Service: Do not interrupt service to facilities occupied by Owner or others unless permitted under the following conditions and then only after arranging to provide temporary water-distribution service according to requirements indicated:

1. Notify [Architect] [Construction Manager] [Owner] no fewer than [two] <Insert number> days in advance of proposed interruption of service.

2. Do not proceed with interruption of water-distribution service without [Architect's] [Construction Manager's] [Owner's] written permission.

1.7 COORDINATION

Edit this Article to suit Project if new water-distribution piping will connect to other on-site water-distribution piping.

A. Coordinate connection to water main with utility company.

PART 2 -  PRODUCTS

2.1 PIPE AND FITTINGS

A. Soft Copper Tube: [ASTM B 88, Type K (ASTM B 88M, Type A)] [and] [ASTM B 88, Type L (ASTM B 88M, Type B)], water tube, annealed temper.

1. Copper, Solder-Joint Fittings: ASME B16.18, cast-copper-alloy or ASME B16.22, wrought-copper, solder-joint pressure type. Furnish only wrought-copper fittings if indicated.

B. Hard Copper Tube: [ASTM B 88, Type K (ASTM B 88M, Type A)] [and] [ASTM B 88, Type L (ASTM B 88M, Type B)], water tube, drawn temper.

1. Copper, Solder-Joint Fittings: ASME B16.18, cast-copper-alloy or ASME B16.22, wrought-copper, solder-joint pressure type. Furnish only wrought-copper fittings if indicated.

C. Mechanical-Joint, Ductile-Iron Pipe: AWWA C151, with mechanical-joint bell and plain spigot end unless grooved or flanged ends are indicated.

1. Mechanical-Joint, Ductile-Iron Fittings: AWWA C110, ductile- or gray-iron standard pattern or AWWA C153, ductile-iron compact pattern.

2. Glands, Gaskets, and Bolts: AWWA C111, ductile- or gray-iron glands, rubber gaskets, and steel bolts.

Pipe and fittings in first paragraph and subparagraphs below are available in NPS 3 to NPS 48 (DN 80 to DN 1200).

D. Push-on-Joint, Ductile-Iron Pipe: AWWA C151, with push-on-joint bell and plain spigot end unless grooved or flanged ends are indicated.

1. Push-on-Joint, Ductile-Iron Fittings: AWWA C110, ductile- or gray-iron standard pattern or AWWA C153, ductile-iron compact pattern.

2. Gaskets: AWWA C111, rubber.

E. Grooved-Joint, Ductile-Iron Pipe: AWWA C151, with cut, rounded-grooved ends.

1. Grooved-End, Ductile-Iron Pipe Appurtenances:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. Retain one of two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

a. Available Manufacturers: Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

b. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

1) Anvil International, Inc.

2) Victaulic Company of America.

3) <Insert manufacturer's name.>

Pipe in first paragraph below is FMG approved in NPS 2 to NPS 24 (DN 50 to DN 600).

F. PE, Fire-Service Pipe: ASTM F 714, AWWA C906, or equivalent for PE water pipe; FMG approved, with minimum thickness equivalent to FMG [Class 150] [and] [Class 200].

1. Molded PE Fittings: ASTM D 3350, PE resin, socket- or butt-fusion type, made to match PE pipe dimensions and class.

G. PVC, AWWA Pipe: AWWA C900, [Class 150] [and] [Class 200], with bell end with gasket, and with spigot end.

1. Comply with UL 1285 for fire-service mains if indicated.

2. PVC Fabricated Fittings: AWWA C900, [Class 150] [and] [Class 200], with bell-and-spigot or double-bell ends. Include elastomeric gasket in each bell.

3. PVC Molded Fittings: AWWA C907, Class 150, with bell-and-spigot or double-bell ends. Include elastomeric gasket in each bell.

4. Push-on-Joint, Ductile-Iron Fittings: AWWA C110, ductile- or gray-iron standard pattern or AWWA C153, ductile-iron compact pattern.

a. Gaskets: AWWA C111, rubber.

5. Mechanical-Joint, Ductile-Iron Fittings: AWWA C110, ductile- or gray-iron standard pattern or AWWA C153, ductile-iron compact pattern.

a. Glands, Gaskets, and Bolts: AWWA C111, ductile- or gray-iron glands, rubber gaskets, and steel bolts.

2.2 JOINING MATERIALS

A. Refer to Section 330500 "Common Work Results for Utilities" for commonly used joining materials.

B. Brazing Filler Metals: AWS A5.8, BCuP Series.

C. Bonding Adhesive for Fiberglass Piping: As recommended by fiberglass piping manufacturer.

D. Plastic Pipe-Flange Gasket, Bolts, and Nuts: Type and material recommended by piping system manufacturer, unless otherwise indicated.

2.3 PIPING SPECIALTIES

A. Transition Fittings: Manufactured fitting or coupling same size as, with pressure rating at least equal to and ends compatible with, piping to be joined.

B. Tubular-Sleeve Pipe Couplings:

1. Description: Metal, bolted, sleeve-type, reducing or transition coupling, with center sleeve, gaskets, end rings, and bolt fasteners and with ends of same sizes as piping to be joined.

a. Standard: AWWA C219.

2.4 GATE VALVES

A. AWWA, Cast-Iron Gate Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. Retain one of three subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Available Manufacturers: Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product: Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. American AVK Co.; Valves & Fittings Div.

b. American Cast Iron Pipe Co.; American Flow Control Div.

c. American Cast Iron Pipe Co.; Waterous Co. Subsidiary.

d. Crane Co.; Crane Valve Group; Stockham Div.

e. East Jordan Iron Works, Inc.

f. McWane, Inc.; Clow Valve Co. Div. (Oskaloosa).
g. McWane, Inc.; Kennedy Valve Div.

h. McWane, Inc.; M & H Valve Company Div.

i. McWane, Inc.; Tyler Pipe Div.; Utilities Div.

j. Mueller Co.; Water Products Div.

k. NIBCO INC.

l. U.S. Pipe and Foundry Company.

m. <Insert manufacturer's name.>

Retain any of five subparagraphs and associated subparagraphs below for valve types and pressure ratings required. If more than one pressure zone is required, show pressure ratings of valves on Drawings.

4. Nonrising-Stem, Metal-Seated Gate Valves:

a. Description: Gray- or ductile-iron body and bonnet; with cast-iron or bronze double-disc gate, bronze gate rings, bronze stem, and stem nut.

1) Standard: AWWA C500.

2) Minimum Pressure Rating: 200 psig (1380 kPa).

3) End Connections: Mechanical joint.

4) Interior Coating: Complying with AWWA C550.

5. Nonrising-Stem, Resilient-Seated Gate Valves:

a. Description: Gray- or ductile-iron body and bonnet; with bronze or gray- or ductile-iron gate, resilient seats, bronze stem, and stem nut.

1) Standard: AWWA C509.

2) Minimum Pressure Rating: 200 psig (1380 kPa).

3) End Connections: Mechanical joint.

4) Interior Coating: Complying with AWWA C550.

6. Nonrising-Stem, High-Pressure, Resilient-Seated Gate Valves:

a. Description: Ductile-iron body and bonnet; with bronze or ductile-iron gate, resilient seats, bronze stem, and stem nut.

1) Standard: AWWA C509.

2) Minimum Pressure Rating: 250 psig (1725 kPa).

3) End Connections: Push on or mechanical joint.

4) Interior Coating: Complying with AWWA C550.

7. OS&Y, Rising-Stem, Metal-Seated Gate Valves:

a. Description: Cast- or ductile-iron body and bonnet, with cast-iron double disc, bronze disc and seat rings, and bronze stem.

1) Standard: AWWA C500.

2) Minimum Pressure Rating: 200 psig (1380 kPa).

3) End Connections: Flanged.

8. OS&Y, Rising-Stem, Resilient-Seated Gate Valves:

a. Description: Cast- or ductile-iron body and bonnet, with bronze or gray- or ductile-iron gate, resilient seats, and bronze stem.

1) Standard: AWWA C509.

2) Minimum Pressure Rating: 200 psig (1380 kPa).

3) End Connections: Flanged.

Retain UL/FMG, cast-iron gate valves for use with indicator posts and OS&Y gate valves for fire-service piping in vaults if required by authorities having jurisdiction.

B. UL/FMG, Cast-Iron Gate Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. Retain one of first three subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Available Manufacturers: Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product: Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. American Cast Iron Pipe Co.; American Flow Control Div.

b. American Cast Iron Pipe Co.; Waterous Co. Subsidiary.

c. Crane Co.; Crane Valve Group; Stockham Div.

d. McWane, Inc.; Clow Valve Co. Div. (Oskaloosa).

HYPERLINK "http://www.specagent.com/LookUp/?uid=123456820656&mf=04&src=wd"
McWane, Inc.; Kennedy Valve Div.

e. McWane, Inc.; M & H Valve Company Div.

f. Mueller Co.; Water Products Div.

g. NIBCO INC.

h. U.S. Pipe and Foundry Company.

i. <Insert manufacturer's name.>

4. UL/FMG, Nonrising-Stem Gate Valves:

a. Description: Iron body and bonnet with flange for indicator post, bronze seating material, and inside screw.

1) Standards: UL 262 and FMG approved.

2) Minimum Pressure Rating: 175 psig (1207 kPa).

3) End Connections: Flanged.

Use supervisory switches with valves in subparagraph and associated subparagraphs below.

5. OS&Y, Rising-Stem Gate Valves:

a. Description: Iron body and bonnet and bronze seating material.

1) Standards: UL 262 and FMG approved.

2) Minimum Pressure Rating: 175 psig (1207 kPa).

3) End Connections: Flanged.

C. Bronze Gate Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. Retain one of three subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Available Manufacturers: Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product: Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Crane Co.; Crane Valve Group; Crane Valves.

b. Crane Co.; Crane Valve Group; Jenkins Valves.

c. Crane Co.; Crane Valve Group; Stockham Div.

d. Hammond Valve.

e. Milwaukee Valve Company.

f. NIBCO INC.

g. Red-White Valve Corporation.

h. <Insert manufacturer's name.>

Use supervisory switches with valves in first subparagraph and associated subparagraphs below.

4. OS&Y, Rising-Stem Gate Valves:

a. Description: Bronze body and bonnet and bronze stem.

1) Standards: UL 262 and FMG approved.

2) Minimum Pressure Rating: 175 psig (1207 kPa).

3) End Connections: Threaded.

5. Nonrising-Stem Gate Valves:

a. Description: Class 125, Type 1, bronze with solid wedge, threaded ends, and malleable-iron handwheel.

1) Standard: MSS SP-80.

2.5 GATE VALVE ACCESSORIES AND SPECIALTIES

Retain first paragraph and subparagraphs below for tapping connections larger than NPS 2 (DN 50).

A. Tapping-Sleeve Assemblies:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. Retain one of first three subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Available Manufacturers: Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product: Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. American Cast Iron Pipe Co.; Waterous Co. Subsidiary.

b. East Jordan Iron Works, Inc.

c. Flowserve.

d. McWane, Inc.; Clow Valve Co. Div. (Oskaloosa).

e. McWane, Inc.; Kennedy Valve Div.

f. McWane, Inc.; M & H Valve Company Div.

g. Mueller Co.; Water Products Div.

h. U.S. Pipe and Foundry Company.

i. <Insert manufacturer's name.>

4. Description: Sleeve and valve compatible with drilling machine.

a. Standard: MSS SP-60.

b. Tapping Sleeve: Cast- or ductile-iron or stainless-steel, two-piece bolted sleeve with flanged outlet for new branch connection. Include sleeve matching size and type of pipe material being tapped and with recessed flange for branch valve.

c. Valve: AWWA, cast-iron, nonrising-stem, [metal] [resilient]-seated gate valve with one raised face flange mating tapping-sleeve flange.

B. Valve Boxes: Comply with AWWA M44 for cast-iron valve boxes. Include top section, adjustable extension of length required for depth of burial of valve, plug with lettering "WATER," and bottom section with base that fits over valve and with a barrel approximately 5 inches (125 mm) in diameter.

1. Operating Wrenches: Steel, tee-handle with one pointed end, stem of length to operate deepest buried valve, and socket matching valve operating nut.

C. Indicator Posts: UL 789, FMG-approved, vertical-type, cast-iron body with operating wrench, extension rod, and adjustable cast-iron barrel of length required for depth of burial of valve.

2.6 [CORPORATION VALVES] [AND] [CURB VALVES]

A. Manufacturers:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. Retain one of two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Available Manufacturers: Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

a. Amcast Industrial Corporation; Lee Brass Co.

b. Ford Meter Box Company, Inc. (The); Pipe Products Div.

c. Jones, James Company.

d. Master Meter, Inc.

e. McDonald, A. Y. Mfg. Co.

f. Mueller Co.; Water Products Div.

g. Red Hed Manufacturing & Supply.

h. <Insert manufacturer's name.>

Retain first paragraph and subparagraphs below for tapping connections NPS 2 (DN 50) and smaller.

B. Service-Saddle Assemblies: Comply with AWWA C800. Include saddle and valve compatible with tapping machine.

1. Service Saddle: Copper alloy with seal and AWWA C800, threaded outlet for corporation valve.

2. Corporation Valve: Bronze body and ground-key plug, with AWWA C800, threaded inlet and outlet matching service piping material.

Retain subparagraph below if utility company requires multiple connections.

3. Manifold: Copper fitting with two to four inlets as required, with ends matching corporation valves and outlet matching service piping material.

C. Curb Valves: Comply with AWWA C800. Include bronze body, ground-key plug or ball, and wide tee head, with inlet and outlet matching service piping material.

D. Service Boxes for Curb Valves: Similar to AWWA M44 requirements for cast-iron valve boxes. Include cast-iron telescoping top section of length required for depth of burial of valve, plug with lettering "WATER," and bottom section with base that fits over curb valve and with a barrel approximately 3 inches (75 mm) in diameter.

1. Shutoff Rods: Steel, tee-handle with one pointed end, stem of length to operate deepest buried valve, and slotted end matching curb valve.

2.7 WATER METERS

A. Water meters will be furnished by utility company.

If utility company furnishes water meters, identify utility company in Part 1 "Summary" Article and delete all paragraphs and subparagraphs below. If water meters are specified in this Section, delete paragraph above and retain and edit paragraphs and subparagraphs below.

B. Manufacturers:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. Retain one of three subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Available Manufacturers: Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product: Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. AMCO Water Metering Systems.

b. Badger Meter, Inc.

c. Carlon Meter.

d. Hays Fluid Controls; a division of ROMAC Industries Inc.

e. McCrometer.

f. Mueller Co.; Hersey Meters.

g. Neptune Technology Group Inc.

h. Sensus Metering Systems.

i. <Insert manufacturer's name.>

Retain one of two paragraphs and associated subparagraphs below. Verify type of meter required with utility company and authorities having jurisdiction.

C. Displacement-Type Water Meters:

1. Description: With bronze main case.

a. Standard: AWWA C700.

b. Registration: Flow in [gallons (liters)] [cubic feet (cubic meters)].

D. Compound-Type Water Meters:

1. Description:

a. Standard: AWWA C702.

b. Registration: Flow in [gallons (liters)] [cubic feet (cubic meters)].

2.8 BACKFLOW PREVENTERS

Copy and edit paragraph and subparagraphs below for each type of reduced-pressure-principle backflow preventer required.

Reduced-pressure-principle backflow preventers in paragraph and subparagraphs below are for high hazard and are available in NPS 3/4 to NPS 10 (DN 20 to DN 250).

A. Reduced-Pressure-Principle Backflow Preventers:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. Retain one of first three subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Available Manufacturers: Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product: Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Ames Fire & Waterworks; a division of Watts Regulator Co.

b. Conbraco Industries, Inc.

c. FEBCO; SPX Valves & Controls.

d. Flomatic Corporation.

e. Watts Water Technologies, Inc.

f. Wilkins; a Zurn company.

g. <Insert manufacturer's name.>

4. Standard: [ASSE 1013] [or] [AWWA C511].

5. Operation: Continuous-pressure applications.

6. Pressure Loss: [12 psig (83 kPa)] <Insert pressure> maximum, through middle 1/3 of flow range.

7. Size: <Insert NPS (DN).>

8. Design Flow Rate: <Insert gpm (L/s).>

9. Selected Unit Flow Range Limits: <Insert gpm (L/s).>

10. Pressure Loss at Design Flow Rate: <Insert psig (kPa)> for NPS 2 (DN 50) and smaller; <Insert psig (kPa)> for NPS 2-1/2 (DN 65) and larger.

11. Body: Bronze for NPS 2 (DN 50) and smaller; [cast iron with interior lining complying with AWWA C550 or that is FDA approved] [steel with interior lining complying with AWWA C550 or that is FDA approved] [stainless steel] for NPS 2-1/2 (DN 65) and larger.

12. End Connections: Threaded for NPS 2 (DN 50) and smaller; [flanged] <Insert type> for NPS 2-1/2 (DN 65) and larger.

13. Configuration: Designed for [horizontal, straight through] [vertical inlet, horizontal center section, and vertical outlet] [vertical] <Insert configuration> flow.

14. Accessories:

a. Valves: Ball type with threaded ends on inlet and outlet of NPS 2 (DN 50) and smaller; OS&Y gate type with flanged ends on inlet and outlet of NPS 2-1/2 (DN 65) and larger.

b. Air-Gap Fitting: ASME A112.1.2, matching backflow preventer connection.

Copy and edit paragraph and subparagraphs below for each type of double-check, backflow-prevention assembly required.

Double-check, backflow-prevention assemblies in paragraph and subparagraphs below are for low hazard and are available in NPS 3/4 to NPS 10 (DN 20 to DN 250).

B. Double-Check, Backflow-Prevention Assemblies:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. Retain one of first three subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Available Manufacturers: Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product: Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Ames Fire & Waterworks; a division of Watts Regulator Co.

b. Conbraco Industries, Inc.

c. FEBCO; SPX Valves & Controls.

d. Flomatic Corporation.

e. Watts Water Technologies, Inc.

f. Wilkins; a Zurn company.

g. <Insert manufacturer's name.>

4. Standard: [ASSE 1015] [or] [AWWA C510].

5. Operation: Continuous-pressure applications, unless otherwise indicated.

6. Pressure Loss: [5 psig (35 kPa)] <Insert pressure> maximum, through middle 1/3 of flow range.

7. Size: <Insert NPS (DN).>

8. Design Flow Rate: <Insert gpm (L/s).>

9. Selected Unit Flow Range Limits: <Insert gpm (L/s).>

10. Pressure Loss at Design Flow Rate: <Insert psig (kPa)> for NPS 2 (DN 50) and smaller; <Insert psig (kPa)> for NPS 2-1/2 (DN 65) and larger.

11. Body: Bronze for NPS 2 (DN 50) and smaller; [cast iron with interior lining complying with AWWA C550 or that is FDA approved] [steel with interior lining complying with AWWA C550 or that is FDA approved] [stainless steel] for NPS 2-1/2 (DN 65) and larger.

12. End Connections: Threaded for NPS 2 (DN 50) and smaller; [flanged] <Insert type> for NPS 2-1/2 (DN 65) and larger.

13. Configuration: Designed for [horizontal, straight through] <Insert configuration> flow.

14. Accessories: Ball valves with threaded ends on inlet and outlet of NPS 2 (DN 50) and smaller; OS&Y gate valves with flanged ends on inlet and outlet of NPS 2-1/2 (DN 65) and larger.

2.9 WATER METER BOXES

Select one of three paragraphs in this Article.

A. Description: Cast-iron body and cover for disc-type water meter, with lettering "WATER METER" in cover; and with slotted, open-bottom base section of length to fit over service piping.

Delete subparagraph below if not permitted.

1. Option: Base section may be cast-iron, PVC, clay, or other pipe.

B. Description: Cast-iron body and double cover for disc-type water meter, with lettering "WATER METER" in top cover; and with separate inner cover; air space between covers; and slotted, open-bottom base section of length to fit over service piping.

Use meter box in paragraph below in walks or unpaved areas away from traffic; do not use in roadways.

C. Description: Polymer-concrete body and cover for disc-type water meter, with lettering "WATER" in cover; and with slotted, open-bottom base section of length to fit over service piping. Include vertical and lateral design loadings of 15,000 lb minimum over 10 by 10 inches (6800 kg minimum over 254 by 254 mm) square.

2.10 CONCRETE VAULTS

Retain this Article if vaults are required and are not specified in Section 033000 "Cast-in-Place Concrete" or Section 033053 "Miscellaneous Cast-in-Place Concrete."

A. Description: Precast, reinforced-concrete vault, designed for A-16 load designation according to ASTM C 857 and made according to ASTM C 858.

1. Ladder: ASTM A 36/A 36M, steel or polyethylene-encased steel steps.

2. Manhole: ASTM A 48/A 48M Class No. 35A minimum tensile strength, gray-iron traffic frame and cover.

a. Dimension: 24-inch (610-mm) minimum diameter, unless otherwise indicated.

Retain "Manhole" Subparagraph and associated subparagraph above or below.

3. Manhole: ASTM A 536, Grade 60-40-18, ductile-iron traffic frame and cover.

a. Dimension: 24-inch- (610-mm-) minimum diameter, unless otherwise indicated.

4. Drain: ASME A112.6.3, cast-iron floor drain with outlet of size indicated. Include body anchor flange, light-duty cast-iron grate, bottom outlet, and integral or field-installed bronze ball or clapper-type backwater valve.

2.11 FIRE HYDRANTS

A. Dry-Barrel Fire Hydrants:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. Retain one of three subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Available Manufacturers: Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product: Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. American AVK Co.; Valves & Fittings Div.

b. American Cast Iron Pipe Co.; American Flow Control Div.

c. American Cast Iron Pipe Co.; Waterous Co. Subsidiary.

d. American Foundry Group, Inc.

e. East Jordan Iron Works, Inc.

f. McWane, Inc.; Clow Valve Co. Div. (Oskaloosa).
g. McWane, Inc.; Kennedy Valve Div.

h. McWane, Inc.; M & H Valve Company Div.

i. Mueller Co.; Water Products Div.

j. Troy Valve; a division of Penn-Troy Manufacturing, Inc.

k. U.S. Pipe and Foundry Company.

l. <Insert manufacturer's name.>

Retain subparagraph and associated subparagraphs below for AWWA dry-barrel fire hydrants.

4. Description: Freestanding, with one NPS 4-1/2 (DN 115) and two NPS 2-1/2 (DN 65) outlets, 5-1/4-inch (133-mm) main valve, drain valve, and NPS 6 (DN 150) mechanical-joint inlet. Include interior coating according to AWWA C550. Hydrant shall have cast-iron body, compression-type valve opening against pressure and closing with pressure.

a. Standard: AWWA C502.

b. Pressure Rating: [150 psig (1035 kPa) minimum] [250 psig (1725 kPa)].

Retain subparagraph and associated subparagraphs below for UL/FMG, dry-barrel fire hydrants.

5. Description: Freestanding, with one NPS 4-1/2 (DN 115) and two NPS 2-1/2 (DN 65) outlets, 5-1/4-inch (133-mm) main valve, drain valve, and NPS 6 (DN 150) mechanical-joint inlet. Hydrant shall have cast-iron body, compression-type valve opening against pressure and closing with pressure.

a. Standards: UL 246, FMG approved.

b. Pressure Rating: [150 psig (1035 kPa) minimum] [250 psig (1725 kPa)].

Retain four subparagraphs below with either "Description" Subparagraph retained above.

c. Outlet Threads: NFPA 1963, with external hose thread used by local fire department. Include cast-iron caps with steel chains.

Edit first two subparagraphs below if required by authorities having jurisdiction.

d. Operating and Cap Nuts: Pentagon, 1-1/2 inches (38 mm) point to flat.

e. Direction of Opening: Open hydrant valve by turning operating nut to left or counterclockwise.

f. Exterior Finish: Red alkyd-gloss enamel paint, unless otherwise indicated.

B. Wet-Barrel Fire Hydrants:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. Retain one of three subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Available Manufacturers: Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product: Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. American AVK Co.; Valves & Fittings Div.

b. Jones, James Company.

c. McWane, Inc.; Clow Valve Co. Div. (Corona).

d. McWane, Inc.; Clow Valve Co. Div. (Oskaloosa).

e. Mueller Co.; Water Products Div.

f. <Insert manufacturer's name.>

Retain subparagraph and associated subparagraphs below for AWWA wet-barrel fire hydrants.

4. Description: Freestanding, with one NPS 4-1/2 (DN 115) and two NPS 2-1/2 (DN 65) outlets, NPS 6 (DN 150) threaded or flanged inlet, and base section with NPS 6 (DN 150) mechanical-joint inlet. Include interior coating according to AWWA C550.

a. Standard: AWWA C503.

b. Pressure Rating: 150 psig (1035 kPa) minimum.

Retain subparagraph and associated subparagraphs below for UL/FMG, wet-barrel fire hydrants.

5. Description: Freestanding, with one NPS 4-1/2 (DN 115) and two NPS 2-1/2 (DN 65) outlets, NPS 6 (DN 150) threaded or flanged inlet, and base section with NPS 6 (DN 150) mechanical-joint inlet.

a. Standards: UL 246 and FMG approved.

b. Pressure Rating: 150 psig (1035 kPa) minimum.

Retain four subparagraphs below with either "Description" Subparagraph retained above.

c. Outlet Threads: NFPA 1963, with external hose thread used by local fire department. Include cast-iron caps with steel chains.

Edit first two subparagraphs below if required by authorities having jurisdiction.

d. Operating and Cap Nuts: Pentagon, 1-1/2 inches (38 mm) point to flat.

e. Direction of Opening: Open hydrant valves by turning operating nut to left or counterclockwise.

f. Exterior Finish: Red alkyd-gloss enamel paint, unless otherwise indicated.

2.12 FIRE DEPARTMENT CONNECTIONS

Copy and edit paragraph and subparagraphs below for each type of fire department connection required.

A. Fire Department Connections:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. Retain one of first three subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Available Manufacturers: Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product: Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Elkhart Brass Mfg. Co., Inc.

b. Fire End & Croker Corporation.

c. Guardian Fire Equipment, Inc.

d. Kidde Fire Fighting.

e. Potter Roemer.

f. Reliable Automatic Sprinkler Co., Inc.

g. <Insert manufacturer's name.>

4. Description: Freestanding, with cast-bronze body, thread inlets according to NFPA 1963 and matching local fire department hose threads, and threaded bottom outlet. Include lugged caps, gaskets, and chains; lugged swivel connection and drop clapper for each hose-connection inlet; 18-inch- (460-mm-) high brass sleeve; and round escutcheon plate.

a. Standard: UL 405.

b. Connections: Two NPS 2-1/2 (DN 65) inlets and one [NPS 4 (DN 100)] [NPS 6 (DN 150)] outlet.

c. Connections: [Three] [Four] NPS 2-1/2 (DN 65) inlets and one NPS 6 (DN 150) outlet.

d. Connections: Six NPS 2-1/2 (DN 65) inlets and one [NPS 6 (DN 150)] [NPS 8 (DN 200)] outlet.

e. Inlet Alignment: [Inline, horizontal] [Square].

f. Finish Including Sleeve: [Polished chrome-plated] [Rough chrome-plated] [Polished bronze].

g. Escutcheon Plate Marking: "[AUTO SPKR] [&] [STANDPIPE]."

PART 3 -  EXECUTION

3.1 EARTHWORK

A. Refer to Section 312000 "Earth Moving" for excavating, trenching, and backfilling.

3.2 PIPING APPLICATIONS

Piping is arbitrarily limited to NPS 6 (DN 150) for water service, NPS 8 (DN 200) for fire-service mains, and NPS 10 (DN 250) for combined water service and fire-service mains.

Select piping applications from this Article. Coordinate with materials specified in Part 2.

A. General: Use pipe, fittings, and joining methods for piping systems according to the following applications.

B. Transition couplings and special fittings with pressure ratings at least equal to piping pressure rating may be used, unless otherwise indicated.

C. Do not use flanges or unions for underground piping.

D. Flanges, unions, and special fittings may be used, instead of joints indicated, on aboveground piping and piping in vaults.

E. Underground water-service piping [NPS 3/4 to NPS 3 (DN 20 to DN 80)] <Insert pipe size range> shall be soft copper tube, [ASTM B 88, Type K (ASTM B 88M, Type A)] [ASTM B 88, Type L (ASTM B 88M, Type B)]; wrought-copper, solder-joint fittings; and brazed joints.

Retain "any of" option in first paragraph below to allow Contractor to select piping materials from those retained.

F. Underground water-service piping [NPS 4 and NPS 6 (DN 100 and DN 150)] <Insert pipe size range> shall be[ any of] the following:

Retain one or more of three subparagraphs below.

1. Soft copper tube, [ASTM B 88, Type K (ASTM B 88M, Type A)] [ASTM B 88, Type L (ASTM B 88M, Type B)]; wrought-copper, solder-joint fittings; and brazed joints.

2. Ductile-iron, [push-on-joint pipe; ductile-iron, push-on-joint fittings; and gasketed] [mechanical-joint pipe; ductile-iron, mechanical-joint fittings; and mechanical] joints.

3. NPS 4 and NPS 6 (DN 100 and DN 150): NPS 6 (DN 150) PVC, AWWA Class 150 pipe; PVC, AWWA Class 150 molded fittings; and gasketed joints.

G. Water Meter Box Water-Service Piping [NPS 3/4 to NPS 2 (DN 20 to DN 50)] <Insert pipe size range> shall be same as underground water-service piping.

H. Aboveground[ and Vault] Water-Service Piping [NPS 3/4 to NPS 3 (DN 20 to DN 80)] <Insert pipe size range> shall be hard copper tube, [ASTM B 88, Type K (ASTM B 88M, Type A)] [ASTM B 88, Type L (ASTM B 88M, Type B)]; wrought-copper, solder-joint fittings; and brazed joints.

Retain "any of" option in paragraph below to allow Contractor to select piping materials from those retained.

I. Aboveground [and vault ]water-service piping [NPS 4 and NPS 6 (DN 100 and DN 150)] <Insert pipe size range> shall be[ any of] the following:

Retain one or more of two subparagraphs below.

1. Hard copper tube, [ASTM B 88, Type K (ASTM B 88M, Type A)] [ASTM B 88, Type L (ASTM B 88M, Type B)]; wrought-copper, solder-joint fittings; and brazed joints.

2. Ductile-iron, grooved-end pipe; ductile-iron, grooved-end appurtenances; and grooved joints.

Retain "any of" option in first paragraph below to allow Contractor to select piping materials from those retained.

J. Underground Fire-Service-Main Piping [NPS 4 to NPS 8 (DN 100 to DN 200)] <Insert pipe size range> shall be[ any of] the following:

Fire-service-main piping materials listed in subparagraphs below are for fire-protection water service. They may not be suitable for potable-water service.

Retain one or more of four subparagraphs below.

1. Ductile-iron, [push-on-joint pipe; ductile-iron, push-on-joint fittings; and gasketed] [mechanical-joint pipe; ductile-iron, mechanical-joint fittings; and mechanical] [grooved-end pipe; ductile-iron-pipe appurtenances; and grooved] joints.

2. PE, Class [150] [200], fire-service pipe; molded PE fittings; and heat-fusion joints.

3. PVC, AWWA Class 150 pipe listed for fire-protection service; PVC Class 150 fabricated or molded fittings; and gasketed joints.

4. PVC, AWWA Class 200 pipe listed for fire-protection service; PVC Class 200 fabricated fittings; and gasketed joints.

K. Aboveground[ and Vault] Fire-Service-Main Piping [NPS 4 to NPS 8 (DN 100 to DN 200)]<Insert pipe size range> shall be ductile-iron, grooved-end pipe; ductile-iron-pipe appurtenances; and grooved joints.

Retain "any of" option in first paragraph below to allow Contractor to select piping materials from those retained.

L. Underground Combined Water-Service and Fire-Service-Main Piping [NPS 6 to NPS 10 (DN 150 to DN 250)] <Insert pipe size range> shall be[ any of] the following:

Retain one or more of two subparagraphs below.

1. Ductile-iron, [push-on-joint pipe; ductile-iron, push-on-joint fittings; and gasketed] [mechanical-joint pipe; ductile-iron, mechanical-joint fittings; and mechanical] [grooved-end pipe; ductile-iron-pipe appurtenances; and grooved] joints.

2. PVC, AWWA Class [150] [200] pipe listed for fire-protection service; PVC fabricated or molded fittings of same class as pipe; and gasketed joints.

M. Aboveground[ and Vault] Combined Water Service and Fire-Service-Main Piping [NPS 6 to NPS 10 (DN 150 to DN 250)] <Insert pipe size range> shall be ductile-iron, grooved-end pipe; ductile-iron-pipe appurtenances; and grooved joints.

3.3 VALVE APPLICATIONS

See Editing Instruction No. 3 in the Evaluations for cautions about selecting products.

A. General Application: Use mechanical-joint-end valves for NPS 3 (DN 80) and larger underground installation. Use threaded- or flanged-end valves for installation in vaults. Use UL/FMG, nonrising-stem gate valves for installation with indicator posts. Use corporation valves and curb valves with ends compatible with piping, for NPS 2 (DN 50) and smaller installation.

B. Drawings indicate valve types to be used. Where specific valve types are not indicated, the following requirements apply:

Retain one of first two subparagraphs below.

1. Underground Valves, NPS 3 (DN 80) and Larger: AWWA, cast-iron, nonrising-stem, [metal] [resilient] [high-pressure, resilient]-seated gate valves with valve box.

2. Underground Valves, NPS 4 (DN 100) and Larger, for Indicator Posts: UL/FMG, cast-iron, nonrising-stem gate valves with indicator post.

3. Use the following for valves in vaults and aboveground:

a. Gate Valves, NPS 2 (DN 50) and Smaller: Bronze, [nonrising] [rising] stem.

b. Gate Valves, NPS 3 (DN 80) and Larger: [AWWA, cast iron, OS&Y rising stem, metal seated] [AWWA, cast iron, OS&Y rising stem, resilient seated] [UL/FMG, cast iron, OS&Y rising stem].

3.4 PIPING SYSTEMS - COMMON REQUIREMENTS

A. See Section 330500 "Common Work Results for Utilities" for piping-system common requirements.

3.5 PIPING INSTALLATION

A. Water-Main Connection: Arrange with utility company for tap of size and in location indicated in water main.

Retain paragraph above if tap is made by utility company; retain paragraph below if tap is made by Contractor.

B. Water-Main Connection: Tap water main according to requirements of water utility company and of size and in location indicated.

Retain paragraph and subparagraphs below for tapping of pipe with connections larger than NPS 2 (DN 50).

C. Make connections larger than NPS 2 (DN 50) with tapping machine according to the following:

1. Install tapping sleeve and tapping valve according to MSS SP-60.

2. Install tapping sleeve on pipe to be tapped. Position flanged outlet for gate valve.

3. Use tapping machine compatible with valve and tapping sleeve; cut hole in main. Remove tapping machine and connect water-service piping.

4. Install gate valve onto tapping sleeve. Comply with MSS SP-60. Install valve with stem pointing up and with valve box.

Retain first paragraph and subparagraphs below for tapping of pipe with connections NPS 2 (DN 50) and smaller.

D. Make connections NPS 2 (DN 50) and smaller with drilling machine according to the following:

1. Install service-saddle assemblies and corporation valves in size, quantity, and arrangement required by utility company standards.

2. Install service-saddle assemblies on water-service pipe to be tapped. Position outlets for corporation valves.

3. Use drilling machine compatible with service-saddle assemblies and corporation valves. Drill hole in main. Remove drilling machine and connect water-service piping.

4. Install corporation valves into service-saddle assemblies.

5. Install manifold for multiple taps in water main.

6. Install curb valve in water-service piping with head pointing up and with service box.

E. Comply with NFPA 24 for fire-service-main piping materials and installation.

1. Install copper tube and fittings according to CDA's "Copper Tube Handbook."

F. Install ductile-iron, water-service piping according to AWWA C600 and AWWA M41.

G. Install PE pipe according to ASTM D 2774 and ASTM F 645.

H. Install PVC, AWWA pipe according to ASTM F 645 and AWWA M23.

Edit first paragraph below for required minimum depth if known.

I. Bury piping with depth of cover over top at least [30 inches (750 mm)] <Insert dimension>, with top at least [12 inches (300 mm)] <Insert dimension> below level of maximum frost penetration.

J. Extend water-service piping and connect to water-supply source and building-water-piping systems at outside face of building wall in locations and pipe sizes indicated.

1. Terminate water-service piping at building wall until building-water-piping systems are installed. Terminate piping with caps, plugs, or flanges as required for piping material. Make connections to building-water-piping systems when those systems are installed.

K. Sleeves are specified in Section 220517 "Sleeves and Sleeve Seals for Plumbing Piping."

L. Mechanical sleeve seals are specified in Section 220517 "Sleeves and Sleeve Seals for Plumbing Piping."

Retain and edit paragraph below for piping with gasketed joints; delete if not required.

M. Install underground piping with restrained joints at horizontal and vertical changes in direction. Use restrained-joint piping, thrust blocks, anchors, tie-rods and clamps, and other supports.

3.6 JOINT CONSTRUCTION

A. See Section 330500 "Common Work Results for Utilities" for basic piping joint construction.

B. Make pipe joints according to the following:

1. Ductile-Iron Piping, Gasketed Joints for Water-Service Piping: AWWA C600 and AWWA M41.

2. Ductile-Iron Piping, Gasketed Joints for Fire-Service-Main Piping: UL 194.

3. Ductile-Iron Piping, Grooved Joints: Cut-groove pipe. Assemble joints with grooved-end, ductile-iron-piping couplings, gaskets, lubricant, and bolts according to coupling manufacturer's written instructions.

4. PE Piping Insert-Fitting Joints: Use plastic insert fittings and fasteners according to fitting manufacturer's written instructions.

5. PVC Piping Gasketed Joints: Use joining materials according to AWWA C900. Construct joints with elastomeric seals and lubricant according to ASTM D 2774 or ASTM D 3139 and pipe manufacturer's written instructions.

6. Dissimilar Materials Piping Joints: Use adapters compatible with both piping materials, with OD, and with system working pressure.

3.7 ANCHORAGE INSTALLATION

Delete this Article if anchorages are not required.

A. Anchorage, General: Install water-distribution piping with restrained joints. Anchorages and restrained-joint types that may be used include the following:

Retain subparagraphs below for types of anchorages and restrained joints to be permitted.

1. Concrete thrust blocks.

2. Locking mechanical joints.

3. Set-screw mechanical retainer glands.

4. Bolted flanged joints.

5. Heat-fused joints.

6. Pipe clamps and tie rods.

7. <Insert devices.>

B. Install anchorages for tees, plugs and caps, bends, crosses, valves, and hydrant branches. Include anchorages for the following piping systems:

1. Gasketed-Joint, Ductile-Iron, Water-Service Piping: According to AWWA C600.

2. Gasketed-Joint, PVC Water-Service Piping: According to AWWA M23.

3. Fire-Service-Main Piping: According to NFPA 24.

C. Apply full coat of asphalt or other acceptable corrosion-resistant material to surfaces of installed ferrous anchorage devices.

3.8 VALVE INSTALLATION

A. AWWA Gate Valves: Comply with AWWA C600 and AWWA M44. Install each underground valve with stem pointing up and with valve box.

B. UL/FMG, Gate Valves: Comply with NFPA 24. Install each underground valve and valves in vaults with stem pointing up and with vertical cast-iron indicator post.

C. MSS Valves: Install as component of connected piping system.

D. Corporation Valves and Curb Valves: Install each underground curb valve with head pointed up and with service box.

3.9 WATER METER INSTALLATION

Delete this Article if utility company provides water meters.

A. Install water meters, piping, and specialties according to utility company's written instructions.

Retain one or both paragraphs below.

B. Water Meters: Install displacement-type water meters, NPS 2 (DN 50) and smaller, in meter boxes with shutoff valves on water meter inlets. Include valves on water meter outlets and valved bypass around meters unless prohibited by authorities having jurisdiction.

C. Water Meters: Install compound-type water meters, NPS 3 (DN 80) and larger, in meter vaults. Include shutoff valves on water meter inlets and outlets and valved bypass around meters. Support meters, valves, and piping on brick or concrete piers.

3.10 BACKFLOW PREVENTER INSTALLATION

A. Install backflow preventers of type, size, and capacity indicated. Include valves and test cocks. Install according to requirements of plumbing and health department and authorities having jurisdiction.

B. Do not install backflow preventers that have relief drain in vault or in other spaces subject to flooding.

C. Do not install bypass piping around backflow preventers.

Revise or delete paragraph below to suit Project.

D. Support NPS 2-1/2 (DN 65) and larger backflow preventers, valves, and piping near floor and on brick or concrete piers.

3.11 WATER METER BOX INSTALLATION

A. Install water meter boxes in paved areas flush with surface.

B. Install water meter boxes in grass or earth areas with top [2 inches (50 mm)] <Insert dimension> above surface.

3.12 CONCRETE VAULT INSTALLATION

A. Install precast concrete vaults according to ASTM C 891.

3.13 FIRE HYDRANT INSTALLATION

A. General: Install each fire hydrant with separate gate valve in supply pipe, anchor with restrained joints or thrust blocks, and support in upright position.

B. Wet-Barrel Fire Hydrants: Install with valve below frost line. Provide for drainage.

C. AWWA Fire Hydrants: Comply with AWWA M17.

D. UL/FMG Fire Hydrants: Comply with NFPA 24.

3.14 FIRE DEPARTMENT CONNECTION INSTALLATION

A. Install protective pipe bollards [on two sides of] [on three sides of] <Describe arrangement> each fire department connection. Pipe bollards are specified in Section 055000 "Metal Fabrications."

3.15 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

A. See Section 330500 "Common Work Results for Utilities" for piping connections to valves and equipment.

B. Connect water-distribution piping to [utility water main] [existing water main] <Insert piping system>. Use [tapping sleeve and tapping valve] [service clamp and corporation valve] <Insert method>.

C. Connect water-distribution piping to interior [domestic water] [and] [fire-suppression] piping.

D. Connect waste piping from concrete vault drains to [sanitary sewerage system. See Section 221313 "Facility Sanitary Sewers" for connection to sanitary-sewer] [storm-drainage system. See Section 334100 "Storm Utility Drainage Piping" for connection to storm-sewer] piping.

3.16 FIELD QUALITY CONTROL

A. Piping Tests: Conduct piping tests before joints are covered and after concrete thrust blocks have hardened sufficiently. Fill pipeline 24 hours before testing and apply test pressure to stabilize system. Use only potable water.

B. Hydrostatic Tests: Test at not less than one-and-one-half times working pressure for two hours.

1. Increase pressure in 50-psig (350-kPa) increments and inspect each joint between increments. Hold at test pressure for 1 hour; decrease to 0 psig (0 kPa). Slowly increase again to test pressure and hold for 1 more hour. Maximum allowable leakage is 2 quarts (1.89 L) per hour per 100 joints. Remake leaking joints with new materials and repeat test until leakage is within allowed limits.

C. Prepare reports of testing activities.

3.17 IDENTIFICATION

A. Install continuous underground[ detectable] warning tape during backfilling of trench for underground water-distribution piping. Locate below finished grade, directly over piping. Underground warning tapes are specified in Section 312000 "Earth Moving."

Delete paragraph below if metallic water-service piping without electrically insulated fittings will be used.

B. Permanently attach equipment nameplate or marker indicating plastic water-service piping, on main electrical meter panel. See Section 330500 "Common Work Results for Utilities" for identifying devices.

3.18 CLEANING

Edit this Article as required to suit authorities having jurisdiction.

A. Clean and disinfect water-distribution piping as follows:

1. Purge new water-distribution piping systems and parts of existing systems that have been altered, extended, or repaired before use.

Retain subparagraph below for fire-protection-water piping not connected to potable-water supply.

2. Use purging and disinfecting procedure prescribed by authorities having jurisdiction or, if method is not prescribed by authorities having jurisdiction, use procedure described in NFPA 24 for flushing of piping. Flush piping system with clean, potable water until dirty water does not appear at points of outlet.

Delete subparagraph above and retain subparagraph and associated subparagraphs below for water-distribution piping connected to potable-water supply.

3. Use purging and disinfecting procedure prescribed by authorities having jurisdiction or, if method is not prescribed by authorities having jurisdiction, use procedure described in AWWA C651 or do as follows:

a. Fill system or part of system with water/chlorine solution containing at least 50 ppm of chlorine; isolate and allow to stand for 24 hours.

Retain last subparagraph above or first subparagraph below.

b. Drain system or part of system of previous solution and refill with water/chlorine solution containing at least 200 ppm of chlorine; isolate and allow to stand for 3 hours.

c. After standing time, flush system with clean, potable water until no chlorine remains in water coming from system.

d. Submit water samples in sterile bottles to authorities having jurisdiction. Repeat procedure if biological examination shows evidence of contamination.

B. Prepare reports of purging and disinfecting activities.

END OF SECTION 221113

	FACILITY WATER DISTRIBUTION PIPING
	221113 - 1



