Copyright 2010 AIA
MasterSpec Professional
03/10

Copyright 2010 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 221119 - DOMESTIC WATER PIPING SPECIALTIES
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Vacuum breakers.

2. Backflow preventers.

3. Water pressure-reducing valves.

4. Balancing valves.

5. Temperature-actuated, water mixing valves.

6. Strainers.

7. Hose bibbs.

8. Wall hydrants.

9. Drain valves.

10. Water-hammer arresters.

11. Trap-seal primer valves.

B. Related Requirements:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

1. Section 220519 "Meters and Gages for Plumbing Piping" for thermometers, pressure gages, and flow meters in domestic water piping.

2. Section 221116 "Domestic Water Piping" for water meters.

3. Section 223200 "Domestic Water Filtration Equipment" for water filters in domestic water piping.

4. Section 224300 "Medical Plumbing Fixtures" for thermostatic mixing valves for sitz baths, thermostatic mixing-valve assemblies for hydrotherapy equipment, and outlet boxes for dialysis equipment.

5. Section 224500 "Emergency Plumbing Fixtures" for water tempering equipment.

6. Section 224713 "Drinking Fountains" for water filters for water coolers.

7. Section 224716 "Pressure Water Coolers" for water filters for water coolers.

8. Section 224723 "Remote Water Coolers" for water filters for water coolers.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product.

1.3 INFORMATIONAL SUBMITTALS

A. Field quality-control reports.

1.4 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

2.1 GENERAL REQUIREMENTS FOR PIPING SPECIALTIES

Retain both options in paragraph below if plastic piping specialties are required.

A. Potable-water piping and components shall comply with NSF 61[ and NSF 14].[ Mark "NSF-pw" on plastic piping components.]

2.2 PERFORMANCE REQUIREMENTS

Coordinate this article with Section 221116 "Domestic Water Piping."

A. Minimum Working Pressure for Domestic Water Piping Specialties: [125 psig (860 kPa)] <Insert value> unless otherwise indicated.

2.3 VACUUM BREAKERS

Copy "Pipe-Applied, Atmospheric-Type Vacuum Breakers" Paragraph below and re-edit for each type of vacuum breaker required. If only one type is required, drawing designation may be omitted.

Pipe-applied, atmospheric-type vacuum breakers in first paragraph below are for moderate to high hazard and are available in NPS 1/4 to NPS 3 (DN 8 to DN 80). They are unsuitable for continuous pressure or for protection from backflow.

A. Pipe-Applied, Atmospheric-Type Vacuum Breakers <Insert drawing designation if any>:

1. Standard: ASSE 1001.

2. Size: NPS 1/4 to NPS 3 (DN 8 to DN 80), as required to match connected piping.

3. Body: Bronze.

4. Inlet and Outlet Connections: Threaded.

5. Finish: [Rough bronze] [Chrome plated].

Copy "Hose-Connection Vacuum Breakers" Paragraph below and re-edit for each type of vacuum breaker required. If only one type is required, drawing designation may be omitted.

Hose-connection vacuum breakers in paragraph below are for low hazard and are unsuitable for continuous pressure. Outlet size is garden-hose thread.

B. Hose-Connection Vacuum Breakers <Insert drawing designation if any>:

1. Standard: ASSE 1011.

2. Body: Bronze, nonremovable, with manual drain.

3. Outlet Connection: Garden-hose threaded complying with ASME B1.20.7.

4. Finish: [Chrome or nickel plated] [Rough bronze].

2.4 BACKFLOW PREVENTERS

Copy "Intermediate Atmospheric-Vent Backflow Preventers" Paragraph below and re-edit for each type of backflow preventer required. If only one type is required, drawing designation may be omitted.

Intermediate atmospheric-vent backflow preventers in first paragraph below are for moderate hazard and are available in NPS 1/2 and NPS 3/4 (DN 15 and DN 20).

A. Intermediate Atmospheric-Vent Backflow Preventers <Insert drawing designation if any>:

1. Standard: ASSE 1012.

2. Operation: Continuous-pressure applications.

3. Size: [NPS 1/2 (DN 15)] [NPS 3/4 (DN 20)].

4. Body: Bronze.

5. End Connections: [Union, solder] [Solder] joint.

6. Finish: [Chrome plated] [Rough bronze].

Copy "Reduced-Pressure-Principle Backflow Preventers" Paragraph below and re-edit for each type of backflow preventer required. If only one type is required, drawing designation may be omitted.

Reduced-pressure-principle backflow preventers in first paragraph below are for high hazard and are available in NPS 3/4 to NPS 10 (DN 20 to DN 250).

B. Reduced-Pressure-Principle Backflow Preventers <Insert drawing designation if any>:

1. Standard: ASSE 1013.

2. Operation: Continuous-pressure applications.

3. Pressure Loss: [12 psig (83 kPa)] <Insert value> maximum, through middle third of flow range.

4. Size: <Insert NPS (DN)>.

5. Design Flow Rate: <Insert gpm (L/s)>.

6. Selected Unit Flow Range Limits: <Insert gpm (L/s)>.

7. Pressure Loss at Design Flow Rate: <Insert psig (kPa)> for sizes NPS 2 (DN 50) and smaller; <Insert psig (kPa)> for NPS 2-1/2 (DN 65) and larger.

8. Body: Bronze for NPS 2 (DN 50) and smaller; [cast iron with interior lining that complies with AWWA C550 or that is FDA approved] [steel with interior lining that complies with AWWA C550 or that is FDA approved] [stainless steel] for NPS 2-1/2 (DN 65) and larger.

9. End Connections: Threaded for NPS 2 (DN 50) and smaller; [flanged] <Insert type> for NPS 2-1/2 (DN 65) and larger.

10. Configuration: Designed for [horizontal, straight-through] [vertical-inlet, horizontal-center-section, and vertical-outlet] [vertical] <Insert configuration> flow.

11. Accessories:

a. Valves NPS 2 (DN 50) and Smaller: Ball type with threaded ends on inlet and outlet.

b. Valves NPS 2-1/2 (DN 65) and Larger: Outside-screw and yoke-gate type with flanged ends on inlet and outlet.

c. Air-Gap Fitting: ASME A112.1.2, matching backflow-preventer connection.

Copy "Double-Check, Backflow-Prevention Assemblies" Paragraph below and re-edit for each type of backflow-prevention assembly required. If only one type is required, drawing designation may be omitted.

Double-check, backflow-prevention assemblies in paragraph below are for low hazard and are available in NPS 3/4 to NPS 10 (DN 20 to DN 250).

C. Double-Check, Backflow-Prevention Assemblies <Insert drawing designation if any>:

1. Standard: ASSE 1015.

2. Operation: Continuous-pressure applications unless otherwise indicated.

3. Pressure Loss: [5 psig (35 kPa)] <Insert value> maximum, through middle third of flow range.

4. Size: <Insert NPS (DN)>.

5. Design Flow Rate: <Insert gpm (L/s)>.

6. Selected Unit Flow Range Limits: <Insert gpm (L/s)>.

7. Pressure Loss at Design Flow Rate: <Insert psig (kPa)> for sizes NPS 2 (DN 50) and smaller; <Insert psig (kPa)> for NPS 2-1/2 (DN 65) and larger.

8. Body: Bronze for NPS 2 (DN 50) and smaller; [cast iron with interior lining that complies with AWWA C550 or that is FDA approved] [steel with interior lining that complies with AWWA C550 or that is FDA approved] [stainless steel] for NPS 2-1/2 (DN 65) and larger.

9. End Connections: Threaded for NPS 2 (DN 50) and smaller; [flanged] <Insert type> for NPS 2-1/2 (DN 65) and larger.

10. Configuration: Designed for [horizontal, straight-through] <Insert configuration> flow.

11. Accessories:

a. ValvesNPS 2 (DN 50) and Smaller: Ball type with threaded ends on inlet and outlet.

b. ValvesNPS 2-1/2 (DN 65) and Larger: Outside-screw and yoke-gate type with flanged ends on inlet and outlet.

2.5 WATER PRESSURE-REDUCING VALVES

Copy "Water Regulators" Paragraph below and re-edit for each type of water regulator required. If only one type is required, drawing designation may be omitted.

Water regulators in paragraph below are available in NPS 1/2 to NPS 3 (DN 15 to DN 80).

A. Water Regulators <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Cash Acme; a division of Reliance Worldwide Corporation.

b. Conbraco Industries, Inc.

c. Honeywell International Inc.

d. Watts; a division of Watts Water Technologies, Inc.; Watts Regulator Company.

e. Zurn Industries, LLC; Plumbing Products Group; Wilkins Water Control Products.

f. <Insert manufacturer's name>.

3. Standard: ASSE 1003.

4. Pressure Rating: Initial working pressure of 150 psig (1035 kPa).

5. Size: <Insert NPS (DN)>.

6. Design Flow Rate: <Insert gpm (L/s)>.

7. Design Inlet Pressure: <Insert psig (kPa)>.

8. Design Outlet Pressure Setting: <Insert psig (kPa)>.

9. Body: Bronze[ with chrome-plated finish] for NPS 2 (DN 50) and smaller; cast iron[ with interior lining that complies with AWWA C550 or that is FDA approved] for NPS 2-1/2 and NPS 3 (DN 65 and DN 80).

10. Valves for Booster Heater Water Supply: Include integral bypass.

11. End Connections: Threaded for NPS 2 (DN 50) and smaller; flanged for NPS 2-1/2 and NPS 3 (DN 65 and DN 80).

2.6 BALANCING VALVES

Copy "Memory-Stop Balancing Valves" Paragraph below and re-edit for each type of balancing valve required. If only one type is required, drawing designation may be omitted.

A. Memory-Stop Balancing Valves <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Conbraco Industries, Inc.

b. Crane Co.; Crane Valve Group; Crane Valves.

c. Crane Co.; Crane Valve Group; Jenkins Valves.

d. Crane Co.; Crane Valve Group; Stockham Div.

e. Hammond Valve.

f. Milwaukee Valve Company.

g. NIBCO Inc.

h. Red-White Valve Corp.

i. <Insert manufacturer's name>.

3. Standard: MSS SP-110 for two-piece, copper-alloy ball valves.

4. Pressure Rating: 400-psig (2760-kPa) minimum CWP.

5. Size: NPS 2 (DN 50) or smaller.

6. Body: Copper alloy.

7. Port: Standard or full port.

8. Ball: Chrome-plated brass.

9. Seats and Seals: Replaceable.

10. End Connections: Solder joint or threaded.

11. Handle: Vinyl-covered steel with memory-setting device.

2.7 TEMPERATURE-ACTUATED, WATER MIXING VALVES

Copy "Water-Temperature Limiting Devices" Paragraph below and re-edit for each type of limiting device required. If only one type is required, drawing designation may be omitted.

Water-temperature limiting devices in first paragraph below are unsuitable for service as master thermostatic mixing valves. Devices below are available in NPS 1/2 to NPS 1 (DN 15 to DN 25) and comply with ASSE 1016, ASSE 1017, or both; however, neither standard is adequate for them. ASSE 1070, "Performance Requirements for Water Temperature Limiting Devices," is under development.

A. Water-Temperature Limiting Devices <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Armstrong International, Inc.

b. Cash Acme; a division of Reliance Worldwide Corporation.

c. Conbraco Industries, Inc.

d. Honeywell International Inc.

e. Legend Valve.

f. Leonard Valve Company.

g. Powers; a division of Watts Water Technologies, Inc.

h. Symmons Industries, Inc.

i. TACO Incorporated.

j. Watts; a division of Watts Water Technologies, Inc.; Watts Regulator Company.

k. Zurn Industries, LLC; Plumbing Products Group; Wilkins Water Control Products.

l. <Insert manufacturer's name>.

3. Standard: ASSE 1017.

4. Pressure Rating: 125 psig (860 kPa).

5. Type: Thermostatically controlled, water mixing valve.

6. Material: Bronze body with corrosion-resistant interior components.

7. Connections: Threaded[ union] inlets and outlet.

8. Accessories: Check stops on hot- and cold-water supplies, and adjustable, temperature-control handle.

9. Tempered-Water Setting: <Insert deg F (deg C)>.

Retain "Tempered-Water Design Flow Rate" Subparagraph below only if flow rate is not indicated on Drawings.

10. Tempered-Water Design Flow Rate: <Insert gpm (L/s)>.

11. Valve Finish: [Chrome plated] [Rough bronze].

Copy "Primary, Thermostatic, Water Mixing Valves" Paragraph below and re-edit for each type of water mixing valve required. If only one type is required, drawing designation may be omitted.

Primary, thermostatic, water mixing valves in paragraph below are available in NPS 3/4 to NPS 3 and maybe in NPS 4 (DN 20 to DN 80 and maybe in DN 100), but usually are NPS 2 (DN 50) or smaller.

B. Primary, Thermostatic, Water Mixing Valves <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Armstrong International, Inc.

b. Lawler Manufacturing Company, Inc.

c. Leonard Valve Company.

d. Powers; a division of Watts Water Technologies, Inc.

e. Symmons Industries, Inc.

f. <Insert manufacturer's name>.

3. Standard: ASSE 1017.

4. Pressure Rating: 125 psig (860 kPa)minimum unless otherwise indicated.

5. Type: [Exposed-mounted] [Cabinet-type], thermostatically controlled, water mixing valve.

6. Material: Bronze body with corrosion-resistant interior components.

7. Connections: Threaded[ union] inlets and outlet.

8. Accessories: Manual temperature control, check stops on hot- and cold-water supplies, and adjustable, temperature-control handle.

9. Tempered-Water Setting: <Insert deg F (deg C)>.

Retain "Tempered-Water Design Flow Rate" Subparagraph below only if flow rate is not indicated on Drawings.

10. Tempered-Water Design Flow Rate: <Insert gpm (L/s)>.

11. Selected Valve Flow Rate at 45-psig (310-kPa) Pressure Drop: <Insert gpm (L/s)>.

12. Pressure Drop at Design Flow Rate: <Insert psig (kPa)>.

13. Valve Finish: [Chrome plated] [Polished, chrome plated] [Rough bronze].

14. Piping Finish: [Chrome plated] [Copper].

Retain "Cabinet" Subparagraph below if cabinet is required.

15. Cabinet: Factory fabricated, stainless steel, for [recessed] [surface] mounting and with hinged, stainless-steel door.

2.8 STRAINERS FOR DOMESTIC WATER PIPING

Copy "Y-Pattern Strainers" Paragraph below and re-edit for each type of Y-pattern strainer required. If only one type is required, drawing designation may be omitted.

A. Y-Pattern Strainers <Insert drawing designation if any>:

1. Pressure Rating: 125 psig (860 kPa) minimum unless otherwise indicated.

2. Body: Bronze for NPS 2 (DN 50) and smaller; cast iron[ with interior lining that complies with AWWA C550 or that is FDA approved, epoxy coated and] for NPS 2-1/2 (DN 65) and larger.

3. End Connections: Threaded for NPS 2 (DN 50) and smaller; flanged for NPS 2-1/2 (DN 65) and larger.

4. Screen: Stainless steel with round perforations unless otherwise indicated.

If retaining more than one screen size, indicate screen size on Drawings.

5. Perforation Size:

a. Strainers NPS 2 (DN 50) and Smaller: [0.020 inch (0.51 mm)] [0.033 inch (0.84 mm)] [0.062 inch (1.57 mm)] <Insert dimension>.

b. Strainers NPS 2-1/2 to NPS 4 (DN 65 to DN 100): [0.045 inch (1.14 mm)] [0.062 inch (1.57 mm)] [0.125 inch (3.18 mm)] <Insert dimension>.

c. Strainers NPS 5 (DN 125) and Larger: [0.10 inch (2.54 mm)] [0.125 inch (3.18 mm)] [0.25 inch (6.35 mm)] <Insert dimension>.

6. Drain: [Pipe plug] [Factory-installed, hose-end drain valve].

2.9 HOSE BIBBS

Copy "Hose Bibbs" Paragraph below for each type of hose bibb required. If only one type is required, drawing designation may be omitted.

A. Hose Bibbs <Insert drawing designation if any>:

1. Standard: ASME A112.18.1 for sediment faucets.

2. Body Material: Bronze.

3. Seat: Bronze, replaceable.

4. Supply Connections: NPS 1/2 or NPS 3/4 (DN 15 or DN 20) threaded or solder-joint inlet.

5. Outlet Connection: Garden-hose thread complying with ASME B1.20.7.

6. Pressure Rating: 125 psig (860 kPa).

7. Vacuum Breaker: Integral[ or field-installation,] nonremovable, drainable, hose-connection vacuum breaker complying with ASSE 1011.

8. Finish for Equipment Rooms: Rough bronze, or chrome or nickel plated.

9. Finish for Service Areas: [Rough bronze] [Chrome or nickel plated].

10. Finish for Finished Rooms: Chrome or nickel plated.

11. Operation for Equipment Rooms: Wheel handle or operating key.

12. Operation for Service Areas: [Wheel handle] [Operating key].

13. Operation for Finished Rooms: [Wheel handle] [Operating key].

14. Include operating key with each operating-key hose bibb.

15. Include[ integral] wall flange with each chrome- or nickel-plated hose bibb.

2.10 WALL HYDRANTS

Wall hydrants without integral vacuum breakers or backflow preventers are available but not recommended.

Copy "Nonfreeze Wall Hydrants" Paragraph below for each type of wall hydrant required. If only one type is required, drawing designation may be omitted.

A. Nonfreeze Wall Hydrants <Insert drawing designation if any>:

1. Standard: ASME A112.21.3M for [concealed] [exposed]-outlet, self-draining wall hydrants.

2. Pressure Rating: 125 psig (860 kPa).

3. Operation: Loose key.

4. Casing and Operating Rod: Of length required to match wall thickness. Include wall clamp.

5. Inlet: NPS 3/4 or NPS 1 (DN 20 or DN 25).

6. Outlet: Concealed, with integral vacuum breaker and garden-hose thread complying with ASME B1.20.7.

7. Box: Deep, flush mounted with cover.

8. Box and Cover Finish: [Polished nickel bronze] [Chrome plated] <Insert finish>.

Retain "Outlet," "Box," and "Box and Cover Finish" subparagraphs above for concealed-outlet-type wall hydrants or "Outlet" and "Nozzle and Wall-Plate Finish" subparagraphs below for exposed-outlet-type wall hydrants.

9. Outlet: Exposed, with integral vacuum breaker and garden-hose thread complying with ASME B1.20.7.

10. Nozzle and Wall-Plate Finish: [Polished nickel bronze] [Rough bronze] <Insert finish>.

11. Operating Keys(s): [One] [Two] with each wall hydrant.

Copy "Nonfreeze, Hot- and Cold-Water Wall Hydrants" Paragraph below and re-edit for each type of wall hydrant required. If only one type is required, drawing designation may be omitted.

B. Nonfreeze, Hot- and Cold-Water Wall Hydrants <Insert drawing designation if any>:

1. Standard: ASME A112.21.3M for [concealed] [exposed]-outlet, self-draining wall hydrants.

2. Pressure Rating: 125 psig (860 kPa).

3. Operation: Loose key.

4. Casing and Operating Rods: Of length required to match wall thickness. Include wall clamps.

5. Inlet: NPS 3/4 or NPS 1 (DN 20 or DN 25).

6. Outlet: Concealed.

7. Box: Deep, flush mounted with cover.

8. Box and Cover Finish: [Polished nickel bronze] [Chrome plated] <Insert finish>.

9. Vacuum Breaker:

a. Nonremovable, manual-drain-type, hose-connection vacuum breaker complying with ASSE 1011 or backflow preventer complying with ASSE 1052.

b. Garden-hose thread complying with ASME B1.20.7 on outlet.

10. Operating Keys(s): [One] [Two] with each wall hydrant.

Copy "Moderate-Climate Wall Hydrants" Paragraph below and re-edit for each type of wall hydrant required. If only one type is required, drawing designation may be omitted.

C. Moderate-Climate Wall Hydrants <Insert drawing designation if any>:

1. Standard: ASME A112.21.3M for [concealed] [exposed]-outlet, self-draining wall hydrants.

2. Pressure Rating: 125 psig (860 kPa).

3. Operation: Loose key.

4. Inlet: NPS 3/4 or NPS 1 (DN 20 or DN 25).

5. Outlet:

a. Concealed, with integral vacuum breaker or nonremovable hose-connection vacuum breaker complying with ASSE 1011 or backflow preventer complying with ASSE 1052.

b. Garden-hose thread complying with ASME B1.20.7.

6. Box: Deep, flush mounted with cover.

7. Box and Cover Finish: [Polished nickel bronze] [Chrome plated] <Insert finish>.

Retain "Outlet," "Box," and "Box and Cover Finish" subparagraphs above for concealed-outlet-type wall hydrants or "Outlet" and "Nozzle and Wall-Plate Finish" subparagraphs below for exposed-outlet-type wall hydrants.

8. Outlet:

a. Concealed, with integral vacuum breaker or nonremovable hose-connection vacuum breaker complying with ASSE 1011 or backflow preventer complying with ASSE 1052.

b. Garden-hose thread complying with ASME B1.20.7.

9. Nozzle and Wall-Plate Finish: [Polished nickel bronze] [Rough bronze] <Insert finish>.

10. Operating Keys(s): [One] [Two] with each wall hydrant.

Copy "Vacuum Breaker Wall Hydrants" Paragraph below and re-edit for each type of wall hydrant required. If only one type is required, drawing designation may be omitted.

D. Vacuum Breaker Wall Hydrants <Insert drawing designation if any>:

1. Standard: ASSE 1019, Type A or Type B.

2. Type: Freeze-resistant, automatic draining with integral air-inlet valve.

Retain only Type B in "Classification" Subparagraph below if hose remains attached.

3. Classification: [Type A, for automatic draining with hose removed or ]Type B, for automatic draining with hose removed or with hose attached and nozzle closed.

4. Pressure Rating: 125 psig (860 kPa).

5. Operation: [Loose key] [or] [wheel handle].

6. Casing and Operating Rod: Of length required to match wall thickness. Include wall clamp.

7. Inlet: NPS 1/2 or NPS 3/4 (DN 15 or DN 20).

8. Outlet: Exposed with garden-hose thread complying with ASME B1.20.7.

2.11 DRAIN VALVES

Copy "Ball-Valve-Type, Hose-End Drain Valves" Paragraph below and re-edit for each type of drain valve required. If only one type is required, drawing designation may be omitted.

A. Ball-Valve-Type, Hose-End Drain Valves <Insert drawing designation if any>:

1. Standard: MSS SP-110 for standard-port, two-piece ball valves.

2. Pressure Rating: 400-psig (2760-kPa) minimum CWP.

3. Size: NPS 3/4 (DN 20).

4. Body: Copper alloy.

5. Ball: Chrome-plated brass.

6. Seats and Seals: Replaceable.

7. Handle: Vinyl-covered steel.

8. Inlet: Threaded or solder joint.

9. Outlet: Threaded, short nipple with garden-hose thread complying with ASME B1.20.7 and cap with brass chain.

2.12 WATER-HAMMER ARRESTERS

Copy "Water-Hammer Arresters" Paragraph below and re-edit for each type of water-hammer arrester required. If only one type is required, drawing designation may be omitted.

A. Water-Hammer Arresters <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

To require a specific type of water-hammer arrester, verify its availability with manufacturer.

a. AMTROL, Inc.

b. Josam Company.

c. MIFAB, Inc.

d. Precision Plumbing Products, Inc.

e. Sioux Chief Manufacturing Company, Inc.

f. Smith, Jay R. Mfg. Co.; Division of Smith Industries, Inc.

g. Tyler Pipe; Wade Div.

h. Watts Drainage Products.

i. Zurn Industries, LLC; Plumbing Products Group; Specification Drainage Products.

j. <Insert manufacturer's name>.

3. Standard: ASSE 1010 or PDI-WH 201.

4. Type: [Metal bellows] [Copper tube with piston].

5. Size: ASSE 1010, Sizes AA and A through F, or PDI-WH 201, Sizes A through F.

2.13 TRAP-SEAL PRIMER DEVICE

Copy "Supply-Type, Trap-Seal Primer Device" Paragraph below and re-edit for each type of primer valve required. If only one type is required, drawing designation may be omitted.

A. Supply-Type, Trap-Seal Primer Device <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. MIFAB, Inc.

b. Precision Plumbing Products, Inc.

c. Sioux Chief Manufacturing Company, Inc.

d. Smith, Jay R. Mfg. Co.; Division of Smith Industries, Inc.

e. Watts; a division of Watts Water Technologies, Inc.; Watts Regulator Company.

f. <Insert manufacturer's name>.

3. Standard: ASSE 1018.

4. Pressure Rating: 125 psig (860 kPa) minimum.

5. Body: Bronze.

6. Inlet and Outlet Connections: NPS 1/2 (DN 15) threaded, union, or solder joint.

7. Gravity Drain Outlet Connection: NPS 1/2 (DN 15) threaded or solder joint.

8. Finish: Chrome plated, or rough bronze for units used with pipe or tube that is not chrome finished.

Copy "Drainage-Type, Trap-Seal Primer Device" Paragraph below and re-edit for each type of primer valve required. If only one type is required, drawing designation may be omitted.

B. Drainage-Type, Trap-Seal Primer Device <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Smith, Jay R. Mfg. Co.; Division of Smith Industries, Inc.

b. <Insert manufacturer's name>.

3. Standard: ASSE 1044, lavatory P-trap with NPS 3/8 (DN 10) minimum, trap makeup connection.

4. Size: NPS 1-1/4 (DN 32) minimum.

5. Material: Chrome-plated, cast brass.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Install backflow preventers in each water supply to mechanical equipment and systems and to other equipment and water systems that may be sources of contamination. Comply with authorities having jurisdiction.

1. Locate backflow preventers in same room as connected equipment or system.

2. Install drain for backflow preventers with atmospheric-vent drain connection with air-gap fitting, fixed air-gap fitting, or equivalent positive pipe separation of at least two pipe diameters in drain piping and pipe-to-floor drain. Locate air-gap device attached to or under backflow preventer. Simple air breaks are unacceptable for this application.

3. Do not install bypass piping around backflow preventers.

B. Install water regulators with inlet and outlet shutoff valves[ and bypass with memory-stop balancing valve]. Install pressure gages on inlet and outlet.

C. Install balancing valves in locations where they can easily be adjusted.

D. Install temperature-actuated, water mixing valves with check stops or shutoff valves on inlets and with shutoff valve on outlet.

1. Install cabinet-type units recessed in or surface mounted on wall as specified.

E. Install Y-pattern strainers for water on supply side of each [control valve] [water pressure-reducing valve] [solenoid valve] [and] [pump].

F. Set nonfreeze, nondraining-type post hydrants in concrete or pavement.

G. Set freeze-resistant yard hydrants with riser pipe in concrete or pavement. Do not encase canister in concrete.

Water-hammer arresters in first paragraph below are best shown on water risers and details. Specifying number, size, and location here is difficult.

H. Install water-hammer arresters in water piping according to PDI-WH 201.

I. Install supply-type, trap-seal primer valves with outlet piping pitched down toward drain trap a minimum of 1 percent, and connect to floor-drain body, trap, or inlet fitting. Adjust valve for proper flow.

J. Install drainage-type, trap-seal primer valves as lavatory trap with outlet piping pitched down toward drain trap a minimum of 1 percent, and connect to floor-drain body, trap, or inlet fitting.

3.2 CONNECTIONS

Coordinate piping installations and specialty arrangements with Drawings and with requirements specified in piping systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Comply with requirements for ground equipment in Section 260526 "Grounding and Bonding for Electrical Systems."

B. Fire-retardant-treated-wood blocking is specified in Section 260519 "Low-Voltage Electrical Power Conductors and Cables" for electrical connections.

3.3 FIELD QUALITY CONTROL

Retain "Perform the following tests and inspections" Paragraph below to require Contractor to perform tests and inspections.

A. Perform the following tests and inspections:

1. Test each [pressure vacuum breaker] [reduced-pressure-principle backflow preventer] [double-check, backflow-prevention assembly] [and] [double-check, detector-assembly backflow preventer] <Insert type> according to authorities having jurisdiction and the device's reference standard.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

B. Domestic water piping specialties will be considered defective if they do not pass tests and inspections.

C. Prepare test and inspection reports.

3.4 ADJUSTING

A. Set field-adjustable pressure set points of water pressure-reducing valves.

B. Set field-adjustable flow set points of balancing valves.

C. Set field-adjustable temperature set points of temperature-actuated, water mixing valves.

END OF SECTION 221119

	DOMESTIC WATER PIPING SPECIALTIES
	221119 - 1



