Copyright 2011 AIA
MasterSpec Professional
09/11

Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 221319 - SANITARY WASTE PIPING SPECIALTIES
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Backwater valves.

2. Cleanouts.

3. Floor drains.

4. Roof flashing assemblies.

5. Miscellaneous sanitary drainage piping specialties.

6. Flashing materials.

7. Grease interceptors.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product indicated. Include rated capacities, operating characteristics, and accessories for grease interceptors.

1.3 QUALITY ASSURANCE

A. Drainage piping specialties shall bear label, stamp, or other markings of specified testing agency.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

2.1 BACKWATER VALVES

Copy paragraphs below and re-edit for each product.

Insert drawing designation for each product required. Use these designations on Drawings to identify each product.

A. Horizontal, Cast-Iron Backwater Valves <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Josam Company; Josam Div.

b. MIFAB, Inc.

c. Smith, Jay R. Mfr. Co.; Division of Smith Industries, Inc.

d. Tyler Pipe; Wade Div.

e. Watts Drainage Products Inc.

f. Zurn Plumbing Products Group; Specification Drainage Operation.

g. <Insert manufacturer's name>.

3. Standard: ASME A112.14.1.

4. Size: Same as connected piping.

5. Body: Cast iron.

6. Cover: Cast iron with [bolted] [or] [threaded] access check valve.

7. End Connections: [Hub and spigot] [Hub and spigot or hubless] [Hubless].

8. Type Check Valve: Removable, bronze, swing check, factory assembled or field modified to hang [closed] [open for airflow unless subject to backflow condition].

9. Extension: ASTM A 74, Service class; full-size, cast-iron, soil-pipe extension to field-installed cleanout at floor; replaces backwater valve cover.

B. Drain-Outlet Backwater Valves <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Josam Company; Josam Div.

b. Smith, Jay R. Mfr. Co.; Division of Smith Industries, Inc.

c. Watts Drainage Products Inc.

d. Zurn Plumbing Products Group; Specification Drainage Operation.

e. <Insert manufacturer's name>.

3. Size: Same as floor drain outlet.

4. Body: Cast iron or bronze made for vertical installation in bottom outlet of floor drain.

5. Check Valve: Removable ball float.

6. Inlet: Threaded.

7. Outlet: Threaded or spigot.

2.2 CLEANOUTS

Copy paragraphs below and re-edit for each product.

Insert drawing designation for each product required. Use these designations on Drawings to identify each product.

A. Exposed Cast-Iron Cleanouts <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Josam Company.

b. MIFAB, Inc.

c. Smith, Jay R. Mfg. Co.

d. Tyler Pipe.

e. Watts Drainage Products.

f. Zurn Plumbing Products Group.

g. <Insert manufacturer's name>.

3. Standard: [ASME A112.36.2M for cast iron] <Insert standard> for cleanout test tee.

4. Size: Same as connected drainage piping

5. Body Material: [Hub-and-spigot, cast-iron soil pipe T-branch] [Hubless, cast-iron soil pipe test tee] as required to match connected piping.

6. Closure: [Countersunk] [Countersunk or raised-head] [Raised-head], [brass] [cast-iron] [plastic] plug.

7. Closure Plug Size: Same as or not more than one size smaller than cleanout size.

B. Cast-Iron Floor Cleanouts <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Josam Company; Josam Div.

b. Oatey.

c. Sioux Chief Manufacturing Company, Inc.

d. Smith, Jay R. Mfg. Co.; Division of Smith Industries, Inc.

e. Tyler Pipe; Wade Div.

f. Watts Drainage Products Inc.

g. Zurn Plumbing Products Group; Light Commercial Operation.

h. Zurn Plumbing Products Group; Specification Drainage Operation.

i. <Insert manufacturer's name>.

3. Standard: ASME A112.36.2M for [adjustable housing] [cast-iron soil pipe with cast-iron ferrule] [heavy-duty, adjustable housing] [threaded, adjustable housing] cleanout.

4. Size: Same as connected branch.

5. Type: [Adjustable housing] [Cast-iron soil pipe with cast-iron ferrule] [Heavy-duty, adjustable housing] [Threaded, adjustable housing].

6. Body or Ferrule: [Cast iron] <Insert material>.

7. Clamping Device: [Not required] [Required].

8. Outlet Connection: [Inside calk] [Spigot] [Threaded].

9. Closure: [Brass plug with straight threads and gasket] [Brass plug with tapered threads] [Cast-iron plug] [Plastic plug].

10. Adjustable Housing Material: [Cast iron] [Plastic] <Insert material> with [threads] [set-screws or other device].

11. Frame and Cover Material and Finish: [Nickel-bronze, copper alloy] [Painted cast iron] [Polished bronze] [Rough bronze] <Insert material and finish>.

12. Frame and Cover Shape: [Round] [Square] <Insert shape>.

13. Top Loading Classification: [Extra Heavy] [Heavy] [Light] [Medium] Duty.

14. Riser: ASTM A 74, [Extra-Heavy] [Service] class, cast-iron drainage pipe fitting and riser to cleanout.

C. Cast-Iron Wall Cleanouts <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Josam Company; Josam Div.

b. MIFAB, Inc.

c. Smith, Jay R. Mfg. Co.; Division of Smith Industries, Inc.

d. Tyler Pipe; Wade Div.

e. Watts Drainage Products Inc.

f. Zurn Plumbing Products Group; Specification Drainage Operation.

g. <Insert manufacturer's name>.

3. Standard: ASME A112.36.2M. Include wall access.

4. Size: Same as connected drainage piping.

5. Body: [Hub-and-spigot, cast-iron soil pipe T-branch] [Hubless, cast-iron soil pipe test tee] as required to match connected piping.

Option for drilled-and-threaded plug in first subparagraph below is for a screw for a wall cover plate.

6. Closure: [Countersunk] [Countersunk or raised-head] [Raised-head], [drilled-and-threaded] [brass] [cast-iron] plug.

7. Closure Plug Size: Same as or not more than one size smaller than cleanout size.

8. Wall Access: Round, [deep, chrome-plated bronze] [flat, chrome-plated brass or stainless-steel] cover plate with screw.

Retain subparagraph above for cover plate or subparagraph below for frame and cover to be installed in drywall.

9. Wall Access: [Round] [Square], [nickel-bronze, copper-alloy, or stainless-steel] <Insert material> wall-installation frame and cover.

2.3 FLOOR DRAINS

Copy paragraphs below and re-edit for each product.

Insert drawing designation for each product required. Use these designations on Drawings to identify each product.

A. Cast-Iron Floor Drains <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Commercial Enameling Co.

b. Josam Company; Josam Div.

c. MIFAB, Inc.

d. Prier Products, Inc.

e. Smith, Jay R. Mfg. Co.; Division of Smith Industries, Inc.

f. Tyler Pipe; Wade Div.

g. Watts Drainage Products Inc.

h. Zurn Plumbing Products Group; Light Commercial Operation.

i. Zurn Plumbing Products Group; Specification Drainage Operation.

j. <Insert manufacturer's name>.

3. Standard: ASME A112.6.3[ with backwater valve].

4. Pattern: [Area] [Floor] [Funnel floor] [Sanitary] <Insert pattern> drain.

5. Body Material: [Gray iron] <Insert material>.

6. Seepage Flange: [Not required] [Required].

7. Anchor Flange: [Not required] [Required].

8. Clamping Device: [Not required] [Required].

9. Outlet: [Bottom] [Side] <Insert type>.

10. Backwater Valve: [Drain-outlet type] [Integral, ASME A112.14.1, swing-check type] [Not required].

Coating in first subparagraph below is usually used only on sanitary floor drains.

11. Coating on Interior and Exposed Exterior Surfaces: [Acid-resistant enamel] [Not required] <Insert material>.

12. Sediment Bucket: [Not required] <Insert description>.

13. Top or Strainer Material: [Bronze] [Gray iron] [Nickel bronze] <Insert material>.

14. Top of Body and Strainer Finish: [Nickel bronze] [Polished bronze] [Rough bronze] <Insert finish>.

15. Top Shape: [Round] [Square] <Insert shape>.

16. Dimensions of Top or Strainer: <Insert dimensions and describe body, sump, and grate.>

17. Top Loading Classification: [Extra Heavy-Duty] [Heavy Duty] [Light Duty] [Medium Duty] <Delete if not applicable>.

18. Funnel: [Not required] [Required] <Insert description and dimensions>.

19. Inlet Fitting: [Not required] [Gray iron, with threaded inlet and threaded or spigot outlet, and trap-seal primer valve connection].

20. Trap Material: [Bronze] [Cast iron] [Copper] [Not required] <Insert material>.

21. Trap Pattern: [Deep-seal P-trap] [Standard P-trap] [Not required] <Insert pattern>.

22. Trap Features: [Cleanout] [Trap-seal primer valve drain connection] [Cleanout and trap-seal primer valve drain connection] [Not required] <Insert type>.

2.4 ROOF FLASHING ASSEMBLIES

Copy paragraph below and re-edit for each product.

Insert drawing designation for each product required. Use these designations on Drawings to identify each product.

A. Roof Flashing Assemblies <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Acorn Engineering Company; Elmdor/Stoneman Div.

b. Thaler Metal Industries Ltd.

c. <Insert manufacturer's name>.

3. Description: Manufactured assembly made of [4.0-lb/sq. ft. (20-kg/sq. m), 0.0625-inch- (1.6-mm-)] [6.0-lb/sq. ft. (30-kg/sq. m), 0.0938-inch- (2.4-mm-)] thick, lead flashing collar and skirt extending at least [6 inches (150 mm)] [8 inches (200 mm)] [10 inches (250 mm)] from pipe, with galvanized-steel boot reinforcement and counterflashing fitting.

Retain one or more of three subparagraphs below. If retaining more than one, indicate location of each on Drawings.

a. Open-Top Vent Cap: Without cap.

b. Low-Silhouette Vent Cap: With vandal-proof vent cap.

c. Extended Vent Cap: With field-installed, vandal-proof vent cap.

2.5 MISCELLANEOUS SANITARY DRAINAGE PIPING SPECIALTIES

Copy paragraphs below and re-edit for each product.

Insert drawing designation for each product required. Use these designations on Drawings to identify each product.

A. Open Drains <Insert drawing designation if any>:

1. Description: Shop or field fabricate from ASTM A 74, Service class, hub-and-spigot, cast-iron, soil-pipe fittings. Include P-trap, hub-and-spigot riser section; and where required, increaser fitting joined with ASTM C 564, rubber gaskets.

2. Size: Same as connected waste piping[ with increaser fitting of size indicated].

B. Deep-Seal Traps <Insert drawing designation if any>:

1. Description: Cast-iron or bronze casting, with inlet and outlet matching connected piping and cleanout trap-seal primer valve connection.

2. Size: Same as connected waste piping.

a. NPS 2 (DN 50): 4-inch- (100-mm-) minimum water seal.

b. NPS 2-1/2 (DN 65) and Larger: 5-inch- (125-mm-) minimum water seal.

C. Floor-Drain, Trap-Seal Primer Fittings <Insert drawing designation if any>:

1. Description: Cast iron, with threaded inlet and threaded or spigot outlet, and trap-seal primer valve connection.

2. Size: Same as floor drain outlet with NPS 1/2 (DN 15) side inlet.

D. Air-Gap Fittings <Insert drawing designation if any>:

1. Standard: ASME A112.1.2, for fitting designed to ensure fixed, positive air gap between installed inlet and outlet piping.

2. Body: Bronze or cast iron.

3. Inlet: Opening in top of body.

4. Outlet: Larger than inlet.

5. Size: Same as connected waste piping and with inlet large enough for associated indirect waste piping.

E. Sleeve Flashing Device <Insert drawing designation if any>:

1. Description: Manufactured, cast-iron fitting, with clamping device, that forms sleeve for pipe floor penetrations of floor membrane. Include galvanized-steel pipe extension in top of fitting that will extend [1 inch (25 mm)] [2 inches (51 mm)] <Insert dimension> above finished floor and galvanized-steel pipe extension in bottom of fitting that will extend through floor slab.

2. Size: As required for close fit to riser or stack piping.

F. Stack Flashing Fittings <Insert drawing designation if any>:

1. Description: Counterflashing-type, cast-iron fitting, with bottom recess for terminating roof membrane, and with threaded or hub top for extending vent pipe.

2. Size: Same as connected stack vent or vent stack.

G. Vent Caps <Insert drawing designation if any>:

1. Description: Cast-iron body with threaded or hub inlet and vandal-proof design. Include vented hood and setscrews to secure to vent pipe.

2. Size: Same as connected stack vent or vent stack.

2.6 FLASHING MATERIALS

Coordinate this article with Section 076200 "Sheet Metal Flashing and Trim" and Section 077200 "Roof Accessories."

Coordinate first two paragraphs below with Section 076200 "Sheet Metal Flashing and Trim" if used on roofs.

A. Lead Sheet: ASTM B 749, Type L51121, copper bearing, with the following minimum weights and thicknesses, unless otherwise indicated:

1. General Use: 4.0-lb/sq. ft. (20-kg/sq. m), 0.0625-inch (1.6-mm) thickness.

2. Vent Pipe Flashing: 3.0-lb/sq. ft. (15-kg/sq. m), 0.0469-inch (1.2-mm) thickness.

3. Burning: 6-lb/sq. ft. (30-kg/sq. m), 0.0938-inch (2.4-mm) thickness.

B. Fasteners: Metal compatible with material and substrate being fastened.

C. Metal Accessories: Sheet metal strips, clamps, anchoring devices, and similar accessory units required for installation; matching or compatible with material being installed.

D. Solder: ASTM B 32, lead-free alloy.

E. Bituminous Coating: SSPC-Paint 12, solvent-type, bituminous mastic.

2.7 GREASE INTERCEPTORS

Copy paragraph below and re-edit for each product.

Insert drawing designation. Use these designations on Drawings to identify each product.

A. Grease Interceptors <Insert drawing designation if any>:

1. Cast-Iron or Steel Grease Interceptors:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

a. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

b. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1) Applied Chemical Technology, Incorporated.

2) Josam Company.

3) MIFAB, Inc.

4) Rockford Sanitary Systems, Inc.

5) Schier Products Company.

6) Smith, Jay R. Mfg. Co.

7) Tyler Pipe.

8) Watts Drainage Products.

9) Zurn Plumbing Products Group.

10) <Insert manufacturer's name>.

2. Plastic Grease Interceptors:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

a. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

b. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1) Ashland Trap Distribution Co.

2) Bio-Microbics, Inc.

3) Canplas LLC.

4) Schier Products Company.

5) Zurn Plumbing Products Group.

6) <Insert manufacturer's name>.

3. Standard: ASME A112.14.3[ and PDI-G101], for intercepting and retaining fats, oils, and greases from food[-preparation] [or] [-processing] wastewater.

PDI certification is currently limited to 50-gpm (3.15-L/s) flow rate and 100-lb (45.4-kg) grease retention by PDI-G101. Larger uncertified units are available. PDI-G101 is being revised, should be available by end of 2003, and will include capacities to 100 gpm (6.3 L/s).

4. Plumbing and Drainage Institute Seal: [Not required] [Required].

5. Body Material: [Cast iron] [Cast iron or steel] [Plastic] <Insert material>.

6. Interior Lining: [Corrosion-resistant enamel] [Not required] <Insert lining>.

7. Exterior Coating: [Corrosion-resistant enamel] [Not required] <Insert coating>.

8. Body Dimensions: <Insert dimensions.>

9. Body Extension: [Not required] [Required].

Rate in first subparagraph below is limited to 100 gpm (6.3 L/s).

10. Flow Rate: <Insert interceptor design rate.>

Capacity in first subparagraph below is limited to 200 lb (90.7 kg).

11. Grease Retention Capacity: <Insert capacity.>

12. Inlet and Outlet Size: <Insert size.>

13. End Connections: [Flanged] [Hub] [Threaded].

14. Cleanout: Integral[ or field installed on outlet].

15. Mounting: [Above floor] [Recessed in acid-resistant, coated steel frame and cradle] [Recessed, flush with floor] <Insert mounting>.

16. Flow-Control Fitting: [Not required] [Required].

17. Operation: [Automatic recovery] [Manual cleaning] [Semiautomatic, manual drawoff] <Insert operation>.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Install backwater valves in building drain piping. For interior installation, provide cleanout deck plate flush with floor and centered over backwater valve cover, and of adequate size to remove valve cover for servicing.

B. Install cleanouts in aboveground piping and building drain piping according to the following, unless otherwise indicated:

1. Size same as drainage piping up to NPS 4 (DN 100). Use NPS 4 (DN 100) for larger drainage piping unless larger cleanout is indicated.

2. Locate at each change in direction of piping greater than 45 degrees.

3. Locate at minimum intervals of 50 feet (15 m) for piping NPS 4 (DN 100) and smaller and 100 feet (30 m) for larger piping.

4. Locate at base of each vertical soil and waste stack.

C. For floor cleanouts for piping below floors, install cleanout deck plates with top flush with finished floor.

D. For cleanouts located in concealed piping, install cleanout wall access covers, of types indicated, with frame and cover flush with finished wall.

E. Install floor drains at low points of surface areas to be drained. Set grates of drains flush with finished floor, unless otherwise indicated.

1. Position floor drains for easy access and maintenance.

2. Set floor drains below elevation of surrounding finished floor to allow floor drainage. Set with grates depressed according to the following drainage area radii:

a. Radius, 30 Inches (750 mm) or Less: Equivalent to 1 percent slope, but not less than 1/4-inch (6.35-mm) total depression.

b. Radius, 30 to 60 Inches (750 to 1500 mm): Equivalent to 1 percent slope.

c. Radius, 60 Inches (1500 mm) or Larger: Equivalent to 1 percent slope, but not greater than 1-inch (25-mm) total depression.

3. Install floor-drain flashing collar or flange so no leakage occurs between drain and adjoining flooring. Maintain integrity of waterproof membranes where penetrated.

4. Install individual traps for floor drains connected to sanitary building drain, unless otherwise indicated.

Retain one of first two paragraphs below.

F. Install roof flashing assemblies on sanitary stack vents and vent stacks that extend through roof.

G. Install flashing fittings on sanitary stack vents and vent stacks that extend through roof.

H. Assemble open drain fittings and install with top of hub [1 inch (25 mm)] [2 inches (51 mm)] <Insert dimension> above floor.

I. Install deep-seal traps on floor drains and other waste outlets, if indicated.

J. Install floor-drain, trap-seal primer fittings on inlet to floor drains that require trap-seal primer connection.

1. Exception: Fitting may be omitted if trap has trap-seal primer connection.

2. Size: Same as floor drain inlet.

K. Install air-gap fittings on draining-type backflow preventers and on indirect-waste piping discharge into sanitary drainage system.

L. Install sleeve flashing device with each riser and stack passing through floors with waterproof membrane.

Retain first paragraph below to reduce vandalism.

M. Install vent caps on each vent pipe passing through roof.

N. Install grease interceptors, including trapping, venting, and flow-control fitting, according to authorities having jurisdiction and with clear space for servicing.

Retain one or more of first three subparagraphs below.

1. Above-Floor Installation: Set unit with bottom resting on floor, unless otherwise indicated.

2. Flush with Floor Installation: Set unit and extension, if required, with cover flush with finished floor.

3. Recessed Floor Installation: Set unit in receiver housing having bottom or cradle supports, with receiver housing cover flush with finished floor.

4. Install cleanout immediately downstream from interceptors not having integral cleanout on outlet.

O. Install traps on plumbing specialty drain outlets. Omit traps on indirect wastes unless trap is indicated.

3.2 CONNECTIONS

A. Comply with requirements in Section 221316 "Sanitary Waste and Vent Piping" for piping installation requirements. Drawings indicate general arrangement of piping, fittings, and specialties.

B. Install piping adjacent to equipment to allow service and maintenance.

C. Grease Interceptors: Connect inlet and outlet to unit, and connect flow-control fitting and vent to unit inlet piping. Install valve on outlet of automatic drawoff-type unit.

3.3 FLASHING INSTALLATION

Coordinate this article with Section 076200 "Sheet Metal Flashing and Trim."

A. Fabricate flashing from single piece unless large pans, sumps, or other drainage shapes are required. Join flashing according to the following if required:

1. Lead Sheets: Burn joints of lead sheets 6.0-lb/sq. ft. (30-kg/sq. m), 0.0938-inch (2.4-mm) thickness or thicker. Solder joints of lead sheets 4.0-lb/sq. ft. (20-kg/sq. m), 0.0625-inch (1.6-mm) thickness or thinner.

B. Install sheet flashing on pipes, sleeves, and specialties passing through or embedded in floors and roofs with waterproof membrane.

1. Pipe Flashing: Sleeve type, matching pipe size, with minimum length of 10 inches (250 mm), and skirt or flange extending at least 8 inches (200 mm) around pipe.

2. Sleeve Flashing: Flat sheet, with skirt or flange extending at least 8 inches (200 mm) around sleeve.

3. Embedded Specialty Flashing: Flat sheet, with skirt or flange extending at least 8 inches (200 mm) around specialty.

C. Set flashing on floors and roofs in solid coating of bituminous cement.

D. Secure flashing into sleeve and specialty clamping ring or device.

Retain one or both paragraphs below.

E. Install flashing for piping passing through roofs with counterflashing or commercially made flashing fittings, according to Section 076200 "Sheet Metal Flashing and Trim."

F. Extend flashing up vent pipe passing through roofs and turn down into pipe, or secure flashing into cast-iron sleeve having calking recess.

3.4 LABELING AND IDENTIFYING

A. Equipment Nameplates and Signs: Install engraved plastic-laminate equipment nameplate or sign on or near each grease interceptor.

B. Distinguish among multiple units, inform operator of operational requirements, indicate safety and emergency precautions, and warn of hazards and improper operations, in addition to identifying unit. Nameplates and signs are specified in Section 220553 "Identification for Plumbing Piping and Equipment."

3.5 PROTECTION

A. Protect drains during remainder of construction period to avoid clogging with dirt or debris and to prevent damage from traffic or construction work.

B. Place plugs in ends of uncompleted piping at end of each day or when work stops.

END OF SECTION 221319

	SANITARY WASTE PIPING SPECIALTIES
	221319 - 1



