Copyright 2011 AIA
MasterSpec Professional
09/11

Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 221329 - SANITARY SEWERAGE PUMPS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

Terminology and descriptions for pumps used in this Section are from HI 1.1-1.2 and HI 3.1-3.5.

1. Submersible sewage pumps.

2. Wet-pit-volute sewage pumps.

3. Sewage-pump basins and basin covers.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product indicated.

B. Wiring Diagrams: For power, signal, and control wiring.

1.3 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

1.4 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

B. UL Compliance: Comply with UL 778 for motor-operated water pumps.

PART 2 -  PRODUCTS

2.1 SUBMERSIBLE SEWAGE PUMPS

Retain "Sewage-Pump Basins and Basin Covers" Article if retaining this article.

A. Submersible, Fixed-Position, Single-Seal Sewage Pumps:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first subparagraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Barnes; Crane Pumps & Systems.

b. Bell & Gossett Domestic Pump; ITT Corporation.

c. EBARA Fluid Handling.

d. Flo Fab inc.

e. Goulds Pumps; ITT Corporation.

f. Grundfos Pumps Corp.

g. ITT Flygt Corporation.

h. Liberty Pumps.

i. Little Giant Pump Co.

j. McDonald, A. Y. Mfg. Co.

k. PACO Pumps; Grundfos Pumps Corporation, U.S.A.

l. Peerless Pump, Inc.

m. Pentair Pump Group; Hydromatic Pumps.

n. Pentair Pump Group; Myers.

o. Swaby Manufacturing Company.

p. Weil Pump Company, Inc.

q. Weinman Division; Crane Pumps & Systems.

r. WILO-EMU USA LLC.

s. Zoeller Company.

t. <Insert manufacturer's name>.

3. Description: Factory-assembled and -tested sewage-pump unit.

4. Pump Type: Submersible, end-suction, single-stage, close-coupled, overhung-impeller, centrifugal sewage pump as defined in HI 1.1-1.2 and HI 1.3.

5. Pump Casing: Cast iron, with open inlet, legs that elevate pump to permit flow into impeller, and vertical discharge for piping connection.

If Project has more than one type or configuration of sewage pump, retain appropriate options in first subparagraph below and indicate impeller material for each pump in schedule on Drawings. See sample schedule in Evaluations.

6. Impeller: Statically and dynamically balanced, [ASTM A 48/A 48M, Class No. 25 A cast iron] [ASTM A 532/A 532M, abrasion-resistant cast iron] [ASTM B 584, cast bronze] [and] [stainless steel], nonclog, open, or semiopen design for solids handling, and keyed and secured to shaft.

7. Pump and Motor Shaft: Stainless steel [or steel], with factory-sealed, grease-lubricated ball bearings.

8. Seal: Mechanical.

9. Motor: Hermetically sealed, capacitor-start type; with built-in overload protection; lifting eye or lug; and three-conductor, waterproof power cable of length required and with grounding plug and cable-sealing assembly for connection at pump.

Verify that pump selected has motor feature in first subparagraph below, if either is required, or delete.

a. Motor Housing Fluid: [Air] [Oil].

Retain one of two "Controls" subparagraphs below.

Controls in first subparagraph below are rod-and-float type.

10. Controls:

a. Enclosure: NEMA 250, [Type 1] [Type 4X] <Insert type>.

b. Switch Type: Pedestal-mounted float switch with float rods and rod buttons.

Retain first subparagraph below for duplex pump units. Revise if unit includes three or more pumps.

c. Automatic Alternator: Start pumps on successive cycles and start multiple pumps if one cannot handle load.

d. Float Guides: Pipe or other restraint for floats and rods in basins of depth greater than 60 inches (1500 mm).

e. High-Water Alarm: Cover-mounted, compression-probe alarm, with electric bell; 120-V ac, with transformer and contacts for remote alarm bell.

Controls in first subparagraph below are float- and pressure-switch types.

11. Controls:

a. Enclosure: NEMA 250, [Type 1] [Type 4X] <Insert type>; [pedestal] [wall]-mounted.

b. Switch Type: [Mechanical-float] [Mercury-float] [Pressure] <Insert type> type, in NEMA 250, Type 6 enclosures with mounting rod and electric cables.

Retain first subparagraph below for duplex pump units. Revise if unit includes three or more pumps.

c. Automatic Alternator: Start pumps on successive cycles and start multiple pumps if one cannot handle load.

d. High-Water Alarm: Rod-mounted, NEMA 250, Type 6 enclosure with [mechanical-float, mercury-float, or pressure] <Insert type> switch matching control and electric bell; 120-V ac, with transformer and contacts for remote alarm bell.

12. Control-Interface Features:

Two subparagraphs below are optional control features.

a. Remote Alarm Contacts: For remote alarm interface.

b. Building Automation System Interface: Auxiliary contacts in pump controls for interface to building automation system and capable of providing the following:

1) On-off status of pump.

2) Alarm status.

B. Submersible, Quick-Disconnect, Double-Seal Sewage Pumps:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first subparagraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. ABS Pumps Inc.

b. Barnes; Crane Pumps & Systems.

c. Bell & Gossett Domestic Pump; ITT Corporation.

d. BJM Pumps, LLC.

e. Chicago Pump Company; a division of Yeomans Chicago Corporation.

f. EBARA Fluid Handling.

g. E.I.M. Electric Co., Ltd.

h. Federal Pump Corp.

i. Gorman-Rupp Company (The).

j. Goulds Pumps; ITT Corporation.

k. HOMA Pump Technology Inc.

l. ITT Flygt Corporation.

m. KSB Inc.

n. PACO Pumps; Grundfos Pumps Corporation, U.S.A.

o. Pentair Pump Group; Fairbanks Morse.

p. Pentair Pump Group; Hydromatic Pumps.

q. Pentair Pump Group; Myers.

r. PX Pumps USA.

s. Stancor, Inc.

t. Sta-Rite Industries, Inc.

u. Swaby Manufacturing Company.

v. Tsurumi America, Inc.

w. Weil Pump Company, Inc.

x. Weinman Division; Crane Pumps & Systems.

y. WILO-EMU USA LLC.

z. Zoeller Company.

aa. <Insert manufacturer's name>.

3. Description: Factory-assembled and -tested sewage-pump unit with guide-rail supports.

4. Pump type: Submersible, end-suction, single-stage, close-coupled, overhung-impeller, centrifugal sewage pump as defined in HI 1.1-1.2 and HI 1.3.

5. Pump Casing: Cast iron, with open inlet, and discharge fittings for connection to guide-rail support.

If Project has more than one type or configuration of sewage pump, retain appropriate options in first subparagraph below and indicate impeller material for each pump in schedule on Drawings. See sample schedule in Evaluations.

6. Impeller: Statically and dynamically balanced, [ASTM A 48/A 48M, Class No. 25 A cast iron] [ASTM A 532/A 532M, abrasion-resistant cast iron] [ASTM B 584, cast bronze] [and] [stainless steel], nonclog, open, or semiopen design for solids handling, and keyed and secured to shaft.

7. Pump and Motor Shaft: Stainless steel [or steel], with factory-sealed, grease-lubricated ball bearings.

8. Seals: Mechanical.

Verify that pump selected has feature in first subparagraph below, if required, or delete.

9. Moisture-Sensing Probe: Internal moisture sensor and moisture alarm.

10. Motor: Hermetically sealed, capacitor-start type; with built-in overload protection; lifting eye or lug; and three-conductor, waterproof power cable of length required and with grounding plug and cable-sealing assembly for connection at pump.

Verify that pump selected has motor feature in first subparagraph below, if required, or delete.

a. Motor Housing Fluid: [Air] [Oil].

Retain one of two "Controls" subparagraphs below.

Controls in first subparagraph below are rod-and-float type.

11. Controls:

a. Enclosure: NEMA 250, [Type 1] [Type 4X] <Insert type>.

b. Switch Type: Pedestal-mounted float switch with float rods and rod buttons.

Retain first subparagraph below for duplex pump units. Revise if unit includes three or more pumps.

c. Automatic Alternator: Start pumps on successive cycles and start multiple pumps if one cannot handle load.

d. Float Guides: Pipe or other restraint for floats and rods in basins of depth greater than 60 inches (1500 mm).

e. High-Water Alarm: Cover-mounted, compression-probe alarm, with electric bell; 120-V ac, with transformer and contacts for remote alarm bell.

Controls in first subparagraph below are float- and pressure-switch types.

12. Controls:

a. Enclosure: NEMA 250, [Type 1] [Type 4X] <Insert type>; [pedestal] [wall]-mounted.

b. Switch Type: [Mechanical-float] [Mercury-float] [Pressure] <Insert type> type, in NEMA 250, Type 6 enclosures with mounting rod and electric cables.

Retain first subparagraph below for duplex pump units. Revise if unit includes three or more pumps.

c. Automatic Alternator: Start pumps on successive cycles and start multiple pumps if one cannot handle load.

d. High-Water Alarm: Rod-mounted, NEMA 250, Type 6 enclosure with [mechanical-float, mercury-float, or pressure] <Insert type> switch matching control and electric bell; 120-V ac, with transformer and contacts for remote alarm bell.

13. Control-Interface Features:

First two subparagraphs below are optional control features.

a. Remote Alarm Contacts: For remote alarm interface.

b. Building Automation System Interface: Auxiliary contacts in pump controls for interface to building automation system and capable of providing the following:

1) On-off status of pump.

2) Alarm status.

14. Guide-Rail Supports:

a. Standard: SWPA's "Submersible Sewage Pumping Systems (SWPA) Handbook."

b. Guide Rails: Vertical pipes or structural members, made of galvanized steel or other corrosion-resistant metal, attached to baseplate and basin sidewall or cover.

c. Baseplate: Corrosion-resistant metal plate, attached to basin floor, supporting guide rails and stationary elbow.

d. Pump Yoke: Motor-mounted or casing-mounted yokes or other attachments for aligning pump during connection of flanges.

e. Movable Elbow: Pump discharge-elbow fitting with flange, seal, and positioning device.

f. Stationary Elbow: Fixed discharge-elbow fitting with flange that mates to movable-elbow flange and support attached to baseplate.

g. Lifting Cable: Stainless steel; attached to pump and cover at manhole.

If Project has more than one type or configuration of sewage pump, delete paragraph below and schedule sewage pumps on Drawings. See sample schedule in Evaluations.

C. Capacities and Characteristics:

1. Unit Capacity: <Insert gpm (L/minute)>.

2. Number of Pumps: [One] [Two] <Insert value>.

3. Each Pump:

a. Capacity: <Insert gpm (L/minute)>.

b. Solids Handling Capability: [Not applicable] [2 inches (50 mm)] [2-1/2 inches (65 mm)] [3 inches (75 mm)] <Insert inches (mm)> minimum.

c. Total Dynamic Head: <Insert feet (kPa)>.

d. Speed: <Insert rpm>.

e. Discharge Pipe Size: <Insert NPS (DN)>.

f. Motor Horsepower: <Insert value>.

g. Electrical Characteristics:

1) Volts: [120] [240] [277] [480] <Insert value>.

2) Phases: [Single] [Three].

3) Hertz: 60.

4. Unit Electrical Characteristics:

a. Full-Load Amperes: <Insert value>.

b. Minimum Circuit Ampacity: <Insert value>.

c. Maximum Overcurrent Protection: <Insert value> A.

2.2 WET-PIT-VOLUTE SEWAGE PUMPS

Retain "Sewage-Pump Basins and Basin Covers" Article if retaining this article.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Alyan Pump Company.

2. Armstrong Pumps Inc.

3. Chicago Pump Company; a division of Yeomans Chicago Corporation.

4. Federal Pump Corp.

5. Flo Fab inc.

6. PACO Pumps; Grundfos Pumps Corporation, U.S.A.

7. Peerless Pump, Inc..

8. Pentair Pump Group; Aurora Pump.

9. Swaby Manufacturing Company.

10. Tramco Pump Company.

11. Vertiflo Pump Company.

12. Weil Pump Company, Inc.

13. Weinman Division; Crane Pumps & Systems.

14. Yeomans Chicago Corporation.

15. <Insert manufacturer's name>.

C. Description: Factory-assembled and -tested sewage-pump unit.

D. Pump Type: Wet-pit-volute, single-stage, separately-coupled, overhung-impeller, centrifugal sewage pump as defined in HI 1.1-1.2 and HI 1.3.

E. Pump Casing: Cast iron, with open inlet and threaded or flanged connection for discharge piping.

If Project has more than one type or configuration of sewage pump, retain appropriate options in first two paragraphs below and indicate shaft and impeller material for each pump in schedule on Drawings. See sample schedule in Evaluations.

F. Pump Shaft: [Stainless-steel] [and] [steel].

G. Impeller: Statically and dynamically balanced, [ASTM A 48/A 48M, Class No. 25 A cast iron] [ASTM A 532/A 532M, abrasion-resistant cast iron] [and] [ASTM B 584, cast bronze], nonclog, open, or semiopen design for solids handling, and keyed and secured to shaft.

H. Sleeve Bearings: Bronze. Include oil-lubricated, intermediate sleeve bearings at 48-inch (1200-mm) maximum intervals if basin depth is more than 48 inches (1200 mm), and grease-lubricated, ball-type thrust bearings.

I. Pump and Motor Shaft Coupling: Flexible, capable of absorbing torsional vibration and shaft misalignment.

J. Pump Discharge Piping: Factory or field fabricated, [galvanized, ASTM A 53/A 53M, Schedule 40, steel pipe with ASME B16.1, Class 125, cast-iron flanges and flanged fittings or ASME B16.4, Class 125, gray iron threaded fittings] <Insert pipe material>.

K. Support Plate: Cast iron or coated steel and strong enough to support pumps, motors, and controls. Refer to Part 2 "Sewage-Pump Basins and Basin Covers" Article for requirements.

L. Shaft Seal: Stuffing box, with graphite-impregnated braided-yarn rings and bronze packing gland.

M. Motor: Single-speed; grease-lubricated ball bearings and mounted on vertical, cast-iron pedestal.

Retain one of two "Controls" paragraphs below.

Controls in first paragraph below are rod-and-float type.

N. Controls:

1. Enclosure: NEMA 250, [Type 1] [Type 4X] <Insert type>.

2. Switch Type: Pedestal-mounted float switch with float rods and rod buttons.

Retain first subparagraph below for duplex pump units. Revise if unit includes three or more pumps.

3. Automatic Alternator: Start pumps on successive cycles and start multiple pumps if one cannot handle load.

4. Float Guides: Pipe or other restraint for floats and rods in basins of depth greater than 60 inches (1500 mm).

5. High-Water Alarm: Cover-mounted, compression-probe alarm, with electric bell; 120-V ac, with transformer and contacts for remote alarm bell.

Controls in first paragraph below are float- and pressure-switch types.

O. Controls:

1. Enclosure: NEMA 250, [Type 1] [Type 4X] <Insert type>; [pedestal] [wall]-mounted.

2. Switch Type: [Mechanical-float] [Mercury-float] [Pressure] <Insert type> type, in NEMA 250, Type 6 enclosures with mounting rod and electric cables.

Retain first subparagraph below for duplex pump units. Revise if unit includes three or more pumps.

3. Automatic Alternator: Start pumps on successive cycles and start multiple pumps if one cannot handle load.

4. High-Water Alarm: Rod-mounted, NEMA 250, Type 6 enclosure with [mechanical-float, mercury-float, or pressure] <Insert type> switch matching control and electric bell; 120-V ac, with transformer and contacts for remote alarm bell.

P. Control-Interface Features:

Two subparagraphs below are optional control features.

1. Remote Alarm Contacts: For remote alarm interface.

2. Building Automation System Interface: Auxiliary contacts in pump controls for interface to building automation system and capable of providing the following:

a. On-off status of pump.

b. Alarm status.

If Project has more than one sewage pump, delete paragraph below and schedule sewage pumps on Drawings. See sample schedule in Evaluations.

Q. Capacities and Characteristics:

1. Unit Capacity: <Insert gpm (L/minute).>

2. Number of Pumps: [One] [Two] <Insert value>.

3. Each Pump:

a. Capacity: <Insert gpm (L/minute)>.

b. Solids Handling Capability: [2 inches (50 mm)] [2-1/2 inches (65 mm)] [3 inches (75 mm)] <Insert inches (mm)> minimum.

c. Total Dynamic Head: <Insert feet (kPa)>.

d. Speed: <Insert rpm>.

e. Discharge Pipe Size: <Insert NPS (DN)>.

f. Motor Horsepower: <Insert value>.

g. Electrical Characteristics:

1) Volts: [120] [240] [277] [480] <Insert value>.

2) Phases: [Single] [Three].

3) Hertz: 60.

4. Unit Electrical Characteristics:

a. Full-Load Amperes: <Insert value>.

b. Minimum Circuit Ampacity: <Insert value>.

c. Maximum Overcurrent Protection: <Insert value> A.

2.3 SEWAGE-PUMP BASINS AND BASIN COVERS

Retain this article if retaining one or both of "Submersible Sewage Pumps" or "Wet-Pit-Volute Sewage Pumps" articles.

Sewage pump basins typically are round with space for simplex or multiplex pumps. A reverse-flow assembly often will require a larger basin.

A. Basins: Factory-fabricated, watertight, cylindrical, basin sump with top flange and sidewall openings for pipe connections.

If Project has more than one type or configuration of sewage-pump basin, delete first subparagraph below and schedule sewage-pump basin material on Drawings. See sample schedule in Evaluations.

1. Material: [Cast iron] [Fiberglass] [Polyethylene] <Insert material>.

2. Reinforcement: Mounting plates for pumps, fittings[, guide-rail supports if used,] and accessories.

Retain subparagraph below if required to anchor basin to concrete slab in case of ground-water problems.

3. Anchor Flange: Same material as or compatible with basin sump, cast in or attached to sump, in location and of size required to anchor basin in concrete slab.

Sewage-pump basin covers typically are round with openings for simplex or multiplex pumps.

B. Basin Covers: Fabricate metal cover with openings having gaskets, seals, and bushings; for access to pumps, pump shafts, control rods, discharge piping, vent connections, and power cables.

1. Reinforcement: Steel or cast iron, capable of supporting foot traffic for basins installed in foot-traffic areas.

If Project has more than one type or configuration of sewage pump basin, delete paragraph below and schedule sewage pump basins on Drawings. See sample schedule in Evaluations.

C. Capacities and Characteristics:

1. Capacity: <Insert gal (L)>.

2. Diameter: <Insert inches (mm)>.

3. Depth: <Insert inches (mm)>.

4. Inlet No. 1:

a. Drainage Pipe Size: <Insert NPS (DN)>.

b. Bottom of Sump to Centerline: <Insert inches (mm)>.

c. Type: [Flanged] [Hubbed] [Threaded] outside.

5. Inlet No. 2:

a. Drainage Pipe Size: <Insert NPS (DN)>.

b. Bottom of Sump to Centerline: <Insert inches (mm)>.

c. Type: [Flanged] [Hubbed] [Threaded] outside.

6. Inlet No. 3:

a. Drainage Pipe Size: <Insert NPS (DN)>.

b. Bottom of Sump to Centerline: <Insert inches (mm)>.

c. Type: [Flanged] [Hubbed] [Threaded] outside.

7. Sidewall Outlet:

a. Discharge Pipe Size: <Insert NPS (DN)>.

b. Bottom of Sump to Centerline: <Insert inches (mm)>.

c. Type: [Hubbed inside] [Hubbed outside] <Insert type>.

8. Cover Material: [Cast iron] [Steel with bituminous coating] [Cast iron or steel with bituminous coating] <Insert material>.

9. Cover Diameter: <Insert inches (mm)>, but not less than outside diameter of basin top flange.

10. Manhole Required in Cover: [Yes] [No].

11. Vent Size: <Insert NPS (DN)>.

2.4 MOTORS

Default motor characteristics are specified in Section 220513 "Common Motor Requirements for Plumbing Equipment."

A. Comply with NEMA designation, temperature rating, service factor, enclosure type, and efficiency requirements for motors specified in Section 220513 "Common Motor Requirements for Plumbing Equipment."

1. Motor Sizes: Minimum size as indicated. If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

B. Motors for submersible pumps shall be hermetically sealed.

PART 3 -  EXECUTION

3.1 EARTHWORK

A. Excavation and filling are specified in Section 312000"Earth Moving."

3.2 INSTALLATION

A. Pump Installation Standard: Comply with HI 1.4 for installation of centrifugal pumps.

END OF SECTION 221329

	SANITARY SEWERAGE PUMPS
	221329 - 1



