Copyright 2010 AIA
MasterSpec Professional
03/10

Copyright 2010 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 221353 - FACILITY SEPTIC TANKS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Septic tanks.

2. Distribution boxes.

3. Pipe and fittings.

4. Absorption systems.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product indicated.

1. Include construction details, material descriptions, dimensions of individual components, and profiles.

2. Include manhole openings, covers, and pipe connections.

B. Shop Drawings: For [trench absorption systems] [bed absorption systems].

1. Include manhole openings, covers, pipe connections, and accessories.

2. Include piping with sizes and invert elevations.

3. Include underground structures.

4. Include other utilities.

PART 2 -  PRODUCTS

2.1 CONCRETE SEPTIC TANKS

A. Description: ASTM C 1227, precast, reinforced-concrete tank and covers; [single chamber] [single chamber with internal baffle] [two chambers].

Verify availability of retained option in first paragraph below.

B. Design: For [A-8 (H10-44)] [A-12 (HS15-44)] [A-16 (HS20-44)] traffic loading according to ASTM C 890.

Verify availability of retained option in first paragraph below.

C. Manholes: [20-inch- (508-mm-)] [22-inch- (559-mm-)] [24-inch- (610-mm-)] <Insert size> minimum diameter opening with reinforced-concrete risers to grade and access lid with steel lift rings. Include manhole in center of each septic tank compartment top.

Filter access in first paragraph below is an optional component.

D. Filter Access: Reinforced-concrete access hole, large enough to remove filter, over filter position.

E. Inlet and Outlet Access: [12-inch (305-mm)] <Insert size> minimum diameter, reinforced-concrete access lids with steel lift rings. Include access centered over inlet and outlet.

Resilient connectors in first paragraph below are optional components.

F. Resilient Connectors: ASTM C 923 (ASTM C 923M), of size required for piping, fitted into inlet and outlet openings.

If more than one septic tank is required on Project, delete paragraph and subparagraphs below and schedule septic tanks on Drawings.

G. Capacity and Characteristics:

1. Capacity: <Insert gal. (L)>.

2. Inlet and Outlet Size: <Insert NPS (DN)>.

2.2 POLYETHYLENE SEPTIC TANKS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Chem-Tainer Industries.

2. Norwesco, Inc.

3. Plastic-Mart, Inc.

4. Premier Plastics Ltd.

5. Premier Tech Environment.

6. <Insert manufacturer's name>.

Retain one of three options in first paragraph below. Retain one of first two options for single-chamber tanks and third option for two-chamber tanks. Verify that tanks with baffle are available before retaining option in first paragraph below.

C. Description: Molded, HDPE or PE construction; fabricated for septic tank application; [single chamber] [single chamber with baffle and at least one access riser and manhole] [two chambers each with an access riser and manhole].

Verify availability of retained option in first paragraph below. Access for PE septic tanks is usually small.

D. Manholes: [18-inch- (457-mm-)] [20-inch- (508-mm-)] [22-inch- (559-mm-)] <Insert size> minimum diameter opening with HDPE or PE access risers to grade and cover.

Filter access in first paragraph below is an optional component.

E. Filter Access: Include access hole, large enough to remove filter, over filter position.

Resilient connectors in first paragraph below are optional components.

F. Resilient Connectors: ASTM C 923 (ASTM C 923M) or other watertight seal, of size required for piping, fitted into inlet and outlet openings.

If more than one septic tank is required on Project, delete paragraph and subparagraphs below and schedule septic tanks on Drawings.

G. Capacity and Characteristics:

1. Capacity: <Insert gal. (L)>.

2. Inlet and Outlet Size: <Insert NPS (DN)>.

2.3 FILTERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Premier Tech Environment.

2. Tuf-Tite Corporation.

3. Zabel Industries International, Ltd.; a Polylok company.

4. <Insert manufacturer's name>.

Filters in this article are not usually required; retain only if required. Filter units below are for NPS 4 (DN 100) inlet and outlet. They are available with housings in at least 4-, 8-, and 12-inch (102-, 203-, and 305-mm) diameter sizes.

C. Description: Removable, septic-tank-outlet filter that restricts discharge solids to 1/8 inch (3.2 mm).

D. Housing: HDPE or PVC.

E. Outlet Size: [NPS 4 (DN 100)] [NPS 6 (DN 150)] <Insert NPS (DN)>.

2.4 CONCRETE DISTRIBUTION BOXES

A. Description: Precast concrete, single-chamber box and cover.

Baffle option in first paragraph below is not required for gravity flow.

B. Design: Made according to ASTM C 913, and for [A-8 (H10-44)] [A-12 (HS15-44)] [A-16 (HS20-44)] traffic loading according to ASTM C 890.[ Include baffle opposite inlet].

C. Manholes: [20-inch- (508-mm-)] [22-inch- (559-mm-)] [24-inch- (610-mm-)] <Insert size> minimum diameter opening with reinforced-concrete risers to grade and cover with steel lift rings in center of distribution box cover.

D. Resilient Connectors: ASTM C 923 (ASTM C 923M), of size required for piping, fitted into inlet and outlet openings. Include watertight plugs in outlets not required.

If more than one distribution box is required on Project, delete paragraph and subparagraphs below and schedule distribution boxes on Drawings.

E. Capacity and Characteristics:

1. Inlet Size: <Insert NPS (DN)>.

2. Number of Outlets: [Two] [Three] [Four] <Insert number>.

3. Outlet Size: <Insert NPS (DN)>.

2.5 PE DISTRIBUTION PIPE AND FITTINGS

A. Tube and Fittings: ASTM F 405, perforated corrugated tube with solid-wall fittings.

B. Couplings: PE band, matching tube and fitting dimensions.

2.6 NONPRESSURE PIPE COUPLINGS

A. Description: Comply with ASTM C 1173, elastomeric, sleeve-type, reducing or transition coupling, for joining underground nonpressure piping. Include ends of same sizes as piping to be joined, with corrosion-resistant-metal tension band and tightening mechanism on each end.

1. Sleeve Materials for Plastic Pipes: ASTM F 477, elastomeric seal or ASTM D 5926, PVC.

2. Sleeve Materials for Dissimilar Pipes: ASTM D 5926, PVC or other material compatible with pipe materials being joined.

2.7 [TRENCH] [BED] ABSORPTION-SYSTEM MATERIALS

A. Filter Material: ASTM D 448, Size No. 24, 3/4 to 2-1/2 inches (19 to 63 mm), washed, crushed stone or gravel; or broken, hard-burned clay brick.

B. Filter Mat: [Geotextile woven or spun filter fabric, in one or more layers, for minimum total unit weight of 3 oz./sq. yd. (101 g/sq. m)] [Untreated building paper or similar porous material].

C. Cover for Distribution Pipe: Geotextile woven filter fabric, in one or more layers, for minimum total unit weight of 3 oz./sq. yd. (101 g/sq. m).

D. Fill Material: Soil removed from trench.

PART 3 -  EXECUTION

3.1 EARTHWORK

A. Excavating, trenching, and backfilling for piping is specified in Section 312000 "Earth Moving."

1. Stockpile topsoil for reuse in finish grading without intermixing with other excavated material. Stockpile materials away from edge of excavation and do not store within drip line of remaining trees.

2. Place, grade, and shape stockpiles to drain surface water. Cover to prevent windblown dust.

B. Excavating and Backfilling for Septic Tanks:

1. Excavate sufficient width and length for tanks to depth determined by tank inlet elevation. Provide level bottom.

2. Backfill with excavated soil, mounding soil above original grade without compacting.

Retain first paragraph below for trench absorption systems with distribution piping. Coordinate with Drawings.

C. Excavating and Backfilling for Trench Absorption Systems:

If dimensions are included on Drawings, delete first subparagraph below.

1. Excavate for trench absorption systems 30 inches (762 mm) wide and 24 inches (610 mm) deep, minimum.

2. Backfill with excavated soil, mounding soil above original grade without compacting.

Retain paragraph below for bed absorption systems with distribution piping. Coordinate with Drawings.

D. Excavating and Backfilling for Bed Absorption Systems:

1. Excavate for bed absorption systems of width indicated and 24 inches (610 mm) deep, minimum.

If dimensions are included on Drawings, delete subparagraph below.

2. Backfill with excavated soil, mounding soil above original grade without compacting.

3.2 SEPTIC TANK INSTALLATION

A. Install precast concrete septic tanks according to ASTM C 891.

B. Install septic tanks level.

Retain first paragraph below if FRP or PE septic tanks will be installed in a flood plain. Detail pad on Drawings.

C. Connect septic tank to concrete ballast pad.

D. Install filter in septic tank outlet. Secure filter to septic tank wall. Make direct connections to distribution piping.

Retain first paragraph below only if required for freeze protection.

E. Install insulation on exterior sides and top of septic tank. Comply with requirements for insulation specified in Section 220716 "Plumbing Equipment Insulation."

F. Fill septic tank with water.

3.3 DISTRIBUTION BOX INSTALLATION

A. Install precast-concrete distribution boxes according to ASTM C 891 and at invert elevations indicated. Set level and plumb.

3.4 PIPING INSTALLATION

A. Comply with requirements for sewer pipe installation specified in Section 221313 "Facility Sanitary Sewers."

B. Install distribution piping according to the following:

1. Use perforated pipe and fittings for [trench] [bed] absorption systems with perforations at bottom.

2. PE Tube and Fittings: ASTM F 481.

3.5 PIPE JOINT CONSTRUCTION

A. Join distribution piping with or according to the following:

1. Install pipe and fittings for [trench] [bed] absorption systems with closed joints unless otherwise indicated.

2. PE Tube and Fittings: With PE band couplings.

B. Join dissimilar pipe materials according to ASTM D 5926, with couplings and gaskets compatible with pipe materials being joined.

3.6 CLEANOUT INSTALLATION

A. Install cleanouts according to the following:

Revise list below to suit Project.

1. Inlet and Outlet of Septic Tanks: Cast-iron cleanouts.

2. Inlet and Outlet of Dosing Tanks: Cast-iron cleanouts.

3. Inlet and Outlet of Distribution Boxes: [Cast-iron] [PVC] cleanouts.

4. At Each Change in Direction of Sewer Piping: [Cast-iron] [PVC] cleanouts.

5. At Ends of Each Row[ and at Each Change in Direction] of Distribution Piping: [Cast-iron] [PVC] cleanouts.

B. Comply with requirements for cleanouts specified in Section 221313 "Facility Sanitary Sewers."

Installation method in first paragraph below is suitable for vehicular-traffic areas.

C. Cast-Iron Cleanouts: Install with PVC riser from sewer and distribution piping to cast-iron cleanout housing at grade. Use NPS 4 (DN 100) PVC sewer pipe and fittings with solvent-cemented joints for risers. Attach riser to cleanout housing with rubber gasket or coupling.

D. PVC Cleanouts: Install with PVC riser from sewer and distribution piping to PVC cleanout at grade. Use NPS 4 (DN 100) PVC sewer pipe and fittings with solvent-cemented joints for risers and cleanout fitting.

E. Cleanout Support: Set cleanouts in concrete blocks [18-by-18-by-12-inches (457-by-457-by-305-mm)] <Insert dimensions> deep unless location is in concrete pavement. Formwork, reinforcement, and concrete are specified in [Section 033000 "Cast-in-Place Concrete."] [Section 033053 "Miscellaneous Cast-in-Place Concrete."]

F. Set top of cleanout [1 inch (25 mm)] [2 inches (51 mm)] above surrounding rough grade, or set flush with grade if installed in pavement.

3.7 [TRENCH] [BED] ABSORPTION-SYSTEM INSTALLATION

A. Filter Material: Place supporting layer of filter material over the compacted [trench] [bed] base to a compacted depth not less than 6 inches (152 mm) below bottom of pipe.

Retain first paragraph below if sewer piping should be installed at a certain slope or installed level.

B. Install sewer piping [at minimum slope of 1 percent and maximum slope of 2 percent] [at no slope] <Insert slope>.

Piping in first paragraph below is to be installed level.

C. Install distribution piping solidly bedded in filter material, with full bearing for each pipe section throughout its length. Maintain pipe alignment with no slope.

1. Install perforated pipe with perforations down and joints tightly closed. Install couplings as required.

2. Install elbow fittings with tight joints.

Retain subparagraph below if dimensions are not shown on Drawings; otherwise, delete. Coordinate with Drawings.

3. Install absorption-system materials as follows from surface of excavation to grade:

Retain one of first two subparagraphs below.

a. Trench Size: [12 inches (305 mm)] [36 inches (914 mm)] <Insert value> wide by <Insert value> long.

b. Bed Size: <Insert value> wide with distribution piping [36 inches (914 mm) minimum] <Insert value> apart by <Insert value> long.

c. Bottom Filter Material Layer: [6 inches (152 mm)] [8 inches (203 mm)] <Insert value> thick below distribution piping.

d. Intermediate Filter Material Layer: OD of distribution piping.

e. Top Filter Material Layer: [6-inch (152-mm)] [8-inch (203-mm)] <Insert value> minimum thickness above distribution piping.

f. Filter Mat: Above final filter-material layer.

g. Fill: Above filter mat to final grade.

D. Install filter mat over filter material before backfilling.

3.8 IDENTIFICATION

A. Identification materials and their installation are specified in Section 312000 "Earth Moving." Arrange for installation of green, detectable warning tape directly over piping, at outside edges of underground structures, and at outside edges of absorption systems.

3.9 FIELD QUALITY CONTROL

Percolation tests and site survey information are provided by Owner before start of Project design. Delete first paragraph below if not required.

A. System Tests: Perform testing of completed septic tank system piping and structures according to authorities having jurisdiction.

B. Additional Tests: Fill underground structures with water and let stand overnight. If water level recedes, locate and repair leaks and retest. Repeat tests and repairs until no leaks exist.

3.10 CLEANING

A. Clear interior of piping and structures of dirt and other superfluous material as work progresses.

B. Maintain swab or drag in piping, and pull past each joint as it is completed. Place plugs in ends of uncompleted pipe at end of workday or when work stops.

END OF SECTION 221353

	FACILITY SEPTIC TANKS
	221353 - 1



