Copyright 2010 AIA
MasterSpec Professional
03/10

Copyright 2010 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 221413 - FACILITY STORM DRAINAGE PIPING
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Pipe, tube, and fittings.

2. Specialty pipe fittings.

B. Related Section:

Retain Section in subparagraph below that contains requirements Contractor might expect to find in this Section but are specified in other Sections.

1. Section 334100 "Storm Utility Drainage Piping" for storm drainage piping outside the building.

1.2 PERFORMANCE REQUIREMENTS

Retain paragraph below with "Seismic Qualification Certificates" Paragraph in "Informational Submittals" Article for projects requiring seismic design. Model building codes and ASCE/SEI 7 establish criteria for buildings subject to earthquake motions. Verify requirements of authorities having jurisdiction.

A. Seismic Performance: Storm drainage piping and support and installation shall withstand the effects of earthquake motions determined according to [ASCE/SEI 7] <Insert requirement>.

1.3 ACTION SUBMITTALS

A. Product Data: For each type of product indicated.

B. LEED Submittals:

"Product Data for Credit IEQ 4.1" Subparagraph below applies to LEED-NC, LEED-CI, and LEED-CS; coordinate with requirements for solvent cements and adhesive primers.

1. Product Data for Credit IEQ 4.1: For solvent cements and adhesive primers, documentation including printed statement of VOC content.

"Laboratory Test Reports for Credit IEQ 4" Subparagraph below applies to LEED for Schools.

2. Laboratory Test Reports for Credit IEQ 4: For solvent cements and adhesive primers, documentation indicating that products comply with the testing and product requirements of the California Department of Health Services' "Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers."

1.4 INFORMATIONAL SUBMITTALS

Retain first paragraph below if required by seismic criteria applicable to Project. Coordinate with Section 220548 "Vibration and Seismic Controls for Plumbing Piping and Equipment." See ASCE/SEI 7 for certification requirements for equipment and components.

A. Seismic Qualification Certificates: For storm drainage piping, accessories, and components, from manufacturer.

B. Field quality-control reports.

1.5 QUALITY ASSURANCE

A. Piping materials shall bear label, stamp, or other markings of specified testing agency.

Retain paragraph below if NSF markings are required.

B. Comply with NSF/ANSI 14, "Plastics Piping System Components and Related Materials," for plastic piping components. Include marking with "NSF-drain" for plastic drain piping and "NSF-sewer" for plastic sewer piping.

PART 2 -  PRODUCTS

2.1 PIPING MATERIALS

See "Writing Guide" Article in the Evaluations for a discussion of this Section's organization and the most efficient way to revise this Section. See piping materials articles in the Evaluations for a discussion of piping materials covered by referenced standards.

A. Comply with requirements in "Piping Schedule" Article for applications of pipe, tube, fitting materials, and joining methods for specific services, service locations, and pipe sizes.

2.2 HUB-AND-SPIGOT, CAST-IRON SOIL PIPE AND FITTINGS

Pipe and fittings in this article are available in NPS 2 to NPS 15 (DN 50 to DN 375).

A. Pipe and Fittings: ASTM A 74, Service class.

B. Gaskets: ASTM C 564, rubber.

2.3 HUBLESS, CAST-IRON SOIL PIPE AND FITTINGS

Pipe in first paragraph below is available in NPS 1-1/2 to NPS 15 (DN 40 to DN 375).

A. Pipe and Fittings: ASTM A 888 or CISPI 301.

Retain one or both of two paragraphs below. If retaining more than one, indicate location of each type on Drawings. Couplings in first paragraph below are economical and are made in NPS 1-1/2 to NPS 15 (DN 40 to DN 375). They may not be suitable for installation in corrosive soil.

B. CISPI, Hubless-Piping Couplings:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. ANACO-Husky.

b. Dallas Specialty & Mfg. Co.

c. Fernco Inc.

d. Matco-Norca, Inc.

e. MIFAB, Inc.

f. Mission Rubber Company; a division of MCP Industries, Inc.

g. Stant.

h. Tyler Pipe.

i. <Insert manufacturer's name>.

2. Standards: ASTM C 1277 and CISPI 310.

3. Description: Stainless-steel corrugated shield with stainless-steel bands and tightening devices; and ASTM C 564, rubber sleeve with integral, center pipe stop.

Couplings in paragraph below are made in NPS 1-1/2 to NPS 15 (DN 40 to DN 375).

C. Heavy-Duty, Hubless-Piping Couplings:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. ANACO-Husky.

b. Clamp-All Corp.

c. Dallas Specialty & Mfg. Co.

d. MIFAB, Inc.

e. Mission Rubber Company; a division of MCP Industries, Inc.

f. Stant.

g. Tyler Pipe.

h. <Insert manufacturer's name>.

2. Standards: ASTM C 1277 and ASTM C 1540.

3. Description: Stainless-steel shield with stainless-steel bands and tightening devices; and ASTM C 564, rubber sleeve with integral, center pipe stop.

2.4 COPPER TUBE AND FITTINGS

Tube and fittings in first two paragraphs below are available in NPS 1-1/4 to NPS 8 (DN 32 to DN 200).

A. Copper DWV Tube: ASTM B 306, drainage tube, drawn temper.

B. Copper Drainage Fittings: ASME B16.23, cast-copper fittings or ASME B16.29, wrought-copper, solder-joint fittings.

Flanges in first paragraph below are available in NPS 1/4 to at least NPS 6 (DN 8 to at least DN 150).

C. Copper Flanges: ASME B16.24, Class 150, cast copper with solder-joint end.

1. Flange Gasket Materials: ASME B16.21, full-face, flat, nonmetallic, asbestos-free, 1/8-inch (3.2-mm) maximum thickness unless thickness or specific material is indicated.

2. Flange Bolts and Nuts: ASME B18.2.1, carbon steel unless otherwise indicated.

D. Solder: ASTM B 32, lead free with ASTM B 813, water-flushable flux.

2.5 ABS PIPE AND FITTINGS

Pipe and fittings in this article are available in NPS 1-1/4 to NPS 6 (DN 32 to DN 150). Retain one or both of first two paragraphs below and coordinate with "Piping Schedule" Article.

A. Solid-Wall ABS Pipe: ASTM D 2661, Schedule 40.

B. Cellular-Core ABS Pipe: ASTM F 628, Schedule 40.

C. ABS Socket Fittings: ASTM D 2661, made to ASTM D 3311, drain, waste, and vent patterns.

D. Solvent Cement: ASTM D 2235.

One or both subparagraphs below may be required to comply with Project requirements or authorities having jurisdiction. Retain first subparagraph below if required for LEED-NC, LEED-CI, or LEED-CS Credit IEQ 4.1.

1. ABS solvent cement shall have a VOC content of 325 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

Retain subparagraph below if required for LEED for Schools.

2. Solvent cement shall comply with the testing and product requirements of the California Department of Health Services' "Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers."

2.6 PVC PIPE AND FITTINGS

Pipe and fittings in this article are available in NPS 1-1/4 to NPS 12 (DN 32 to DN 300). Retain one or both of first two paragraphs below and coordinate with "Piping Schedule" Article.

A. Solid-Wall PVC Pipe: ASTM D 2665, drain, waste, and vent.

B. Cellular-Core PVC Pipe: ASTM F 891, Schedule 40.

C. PVC Socket Fittings: ASTM D 2665, made to ASTM D 3311, drain, waste, and vent patterns and to fit Schedule 40 pipe.

D. Adhesive Primer: ASTM F 656.

One or both subparagraphs below may be required to comply with Project requirements or authorities having jurisdiction. Retain first subparagraph below if required for LEED-NC, LEED-CI, or LEED-CS Credit IEQ 4.1.

1. Adhesive primer shall have a VOC content of 550 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

Retain subparagraph below if required for LEED for Schools.

2. Adhesive primer shall comply with the testing and product requirements of the California Department of Health Services' "Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers."

E. Solvent Cement: ASTM D 2564.

One or both subparagraphs below may be required to comply with Project requirements or authorities having jurisdiction. Retain first subparagraph below if required for LEED-NC, LEED-CI, or LEED-CS Credit IEQ 4.1.

1. PVC solvent cement shall have a VOC content of 510 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

Retain subparagraph below if required for LEED for Schools.

2. Solvent cement shall comply with the testing and product requirements of the California Department of Health Services' "Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers."

2.7 SPECIALTY PIPE FITTINGS

A. Transition Couplings:

1. General Requirements: Fitting or device for joining piping with small differences in OD's or of different materials. Include end connections same size as and compatible with pipes to be joined.

Retain pipe couplings in three subparagraphs below if dissimilar piping materials or piping with small differences in OD must be joined.

2. Fitting-Type Transition Couplings: Manufactured piping coupling or specified-piping-system fitting.

Couplings in first subparagraph below are for underground nonpressure piping and should be available in all sizes.

3. Unshielded, Nonpressure Transition Couplings:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. See Section 016000 "Product Requirements."

a. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1) Dallas Specialty & Mfg. Co.

2) Fernco Inc.

3) Mission Rubber Company; a division of MCP Industries, Inc.

4) Plastic Oddities; a division of Diverse Corporate Technologies, Inc.

5) <Insert manufacturer's name>.

b. Standard: ASTM C 1173.

c. Description: Elastomeric, sleeve-type, reducing or transition pattern. Include shear ring and corrosion-resistant-metal tension band and tightening mechanism on each end.

d. Sleeve Materials:

1) For Cast-Iron Soil Pipes: ASTM C 564, rubber.

2) For Plastic Pipes: ASTM F 477, elastomeric seal or ASTM D 5926, PVC.

3) For Dissimilar Pipes: ASTM D 5926, PVC or other material compatible with pipe materials being joined.

Couplings in subparagraph below are for aboveground nonpressure piping and should be available in most sizes.

4. Shielded, Nonpressure Transition Couplings:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. See Section 016000 "Product Requirements."

a. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1) Cascade Waterworks Mfg. Co.

2) Mission Rubber Company; a division of MCP Industries, Inc.

3) <Insert manufacturer's name>.

b. Standard: ASTM C 1460.

c. Description: Elastomeric or rubber sleeve with full-length, corrosion-resistant outer shield and corrosion-resistant-metal tension band and tightening mechanism on each end.

PART 3 -  EXECUTION

3.1 EARTH MOVING

A. Comply with requirements for excavating, trenching, and backfilling specified in Section 312000 "Earth Moving."

3.2 PIPING INSTALLATION

See "Writing Guide" Article in the Evaluations for a discussion of how this Section is organized and the most efficient way to revise this Section.

A. Drawing plans, schematics, and diagrams indicate general location and arrangement of piping systems. Indicated locations and arrangements were used to size pipe and calculate friction loss, expansion, pump sizing, and other design considerations. Install piping as indicated unless deviations from layout are approved on coordination drawings.

B. Install piping in concealed locations unless otherwise indicated and except in equipment rooms and service areas.

C. Install piping indicated to be exposed and piping in equipment rooms and service areas at right angles or parallel to building walls. Diagonal runs are prohibited unless specifically indicated otherwise.

D. Install piping above accessible ceilings to allow sufficient space for ceiling panel removal.

E. Install piping at indicated slopes.

F. Install piping free of sags and bends.

G. Install fittings for changes in direction and branch connections.

Retain first paragraph below if piping is required to withstand specific design loads.

H. Install seismic restraints on piping. Comply with requirements for seismic-restraint devices specified in Section 220548 "Vibration and Seismic Controls for Plumbing Piping and Equipment."

I. Make changes in direction for storm drainage piping using appropriate branches, bends, and long-sweep bends. Do not change direction of flow more than 90 degrees. Use proper size of standard increasers and reducers if pipes of different sizes are connected. Reducing size of drainage piping in direction of flow is prohibited.

J. Lay buried building storm drainage piping beginning at low point of each system. Install true to grades and alignment indicated, with unbroken continuity of invert. Place hub ends of piping upstream. Install required gaskets according to manufacturer's written instructions for use of lubricants, cements, and other installation requirements. Maintain swab in piping and pull past each joint as completed.

K. Install storm drainage piping at the following minimum slopes unless otherwise indicated:

Revise two subparagraphs below as required by authorities having jurisdiction.

1. Building Storm Drain: [1 percent] [2 percent] <Insert slope> downward in direction of flow for piping NPS 3 (DN 80) and smaller; [1 percent] [2 percent] <Insert slope> downward in direction of flow for piping NPS 4 (DN 100) and larger.

2. Horizontal Storm-Drainage Piping: [2 percent] <Insert slope> downward in direction of flow.

L. Install cast-iron soil piping according to CISPI's "Cast Iron Soil Pipe and Fittings Handbook," Chapter IV, "Installation of Cast Iron Soil Pipe and Fittings."

Retain subparagraph below if piping will be in corrosive soil.

1. Install encasement on underground piping according to ASTM A 674 or AWWA C105.

M. Install aboveground copper tubing according to CDA's "Copper Tube Handbook."

N. Install aboveground ABS piping according to ASTM D 2661.

O. Install aboveground PVC piping according to ASTM D 2665.

P. Install underground [ABS] [and] [PVC] piping according to ASTM D 2321.

Q. Plumbing Specialties:

1. Install backwater valves in storm drainage gravity-flow piping. Comply with requirements for backwater valves specified in Section 221423 "Storm Drainage Piping Specialties."

2. Install cleanouts at grade and extend to where building storm drains connect to building storm sewers in storm drainage gravity-flow piping. Install cleanout fitting with closure plug inside the building in storm drainage force-main piping. Comply with requirements for cleanouts specified in Section 221423 "Storm Drainage Piping Specialties."

3. Install drains in storm drainage gravity-flow piping. Comply with requirements for drains specified in Section 221423 "Storm Drainage Piping Specialties."

R. Do not enclose, cover, or put piping into operation until it is inspected and approved by authorities having jurisdiction.

S. Install sleeves for piping penetrations of walls, ceilings, and floors. Comply with requirements for sleeves specified in Section 220517 "Sleeves and Sleeve Seals for Plumbing Piping."

Retain first paragraph below for piping that penetrates an exterior concrete wall or concrete slab.

T. Install sleeve seals for piping penetrations of concrete walls and slabs. Comply with requirements for sleeve seals specified in Section 220517 "Sleeves and Sleeve Seals for Plumbing Piping."

U. Install escutcheons for piping penetrations of walls, ceilings, and floors. Comply with requirements for escutcheons specified in Section 220518 "Escutcheons for Plumbing Piping."

3.3 JOINT CONSTRUCTION

A. Join hub-and-spigot, cast-iron soil piping with gasketed joints according to CISPI's "Cast Iron Soil Pipe and Fittings Handbook" for compression joints.

B. Join hubless, cast-iron soil piping according to CISPI 310 and CISPI's "Cast Iron Soil Pipe and Fittings Handbook" for hubless-piping coupling joints.

C. Join copper tube and fittings with soldered joints according to ASTM B 828 procedure. Use ASTM B 813, water-flushable, lead-free flux and ASTM B 32, lead-free-alloy solder.

D. Flanged Joints: Align bolt holes. Select appropriate gasket material, size, type, and thickness. Install gasket concentrically positioned. Use suitable lubricants on bolt threads. Torque bolts in cross pattern.

E. Plastic, Nonpressure-Piping, Solvent-Cemented Joints: Clean and dry joining surfaces. Join pipe and fittings according to the following:

1. Comply with ASTM F 402 for safe-handling practice of cleaners, primers, and solvent cements.

2. ABS Piping: Join according to ASTM D 2235 and ASTM D 2661 Appendixes.

3. PVC Piping: Join according to ASTM D 2855 and ASTM D 2665 Appendixes.

3.4 SPECIALTY PIPE FITTING INSTALLATION

A. Transition Couplings:

1. Install transition couplings at joints of piping with small differences in OD's.

2. In Drainage Piping: [Unshielded] [Shielded], nonpressure transition couplings.

3.5 VALVE INSTALLATION

A. Backwater Valves: Install backwater valves in piping subject to backflow.

1. Horizontal Piping: Horizontal backwater valves.[ Use normally closed type unless otherwise indicated.]

2. Install backwater valves in accessible locations.

3. Comply with requirements for backwater valves specified in Section 221423 "Storm Drainage Piping Specialties."

3.6 HANGER AND SUPPORT INSTALLATION

Retain first paragraph below if Project is in seismic area.

A. Comply with requirements for seismic-restraint devices specified in Section 220548 "Vibration and Seismic Controls for Plumbing Piping and Equipment."

B. Comply with requirements for pipe hanger and support devices and installation specified in Section 220529 "Hangers and Supports for Plumbing Piping and Equipment."

1. Install [carbon-steel] <Insert material> pipe hangers for horizontal piping in noncorrosive environments.

2. Install [stainless-steel] [fiberglass] pipe hangers for horizontal piping in corrosive environments.

3. Install [carbon-steel] <Insert material> pipe support clamps for vertical piping in noncorrosive environments.

4. Install stainless-steel pipe support clamps for vertical piping in corrosive environments.

5. Vertical Piping: MSS Type 8 or Type 42, clamps.

6. Individual, Straight, Horizontal Piping Runs:

a. 100 Feet (30 m) and Less: MSS Type 1, adjustable, steel clevis hangers.

b. Longer Than 100 Feet (30 m): MSS Type 43, adjustable roller hangers.

c. Longer Than 100 Feet (30 m) if Indicated: MSS Type 49, spring cushion rolls.

7. Multiple, Straight, Horizontal Piping Runs 100 Feet (30 m) or Longer: MSS Type 44, pipe rolls. Support pipe rolls on trapeze.

8. Base of Vertical Piping: MSS Type 52, spring hangers.

C. Support horizontal piping and tubing within 12 inches (300 mm) of each fitting[, valve,] and coupling.

D. Support vertical piping and tubing at base and at each floor.

E. Rod diameter may be reduced one size for double-rod hangers, with 3/8-inch (10-mm) minimum rods.

Maximum spans in remaining paragraphs were taken from MSS SP-69 for water service and from model plumbing codes. The most restrictive piping and spacing dimensions allowed are shown.

F. Install hangers for cast-iron soil piping with the following maximum horizontal spacing and minimum rod diameters:

1. NPS 1-1/2 and NPS 2 (DN 40 and DN 50): 60 inches (1500 mm) with 3/8-inch (10-mm) rod.

2. NPS 3 (DN 80): 60 inches (1500 mm) with 1/2-inch (13-mm) rod.

3. NPS 4 and NPS 5 (DN 100 and DN 125): 60 inches (1500 mm) with 5/8-inch (16-mm) rod.

4. NPS 6 and NPS 8 (DN 150 and DN 200): 60 inches (1500 mm) with 3/4-inch (19-mm) rod.

5. NPS 10 and NPS 12 (DN 250 and DN 300): 60 inches (1500 mm) with 7/8-inch (22-mm) rod.

6. Spacing for 10-foot (3-m) pipe lengths may be increased to 10 feet (3 m). Spacing for fittings is limited to 60 inches (1500 mm).

G. Install supports for vertical cast-iron soil piping every 15 feet (4.5 m).

H. Install hangers for copper tubing with the following maximum horizontal spacing and minimum rod diameters:

1. NPS 1-1/4 (DN 32): 72 inches (1800 mm) with 3/8-inch (10-mm) rod.

2. NPS 1-1/2 and NPS 2 (DN 40 and DN 50): 96 inches (2400 mm) with 3/8-inch (10-mm) rod.

3. NPS 2-1/2 (DN 65): 108 inches (2700 mm) with 1/2-inch (13-mm) rod.

4. NPS 3 to NPS 5 (DN 80 to DN 125): 10 feet (3 m) with 1/2-inch (13-mm) rod.

5. NPS 6 (DN 150): 10 feet (3 m) with 5/8-inch (16-mm) rod.

6. NPS 8 (DN 200): 10 feet (3 m) with 3/4-inch (19-mm) rod.

I. Install supports for vertical copper tubing every 10 feet (3 m).

J. Install hangers for [ABS] [and] [PVC] piping with the following maximum horizontal spacing and minimum rod diameters:

1. NPS 1-1/2 and NPS 2 (DN 40 and DN 50): 48 inches (1200 mm) with 3/8-inch (10-mm) rod.

2. NPS 3 (DN 80): 48 inches (1200 mm) with 1/2-inch (13-mm) rod.

3. NPS 4 and NPS 5 (DN 100 and DN 125): 48 inches (1200 mm) with 5/8-inch (16-mm) rod.

4. NPS 6 and NPS 8 (DN 150 and DN 200): 48 inches (1200 mm) with 3/4-inch (19-mm) rod.

5. NPS 10 and NPS 12 (DN 250 and DN 300): 48 inches (1200 mm) with 7/8-inch (22-mm) rod.

K. Install supports for vertical [ABS] [and] [PVC] piping every 48 inches (1200 mm).

L. Support piping and tubing not listed above according to MSS SP-69 and manufacturer's written instructions.

3.7 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified. If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Drawings indicate general arrangement of piping, fittings, and specialties.

B. Connect interior storm drainage piping to exterior storm drainage piping. Use transition fitting to join dissimilar piping materials.

C. Connect storm drainage piping to roof drains and storm drainage specialties.

1. Install test tees (wall cleanouts) in conductors near floor, and floor cleanouts with cover flush with floor.

Pit installation option in first subparagraph below should be detailed on Drawings.

2. Install horizontal backwater valves [with cleanout cover flush with floor] [in pit with pit cover flush with floor] <Insert description>.

3. Comply with requirements for [backwater valves] [cleanouts] [and] [drains] specified in Section 221423 "Storm Drainage Piping Specialties."

D. Where installing piping adjacent to equipment, allow space for service and maintenance of equipment.

3.8 IDENTIFICATION

A. Identify exposed storm drainage piping. Comply with requirements for identification specified in Section 220553 "Identification for Plumbing Piping and Equipment."

3.9 FIELD QUALITY CONTROL

Portions of testing and inspecting requirements in this article are taken from model plumbing codes. Revise if requirements vary.

A. During installation, notify authorities having jurisdiction at least 24 hours before inspection must be made. Perform tests specified below in presence of authorities having jurisdiction.

1. Roughing-in Inspection: Arrange for inspection of piping before concealing or closing-in after roughing-in.

2. Final Inspection: Arrange for final inspection by authorities having jurisdiction to observe tests specified below and to ensure compliance with requirements.

B. Reinspection: If authorities having jurisdiction find that piping will not pass test or inspection, make required corrections and arrange for reinspection.

C. Reports: Prepare inspection reports and have them signed by authorities having jurisdiction.

D. Test storm drainage piping according to procedures of authorities having jurisdiction or, in absence of published procedures, as follows:

1. Test for leaks and defects in new piping and parts of existing piping that have been altered, extended, or repaired. If testing is performed in segments, submit separate report for each test, complete with diagram of portion of piping tested.

2. Leave uncovered and unconcealed new, altered, extended, or replaced storm drainage piping until it has been tested and approved. Expose work that was covered or concealed before it was tested.

3. Test Procedure: Test storm drainage piping[, except outside leaders,] on completion of roughing-in. Close openings in piping system and fill with water to point of overflow, but not less than 10-foot head of water (30 kPa). From 15 minutes before inspection starts until completion of inspection, water level must not drop. Inspect joints for leaks.

4. Repair leaks and defects with new materials and retest piping, or portion thereof, until satisfactory results are obtained.

5. Prepare reports for tests and required corrective action.

3.10 CLEANING

A. Clean interior of piping. Remove dirt and debris as work progresses.

B. Protect drains during remainder of construction period to avoid clogging with dirt and debris and to prevent damage from traffic and construction work.

C. Place plugs in ends of uncompleted piping at end of day and when work stops.

3.11 PIPING SCHEDULE

Retain piping applications from this article. Coordinate with materials specified in Part 2. Revise to suit Project.

A. Flanges and unions may be used on aboveground pressure piping unless otherwise indicated.

Retain "any of" option in first paragraph below to allow Contractor to select piping materials from those retained.

B. Aboveground storm drainage piping [NPS 6 (DN 150) and smaller] <Insert pipe size range> shall be[ any of] the following:

Retain one or more of first five subparagraphs below. If more than one type of material and joining method is used, identify various materials on Drawings and show points of transition from one material to another.

1. Service class, cast-iron soil pipe and fittings; gaskets; and gasketed joints.

2. Hubless, cast-iron soil pipe and fittings; [CISPI,] [heavy-duty,] hubless-piping couplings; and coupled joints.

Copper tube and fittings in first subparagraph below are only available in NPS 1-1/4 to NPS 8 (DN 32 to DN 200).

3. Copper DWV tube, copper drainage fittings, and soldered joints.

4. [Solid-wall] [Cellular-core] ABS pipe, ABS socket fittings, and solvent-cemented joints.

5. [Solid-wall] [Cellular-core] PVC pipe, PVC socket fittings, and solvent-cemented joints.

6. Dissimilar Pipe-Material Couplings: [Unshielded] [Shielded], nonpressure transition couplings.

Retain "any of" option in first paragraph below to allow Contractor to select piping materials from those retained.

C. Aboveground, storm drainage piping [NPS 8 (DN 200) and larger] <Insert pipe size range> shall be[ any of] the following:

Retain one or more of first four subparagraphs below. If more than one type of material and joining method is used, identify various materials on Drawings and show points of transition from one material to another.

1. Service class, cast-iron soil pipe and fittings; gaskets; and gasketed joints.

2. Hubless, cast-iron soil pipe and fittings; [CISPI,] [heavy-duty,] hubless-piping couplings; and coupled joints.

Copper tube and fittings in first subparagraph below are only available in NPS 1-1/4 to NPS 8 (DN 32 to DN 200).

3. Copper DWV tube, copper drainage fittings, and soldered joints.

4. [Solid-wall] [Cellular-core] PVC pipe, PVC socket fittings, and solvent-cemented joints.

5. Dissimilar Pipe-Material Couplings: [Unshielded] [Shielded], nonpressure transition couplings.

Retain "any of" option in first paragraph below to allow Contractor to select piping materials from those retained.

D. Underground storm drainage piping [NPS 6 (DN 150) and smaller] <Insert pipe size range> shall be[ any of] the following:

Retain one or more of first four subparagraphs below. If more than one type of material and joining method is used, identify various materials on Drawings and show points of transition from one material to another.

1. Service class, cast-iron soil pipe and fittings; gaskets; and gasketed joints.

2. Hubless, cast-iron soil pipe and fittings; [CISPI,] [heavy-duty,] hubless-piping couplings; and coupled joints.

3. [Solid-wall] [Cellular-core] ABS pipe, ABS socket fittings, and solvent-cemented joints.

4. [Solid-wall] [Cellular-core] PVC pipe, PVC socket fittings, and solvent-cemented joints.

5. Dissimilar Pipe-Material Couplings: [Unshielded] [Shielded], nonpressure transition couplings.

Retain "any of" option in paragraph below to allow Contractor to select piping materials from those retained.

E. Underground, storm drainage piping [NPS 8 (DN 200) and larger] <Insert pipe size range> shall be[ any of] the following:

Retain one or more of first four subparagraphs below. If more than one type of material and joining method is used, identify various materials on Drawings and show points of transition from one material to another.

1. [Extra Heavy] [Service] class, cast-iron soil pipe and fittings; [gaskets; and gasketed] [calking materials; and calked] joints.

2. Hubless, cast-iron soil pipe and fittings; [CISPI,] [heavy-duty,] [cast-iron,] hubless-piping couplings; and coupled joints.

PVC piping in first subparagraph below is limited in size to NPS 12 (DN 300).

3. [Solid-wall] [Cellular-core] PVC pipe, PVC socket fittings, and solvent-cemented joints.

4. Cellular-core, sewer and drain series, PVC pipe; PVC socket fittings; and solvent-cemented joints.

5. Dissimilar Pipe-Material Couplings: [Unshielded] [Shielded], nonpressure transition couplings.

END OF SECTION 221413

	FACILITY STORM DRAINAGE PIPING
	221413 - 1



