Copyright 2011 AIA
MasterSpec Professional
09/11

Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 223100 - DOMESTIC WATER SOFTENERS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Residential water softeners.

2. Commercial water softeners.

3. Chemicals.

4. Water-testing sets.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product indicated.

1. Include construction details, material descriptions, dimensions of individual components and profiles, and finishes for water softeners.

2. Include rated capacities, operating characteristics, electrical characteristics, and furnished specialties and accessories.

3. Wiring Diagrams: For power, signal, and control wiring.

1.3 INFORMATIONAL SUBMITTALS

A. Field quality-control reports.

B. Warranty: Sample of special warranty.

1.4 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

1.5 MAINTENANCE MATERIAL SUBMITTALS

A. Furnish extra materials that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

1. Salt for Brine Tanks: Furnish in same form as and at least [four] <Insert number> times original load, but not less than [200 lb (90.7 kg)] [1000 lb (453.6 kg)] <Insert weight>.

2. Store salt on raised platform where directed by Owner. Do not store in contact with concrete floor.

1.6 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended application.

Retain first paragraph below only if ASME-code mineral tanks are specified.

B. ASME Compliance for Steel Tanks: Fabricate and label mineral tanks to comply with ASME Boiler and Pressure Vessel Code: Section VIII, Division 1, where indicated.

C. UL Compliance: Fabricate and label water softeners to comply with UL 979, "Water Treatment Appliances."

1.7 WARRANTY

A. Special Warranty: Manufacturer's standard form in which manufacturer agrees to repair or replace components of water softeners that fail in materials or workmanship within specified warranty period.

Verify available warranties and warranty periods on water softeners with manufacturers listed in Part 2 articles.

1. Residential Water Softeners, Warranty Period: From date of Substantial Completion.

a. Tanks: [Five] <Insert number> years.

b. Control Valve: [One] <Insert number> year(s).

2. Commercial Water Softeners, Warranty Period: From date of Substantial Completion.

a. Mineral Tanks: [Five] [10] <Insert number> years.

b. Brine Tanks: [10] <Insert number> years.

c. Control Valve: [One] <Insert number> year(s).

PART 2 -  PRODUCTS

2.1 RESIDENTIAL WATER SOFTENERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Alamo Water Refiners, Inc.

2. Aquion Water Treatment Products.

3. Culligan International Company.

4. CUNO Incorporated.

5. Diamond Water Conditioning; a Griesbach company.

6. Diamond Water Systems, Inc.

7. EcoWater Systems, LLC.

8. Flint & Walling, Inc.; a subsidiary of Zoeller Co.

9. Kinetico Incorporated.

10. Marlo Incorporated.

11. Springsoft International, Inc.

12. WaterSoft; a division of Amtrol, Inc.

13. <Insert manufacturer's name>.

Copy first paragraph below and re-edit for each type of residential water softener. Water softeners described in this article are appropriate for a service flow rate of between 4 and 12 gpm (0.25 to 0.76 L/s).

C. Description: Factory-assembled, fully automatic, pressure-type water softener.

1. Standard: Comply with NSF 61, "Drinking Water System Components - Health Effects."

2. Configuration: Unit with one mineral tank and one brine tank[ or cabinet-style, combination mineral and brine tank unit with equivalent characteristics].

3. Mineral Tank: Steel or FRP, with coating or liner suitable for potable-water service and [125-psig (860-kPa)] <Insert pressure> minimum pressure rating.

4. Controls: For fully automatic operation.

5. Brine Tank: Combination measuring and wet-salt storing system.

a. Tank and Cover Material: FRP or molded PE.

b. Brine Valve: Float operated and plastic fitted for automatic control of brine withdrawal and freshwater refill.

c. Size: Large enough for at least two regenerations at full salting.

6. Factory-Installed Accessories:

a. Piping, valves, tubing, and drains.

b. Sampling cock.

c. Main-operating-valve position indicator.

If Project has more than one type or configuration of water softener, delete paragraph below and schedule water softeners on Drawings.

D. Capacities and Characteristics:

1. Water Analysis:

a. Hardness: <Insert grains/gal. or ppm (mg/L)>.

b. Iron: <Insert ppm (mg/L)>.

c. Dissolved Solids: <Insert ppm (mg/L)>.

d. Concentration: <Insert pH>.

e. Inlet Water Pressure: <Insert psig (kPa)>.

f. Water Temperature: <Insert deg F (deg C)>.

2. Continuous Service Flow Rate: <Insert number> gpm at 15-psig (<Insert number> L/s at 104-kPa) pressure drop.

3. Peak Service Flow Rate: <Insert number> gpm at 25-psig (<Insert number> L/s at 173-kPa) pressure drop.

4. Mineral Quantity: <Insert cu. ft. (cu. m)>.

5. Mineral Exchange Capacity: <Insert grains/cu. ft. per lb (kg/cu. m per kg) of salt>.

6. Electrical Characteristics:

a. Volts: <Insert value>.

b. Phases: <Insert value>.

c. Hertz: <Insert value>.

d. Full-Load Amperes: <Insert value>.

e. Minimum Circuit Ampacity: <Insert value>.

f. Maximum Overcurrent Protection: <Insert amperage>.

7. Salt Capacity: <Insert lb (kg)>.

2.2 COMMERCIAL WATER SOFTENERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Aquion Water Treatment Products.

2. Culligan International Company.

3. CUNO Incorporated.

4. Diamond Water Conditioning; a Griesbach company.

5. Diamond Water Systems, Inc.

6. Ecodyne Water Treatment, Inc.

7. Hungerford & Terry, Inc.

8. Integration Separation Solutions, LLC.

9. Kinetico Incorporated.

10. Marlo Incorporated.

11. Parker Boiler.

12. Springsoft International, Inc.

13. Water King.

14. WaterSoft; a division of Amtrol, Inc.

15. <Insert manufacturer's name>.

C. Description: Factory-assembled, pressure-type water softener.

Retain first subparagraph below for potable water; delete if not required.

1. Standard: Comply with NSF 61, "Drinking Water System Components - Health Effects."

2. Configuration: [Single unit with one mineral tank] [Twin unit with two mineral tanks] and one brine tank.

3. Mounting: On skids.

If water temperature will be above 120 deg F (49 deg C), contact manufacturer of selected softener to verify that components are suitable.

4. Wetted Components: Suitable for water temperatures from [40 to at least 100 deg F (5 to at least 38 deg C)] [40 to at least 120 deg F (5 to at least 49 deg C)] [40 to at least 150 deg F (5 to at least 66 deg C)] <Insert temperature>.

5. Mineral Tanks: [Steel] [Stainless steel], electric welded; pressure-vessel quality.

First option in "Pressure Rating" Subparagraph below is usual minimum pressure rating; use higher rating if required.

a. Pressure Rating: [100 psig (690 kPa)] [125 psig (860 kPa)] [150 psig (1035 kPa)] <Insert pressure> minimum.

b. Freeboard: 50 percent minimum for backwash expansion above normal resin bed level.

Revise tank size in "Handholes" and "Manhole" subparagraphs below to suit Project. Some manufacturers offer manholes in tanks with smaller diameters.

c. Handholes: 4 inches (102 mm) round or 4 by 6 inches (102 by 152 mm) elliptical, in top head and lower sidewall of tanks [30 inches (762 mm)] <Insert tank size> and smaller in diameter.

d. Manhole: 11 by 15 inches (280 by 380 mm) in top head of tanks larger than [30 inches (762 mm)] <Insert tank size> in diameter.

e. Support Legs or Skirt: Constructed of structural steel, welded to tank[ before testing and labeling].

Retain one of two "Finish" subparagraphs below; delete both if tanks are stainless steel.

f. Finish: Hot-dip galvanized on exterior and interior of tank after fabrication unless tank is stainless steel.

g. Finish: Exterior of tank spray-painted with rust-resistant prime coat, 2- to 3-mil (0.051- to 0.076-mm) dry film thickness. Interior sandblasted and lined with epoxy-polyamide coating, 8- to 10-mil (0.203- to 0.254-mm) dry film thickness.

h. Upper Distribution System: Single, point type, fabricated from galvanized-steel pipe and fittings.

i. Lower Distribution System: Hub and radial-arm or header-lateral type; fabricated from PVC pipe and fittings with individual, fine-slotted, nonclogging PE strainers, and arranged for even flow distribution through resin bed.

Retain "Liner" Subparagraph below for potable water; delete if tanks are stainless steel.

j. Liner: PE, ABS, or other material suitable for potable water.

6. Controls: Fully automatic; factory wired and factory mounted on unit.

a. Adjustable duration of various regeneration steps.

b. Push-button start and complete manual operation.

c. Electric time clock and switch for fully automatic operation, adjustable to initiate regeneration at any hour of day and any day of week or at fixed intervals.

d. Sequence of Operation: Multiport pilot-control valve automatically pressure-actuates main operating valve through steps of regeneration and return to service.

e. Pointer on pilot-control valve shall indicate cycle of operation.

f. Includes means of manual operation of pilot-control valve if power fails.

7. Main Operating Valves: Industrial, automatic, multiport, diaphragm type with the following features:

a. Slow opening and closing, nonslam operation.

b. Diaphragm guiding on full perimeter from fully open to fully closed.

c. Isolated, dissimilar metals within valve.

d. Self-adjusting, internal, automatic brine injector that draws brine and rinses at constant rate independent of pressure.

Retain first subparagraph below only for single mineral-tank units.

e. Valve for single mineral-tank unit with internal automatic bypass of raw water during regeneration.

f. Sampling cocks for soft water.

g. Special tools are not required for service.

8. Flow Control: Automatic, to control backwash and flush rates over wide variations in operating pressure; does not require field adjustments.

Retain first subparagraph below only for single mineral-tank units.

a. Demand-Initiated Control: Single mineral tank is equipped with automatic-reset-head water meter that electrically activates cycle controller to initiate regeneration at preset total in gallons (liters). Head automatically resets to preset total in gallons (liters) for next service run.

Retain first subparagraph below only for twin mineral-tank units.

b. Demand-Initiated Control: Each mineral tank of twin mineral-tank unit is equipped with automatic-reset-head water meter that electrically activates cycle controllers to initiate regeneration at preset total in gallons (liters). Head automatically resets to preset total in gallons (liters) for next service run. Electrical lockout prevents simultaneous regeneration of both tanks.

9. Brine Tank: Combination measuring and wet-salt storing system.

a. Tank and Cover Material: Fiberglass, 3/16 inch (4.8 mm) thick; or molded PE, 3/8 inch (9.5 mm) thick.

b. Brine Valve: Float operated and plastic fitted for automatic control of brine withdrawal and freshwater refill.

c. Size: Large enough for at least four regenerations at full salting.

10. Factory-Installed Accessories:

a. Piping, valves, tubing, and drains.

b. Sampling cocks.

c. Main-operating-valve position indicators.

d. Water meters.

If Project has more than one type or configuration of water softener, delete paragraph below and schedule water softeners on Drawings.

D. Capacities and Characteristics:

1. Water Analysis:

a. Hardness: <Insert grains/gal. or ppm (mg/L)>.

b. Iron: <Insert ppm (mg/L)>.

c. Dissolved Solids: <Insert ppm (mg/L)>.

d. Concentration: <Insert pH>.

e. Inlet Water Pressure: <Insert psig (kPa)>.

f. Water Temperature: <Insert deg F (deg C)>.

2. Continuous Service Flow Rate: <Insert number> gpm at 15-psig (<Insert number> L/s at 104-kPa) pressure drop.

3. Peak Service Flow Rate: <Insert number> gpm at 25-psig (<Insert number> L/s at 173-kPa) pressure drop.

4. Water Meter Size: <Insert NPS (DN)>.

5. Manifold Pipe Size: <Insert NPS (DN)>.

6. Backwash-to-Drain Pipe Size: <Insert NPS (DN)>.

7. Water Consumption: <Insert gal./day (cu. m/day)>.

8. Water Demand: <Insert hours/day>.

Number of mineral tanks in first subparagraph below must match option retained in "Configuration" Subparagraph above.

9. Number of Mineral Tanks: [One] [Two].

10. Mineral Quantity, Each Tank: <Insert cu. ft. (cu. m)>.

11. Mineral Exchange Capacity: <Insert grains/cu. ft. per lb (kg/cu. m per kg) of salt>.

12. Electrical Characteristics:

a. Volts: <Insert value>.

b. Phases: <Insert value>.

c. Hertz: <Insert value>.

d. Full-Load Amperes: <Insert value>.

e. Minimum Circuit Ampacity: <Insert value>.

f. Maximum Overcurrent Protection: <Insert amperage>.

13. Salt Capacity: <Insert lb (kg)>.

14. Minimum Number of Regenerations per Refill: <Insert number>.

15. Floor Area Required: <Insert sq. ft. (sq. m)>.

16. Height Required: <Insert inches (mm)>.

2.3 CHEMICALS

A. Mineral: High-capacity, sulfonated-polystyrene, ion-exchange resin that is stable over entire pH range with good resistance to bead fracture from attrition or shock.

1. Exchange Capacity: [30,000 grains/cu. ft. (69 kg/cu. m)] <Insert capacity> of calcium carbonate of resin when regenerated with 15 lb (6.8 kg) of salt.

B. Salt for Brine Tanks: High-purity sodium chloride, free of dirt and foreign material. Rock and granulated forms are unacceptable.

1. Form: Processed, [food-grade salt pellets] [plain salt pellets] [crystallized solar salt collected from shallow ponds and milled into irregular particles] [plain, brine block salt].

2.4 WATER-TESTING SETS

A. Description: Manufacturer's standard water-hardness testing apparatus and chemicals with testing procedure instructions. Include metal container suitable for wall mounting.

PART 3 -  EXECUTION

3.1 WATER SOFTENER INSTALLATION

A. Equipment Mounting:

Retain first subparagraph below to require equipment to be installed on cast-in-place concrete equipment bases.

1. Install [residential] [and] [commercial] water softeners on cast-in-place concrete equipment base(s). Comply with requirements for equipment bases and foundations specified in [Section 033000 "Cast-in-Place Concrete."] [Section 033053 "Miscellaneous Cast-in-Place Concrete."]

Retain one of two subparagraphs below. Retain first for projects in seismic areas; retain second for projects not in seismic areas. Indicate vibration isolation and seismic-control device type and minimum deflection in supported equipment schedule on Drawings.

2. Comply with requirements for vibration isolation and seismic control devices specified in Section 220548 "Vibration and Seismic Controls for Plumbing Piping and Equipment"

3. Comply with requirements for vibration isolation devices specified in Section 220548.13 "Vibration Controls for Plumbing Piping and Equipment."

B. Install brine lines and fittings furnished by equipment manufacturer but not specified to be factory installed.

C. Prepare mineral-tank distribution system and underbed for minerals and place specified mineral into mineral tanks.

D. Install water-testing sets mounted on wall, unless otherwise indicated, and near water softeners.

3.2 CONNECTIONS

A. Comply with requirements for piping specified in Section 221116 "Domestic Water Piping." Drawings indicate general arrangement of piping, fittings, and specialties.

B. Where piping is installed adjacent to equipment, allow space for service and maintenance of equipment.

C. Install shutoff valves on raw-water inlet and soft-water outlet piping of each mineral tank[, and on inlet and outlet headers].

1. Metal general-duty valves are specified in Section 220523 "General-Duty Valves for Plumbing Piping."

2. Plastic valves are specified in Section 221116 "Domestic Water Piping."

3. Exception: Water softeners with factory-installed shutoff valves at locations indicated.

D. Install pressure gages on raw-water inlet and soft-water outlet piping of each mineral tank. Pressure gages are specified in Section 220519 "Meters and Gages for Plumbing Piping."

1. Exception: Water softeners with factory-installed pressure gages at locations indicated.

Retain "Exception" subparagraph below only if pressure gages are not required.

2. Exception: Household water softeners.

E. Install valved bypass in water piping around water softeners.

1. Metal general-duty valves are specified in Section 220523 "General-Duty Valves for Plumbing Piping."

2. Plastic valves are specified in Section 221116 "Domestic Water Piping."

3. Water piping is specified in Section 221116 "Domestic Water Piping."

Retain one or both "Exception" subparagraphs below only if bypass is not required.

4. Exception: Household water softeners.

5. Exception: Water softeners in hot-water service.

F. Install drains as indirect wastes to spill into open drains or over floor drains.

3.3 IDENTIFICATION

A. Identify system components. Comply with requirements for identification specified in Section 220553 "Identification for Plumbing Piping and Equipment."

3.4 FIELD QUALITY CONTROL

Retain first paragraph below to describe tests and inspections to be performed.

A. Tests and Inspections:

1. Leak Test: After installation, charge system and test for leaks. Repair leaks and retest until no leaks exist.

2. Operational Test: After electrical circuitry has been energized, start units to confirm proper unit operation.

3. Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.

B. Prepare test and inspection reports.

3.5 STARTUP SERVICE

Retain this article if a factory-authorized service representative is required.

A. [Engage a factory-authorized service representative to perform] [Perform] startup service.

1. Complete installation and startup checks according to manufacturer's written instructions.

B. Add water to brine tanks and fill with the following form of salt:

1. Residential Water Softeners: Processed, [food-grade salt pellets] [plain salt pellets] [crystallized solar salt collected from shallow ponds and milled into irregular particles] <Insert salt form>.

2. Commercial Water Softeners: Processed, [plain salt pellets] [crystallized solar salt collected from shallow ponds and milled into irregular particles] [plain, brine block salt] <Insert salt form>.

C. Sample water softener effluent after startup and at three consecutive seven-day intervals (total of four samples), and prepare certified test reports for required water performance characteristics. Comply with the following:

1. ASTM D 859, "Test Method for Silica in Water."

2. ASTM D 1067, "Test Methods for Acidity or Alkalinity of Water."

3. ASTM D 1068, "Test Methods for Iron in Water."

4. ASTM D 1126, "Test Method for Hardness in Water."

5. ASTM D 1129, "Terminology Relating to Water."

6. ASTM D 3370, "Practices for Sampling Water from Closed Conduits."

3.6 DEMONSTRATION

A. [Engage a factory-authorized service representative to train] [Train] Owner's maintenance personnel to adjust, operate, and maintain water softeners.

END OF SECTION 223100

	DOMESTIC WATER SOFTENERS
	223100 - 1



