Copyright 2010 AIA
MasterSpec Professional
03/10

Copyright 2010 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 224213.13 - COMMERCIAL WATER CLOSETS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Water closets.

2. Flushometer valves.

3. Toilet seats.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product.

B. LEED Submittals:

Retain "Product Data for Prerequisite WE 1 ( and Credit WE 3) (, Credit WE 2, and Credit WE 3)" Subparagraph below for LEED-NC, LEED-CS, and LEED for Schools for fixtures and equipment that consume water.

1. Product Data for Prerequisite WE 1[ and Credit WE 3] [, Credit WE 2, and Credit WE 3]: Documentation indicating flow and water consumption requirements.

Retain "Product Data for Prerequisite WE 1" Subparagraph below for LEED-CI for fixtures and equipment that consume water.

2. Product Data for Prerequisite WE 1: Documentation indicating flow and water consumption requirements.

Retain "Product Data for Prerequisite WE 1( and Credit WE 2)" Subparagraph below for LEED-EB for fixtures and equipment that consume water.

3. Product Data for Prerequisite WE 1[ and Credit WE 2]: Documentation indicating flow and water consumption requirements.

Retain "Shop Drawings" Paragraph below if equipment includes wiring.

C. Shop Drawings: Include diagrams for power, signal, and control wiring.

1.3 CLOSEOUT SUBMITTALS

A. Operation and Maintenance Data: For flushometer valves[ and electronic sensors] to include in operation and maintenance manuals.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

Do not use same water-closet designation as is used for another water closet in Section 224100 "Residential Plumbing Fixtures," Section 224300 "Medical Plumbing Fixtures," and Section 224600 "Security Plumbing Fixtures."

2.1 FLOOR-MOUNTED, BOTTOM-OUTLET WATER CLOSETS

Copy "Water Closets" Paragraph below and re-edit for each type of floor-mounted, bottom-outlet, top-spud water closet required.

Insert number to complete drawing designation. Use these designations on Drawings to identify each water closet.

A. Water Closets <Insert drawing designation>: Floor mounted, bottom outlet, top spud.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. American Standard America.

b. Briggs Plumbing Products, Inc.

c. Capizzi.

d. Crane Plumbing, L.L.C.

e. Ferguson Enterprises, Inc.; ProFlo Brand.

f. Gerber Plumbing Fixtures LLC.

g. Kohler Co.

h. Mansfield Plumbing Products LLC.

i. Peerless Pottery Sales, Inc.

j. St. Thomas Creations.

k. TOTO USA, INC.

l. Zurn Industries, LLC; Commercial Brass and Fixtures.

m. <Insert manufacturer's name>.

3. Bowl:

a. Standards: ASME A112.19.2/CSA B45.1 and ASME A112.19.5.

b. Material: Vitreous china.

c. Type: Siphon jet.

d. Style: Flushometer valve.

e. Height: [Standard] [Child] [Handicapped/elderly, complying with ICC/ANSI A117.1].

f. Rim Contour: Elongated.

g. Water Consumption: [1.28 gal. (4.8 L)] [1.6 gal. (6 L)] per flush.

h. Spud Size and Location: NPS 1-1/2 (DN 40); top.

i. Color: [White] <Insert color>.

4. Bowl-to-Drain Connecting Fitting: [ASTM A 1045 or ]ASME A112.4.3.

Coordinate "Flushometer Valve" Subparagraph below with "Flushometer Valves" Article.

5. Flushometer Valve: <Insert flushometer-valve designation>.

Coordinate "Toilet Seat" Subparagraph with "Toilet Seats" Article.

6. Toilet Seat: <Insert toilet-seat designation>.

2.2 WALL-MOUNTED WATER CLOSETS

Copy "Water Closets" Paragraph below and re-edit for each type of wall-mounted, top-spud water closet required.

Insert number to complete drawing designation. Use these designations on Drawings to identify each water closet.

A. Water Closets <Insert drawing designation>: Wall mounted, top spud[, accessible].

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. American Standard America.

b. Briggs Plumbing Products, Inc.

c. Capizzi.

d. Crane Plumbing, L.L.C.

e. Ferguson Enterprises, Inc.; ProFlo Brand.

f. Gerber Plumbing Fixtures LLC.

g. Kohler Co.

h. Mansfield Plumbing Products LLC.

i. Peerless Pottery Sales, Inc.

j. TOTO USA, INC.

k. Zurn Industries, LLC; Commercial Brass and Fixtures.

l. <Insert manufacturer's name>.

3. Bowl:

a. Standards: ASME A112.19.2/CSA B45.1 and ASME A112.19.5.

b. Material: Vitreous china.

c. Type: Siphon jet.

d. Style: Flushometer valve.

e. Height: Standard.

f. Rim Contour: Elongated.

g. Water Consumption: [1.28 gal. (4.8 L)] [1.6 gal. (6 L)] per flush.

h. Spud Size and Location: NPS 1-1/2 (DN 40); top.

Coordinate "Flushometer Valve" Subparagraph below with "Flushometer Valves" Article.

4. Flushometer Valve: <Insert flushometer-valve designation>.

Coordinate "Toilet Seat" Subparagraph with "Toilet Seats" Article.

5. Toilet Seat: <Insert toilet-seat designation>.

6. Support:

a. Standard: ASME A112.6.1M.

b. Description: Waste-fitting assembly, as required to match drainage piping material and arrangement with faceplates, couplings gaskets, and feet; bolts and hardware matching fixture.[ Include additional extension coupling, faceplate, and feet for installation in wide pipe space.]

c. Water-Closet Mounting Height: [Standard] [Child] [Handicapped/elderly according to ICC/ANSI A117.1].

2.3 FLUSHOMETER VALVES

Caution: Flushometer-valve consumption must match the water consumption of the water-closet bowl.

A. Lever-Handle, Diaphragm Flushometer Valves <Insert designation>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Coyne & Delany Co.

b. Gerber Plumbing Fixtures LLC.

c. Sloan Valve Company.

d. Zurn Industries, LLC; Commercial Brass and Fixtures.

e. <Insert manufacturer's name>.

3. Standard: ASSE 1037.

4. Minimum Pressure Rating: 125 psig (860 kPa).

5. Features: Include integral check stop and backflow-prevention device.

6. Material: Brass body with corrosion-resistant components.

7. Exposed Flushometer-Valve Finish: Chrome plated.

Retain "Panel Finish" Subparagraph below for concealed flushometer-valve components.

8. Panel Finish: Chrome plated or stainless steel.

9. Style: [Exposed] [Concealed].

Retain third option in "Consumption" Subparagraph below only for blowout water closets.

10. Consumption: [1.28 gal. (4.8 L)] [1.6 gal. (6 L)] [3.5 gal. (13.2 L)] <Insert value> per flush.

11. Minimum Inlet: NPS 1 (DN 25).

12. Minimum Outlet: NPS 1-1/4 (DN 32).

B. Lever-Handle, Piston Flushometer Valves <Insert designation>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Coyne & Delany Co.

b. Sloan Valve Company.

c. TOTO USA, INC.

d. <Insert manufacturer's name>.

3. Standard: ASSE 1037.

4. Minimum Pressure Rating: 125 psig (860 kPa).

5. Features: Include integral check stop and backflow-prevention device.

6. Material: Brass body with corrosion-resistant components.

7. Exposed Flushometer-Valve Finish: Chrome plated.

Retain "Panel Finish" Subparagraph below for concealed flushometer-valve components.

8. Panel Finish: Chrome plated or stainless steel.

9. Style: [Exposed] [Concealed].

Retain third option in "Consumption" Subparagraph below only for blowout water closets.

10. Consumption: [1.28 gal. (4.8 L)] [1.6 gal. (6 L)] [3.5 gal. (13.2 L)] <Insert value> per flush.

11. Minimum Inlet: NPS 1 (DN 25).

12. Minimum Outlet: NPS 1-1/4 (DN 32).

2.4 TOILET SEATS

Copy "Toilet Seats" Paragraph below and re-edit for each type of toilet seat required.

Insert number to complete drawing designation. Use these designations on Drawings to identify each water closet.

A. Toilet Seats <Insert drawing designation>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. American Standard America.

b. Bemis Manufacturing Company.

c. Centoco Manufacturing Corporation.

d. Church Seats.

e. Jones Stephens Corp.; Comfort Seat Brand.

f. Kohler Co.

g. Olsonite Seat Co.

h. Sanderson Plumbing Products, Inc.

i. Sperzel of Lexington.

j. TOTO USA, INC.

k. Zurn Industries, LLC; Commercial Brass and Fixtures.

l. <Insert manufacturer's name>.

3. Standard: IAPMO/ANSI Z124.5.

4. Material: Plastic.

5. Type: [Commercial (Standard)] [Commercial (Heavy duty)].

6. Shape: [Elongated rim, open front] [Elongated rim, closed front] <Insert shape>.

7. Hinge: [Check] [Self-sustaining] [Self-sustaining, check] [Self-raising].

8. Hinge Material: Noncorroding metal.

9. Seat Cover: [Required] [Not required].

10. Color: [White] [Black] <Insert color>.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Water-Closet Installation:

1. Install level and plumb according to roughing-in drawings.

2. Install floor-mounted water closets on bowl-to-drain connecting fitting attachments to piping or building substrate.

Indicate on Drawings those water closets that are required to be accessible.

3. Install accessible, wall-mounted water closets at mounting height for handicapped/elderly, according to ICC/ANSI A117.1.

B. Support Installation:

1. Install supports, affixed to building substrate, for floor-mounted, back-outlet water closets.

2. Use carrier supports with waste-fitting assembly and seal.

3. Install wall-mounted, back-outlet water-closet supports with waste-fitting assembly and waste-fitting seals; and affix to building substrate.

C. Flushometer-Valve Installation:

1. Install flushometer-valve, water-supply fitting on each supply to each water closet.

2. Attach supply piping to supports or substrate within pipe spaces behind fixtures.

3. Install lever-handle flushometer valves for accessible water closets with handle mounted on open side of water closet.

4. Install actuators in locations that are easy for people with disabilities to reach.

D. Install toilet seats on water closets.

E. Wall Flange and Escutcheon Installation:

1. Install wall flanges or escutcheons at piping wall penetrations in exposed, finished locations and within cabinets and millwork.

2. Install deep-pattern escutcheons if required to conceal protruding fittings.

3. Comply with escutcheon requirements specified in Section 220518 "Escutcheons for Plumbing Piping."

Retain "Joint Sealing" Paragraph below if sealants are not specified in Section 079200 "Joint Sealants."

F. Joint Sealing:

1. Seal joints between water closets and walls and floors using sanitary-type, one-part, mildew-resistant silicone sealant.

2. Match sealant color to water-closet color.

3. Comply with sealant requirements specified in Section 079200 "Joint Sealants."

3.2 CONNECTIONS

Coordinate piping installations and specialty arrangements with Drawings and with requirements specified in piping systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Connect water closets with water supplies and soil, waste, and vent piping. Use size fittings required to match water closets.

B. Comply with water piping requirements specified in Section 221116 "Domestic Water Piping."

C. Comply with soil and waste piping requirements specified in Section 221316 "Sanitary Waste and Vent Piping."

D. Where installing piping adjacent to water closets, allow space for service and maintenance.

3.3 ADJUSTING

A. Operate and adjust water closets and controls. Replace damaged and malfunctioning water closets, fittings, and controls.

B. Adjust water pressure at flushometer valves to produce proper flow.

3.4 CLEANING AND PROTECTION

A. Clean water closets and fittings with manufacturers' recommended cleaning methods and materials.

B. Install protective covering for installed water closets and fittings.

C. Do not allow use of water closets for temporary facilities unless approved in writing by Owner.

END OF SECTION 224213.13

	COMMERCIAL WATER CLOSETS
	224213.13 - 1



