Copyright 2010 AIA
MasterSpec Professional
03/10

Copyright 2010 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 224213.16 - COMMERCIAL URINALS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Urinals.

2. Flushometer valves.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product.

B. LEED Submittals:

Retain "Product Data for Prerequisite WE 1 ( and Credit WE 3) (, Credit WE 2, and Credit WE 3)" Subparagraph below for LEED-NC, LEED-CS, and LEED for Schools for fixtures and equipment that consume water.

1. Product Data for Prerequisite WE 1[ and Credit WE 3] [, Credit WE 2, and Credit WE 3]: Documentation indicating flow and water consumption requirements.

Retain "Product Data for Prerequisite WE 1" Subparagraph below for LEED-CI for fixtures and equipment that consume water.

2. Product Data for Prerequisite WE 1: Documentation indicating flow and water consumption requirements.

Retain "Product Data for Prerequisite WE 1( and Credit WE 2)" Subparagraph below for LEED-EB for fixtures and equipment that consume water.

3. Product Data for Prerequisite WE 1[ and Credit WE 2]: Documentation indicating flow and water consumption requirements.

Retain "Shop Drawings" Paragraph below if equipment includes wiring.

C. Shop Drawings: Include diagrams for power, signal, and control wiring.

1.3 CLOSEOUT SUBMITTALS

A. Operation and Maintenance Data: For flushometer valves[ and electronic sensors] to include in operation and maintenance manuals.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

Do not use same urinal designation as is used for another urinal in Section 224600 "Security Plumbing Fixtures."

2.1 WALL-HUNG URINALS

Copy "Urinals" Paragraph below and re-edit for each type of wall-hung, back-outlet, siphon-jet urinal required.

Insert number to complete drawing designation. Use these designations on Drawings to identify each urinal.

A. Urinals <Insert drawing designation>: Wall hung, back outlet, siphon jet[, accessible].

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. American Standard America.

b. Briggs Plumbing Products, Inc.

c. Ferguson Enterprises, Inc.; ProFlo Brand.

d. Gerber Plumbing Fixtures LLC.

e. Kohler Co.

f. Mansfield Plumbing Products LLC.

g. Peerless Pottery Sales, Inc.

h. <Insert manufacturer's name>.

3. Fixture:

a. Standards: ASME A112.19.2/CSA B45.1 and ASME A112.19.5.

b. Material: Vitreous china.

Option in "Type" Subparagraph below may not be available from some manufacturers. Extended shields vary in shape and dimensions. Verify availability and suitability if required.

c. Type: Siphon jet[ with extended shields].

d. Strainer or Trapway: [Manufacturer's standard strainer] <Insert strainer> with integral trap.

e. Water Consumption: [Water saving] [Low].

First option in "Spud Size and Location" Subparagraph below is available from some manufacturers. Back spud is used with a remote hard-wired, solenoid-actuator, electronic-sensor flushometer valve. Verify availability if required.

f. Spud Size and Location: NPS 3/4 (DN 20); [back] [top].

g. Outlet Size and Location: NPS 2 (DN 50); back.

h. Color: [White] <Insert color>.

4. Flushometer Valve: <Insert urinal flushometer-valve designation from "Urinal Flushometer Valves" Article>.

5. Waste Fitting:

a. Standard: ASME A112.18.2/CSA B125.2 for coupling.

b. Size: NPS 2 (DN 50).

6. Support: ASME A112.6.1M, Type I, urinal carrier with fixture support plates and coupling with seal and fixture bolts and hardware matching fixture.[ Include rectangular, steel uprights.]

Copy "Urinals" Paragraph below and re-edit for each type of wall-hung, back-outlet, washout urinal required.

Insert number to complete drawing designation. Use these designations on Drawings to identify each urinal.

B. Urinals <Insert drawing designation>: Wall hung, back outlet, washout[, accessible].

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. American Standard America.

b. Briggs Plumbing Products, Inc.

c. Capizzi.

d. Crane Plumbing, L.L.C.

e. Duravit USA, Inc.

f. Ferguson Enterprises, Inc.; ProFlo Brand.

g. Gerber Plumbing Fixtures LLC.

h. Kohler Co.

i. Mansfield Plumbing Products LLC.

j. Peerless Pottery Sales, Inc.

k. TOTO USA, INC.

l. Zurn Industries, LLC; Commercial Brass and Fixtures.

m. <Insert manufacturer's name>.

3. Fixture:

a. Standards: ASME A112.19.2/CSA B45.1 and ASME A112.19.5.

b. Material: Vitreous china.

c. Type: Washout with extended shields.

d. Strainer or Trapway: [Manufacturer's standard strainer] <Insert strainer> with integral trap.

e. Water Consumption: [Water saving] [Low].

First option in "Spud Size and Location" Subparagraph below is available from some manufacturers. Back spud is used with a remote hard-wired, solenoid-actuator, electronic-sensor flushometer valve. Verify availability if required.

f. Spud Size and Location: NPS 3/4 (DN 20), [back] [top].

g. Outlet Size and Location: NPS 2 (DN 50), back.

h. Color: [White] <Insert color>.

4. Flushometer Valve: <Insert urinal flushometer-valve designation from "Urinal Flushometer Valves" Article>.

5. Waste Fitting:

a. Standard: ASME A112.18.2/CSA B125.2 for coupling.

b. Size: NPS 2 (DN 50).

6. Support: ASME A112.6.1M, Type I, urinal carrier with fixture support plates and coupling with seal and fixture bolts and hardware matching fixture.[ Include rectangular, steel uprights.]

2.2 WATERLESS URINALS

Copy "Urinals" Paragraph below and re-edit for each type of wall-hung, back-outlet, waterless, vitreous-china urinal required.

Insert number to complete drawing designation. Use these designations on Drawings to identify each urinal.

A. Urinals <Insert drawing designation>: Wall hung, back outlet, waterless, vitreous china, designed for liquid-trap-seal operation.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Duravit USA, Inc.

b. Falcon Waterfree Technologies.

c. Kohler Co.

d. Sloan Valve Company.

e. Waterless Co.

f. Zero Flush.

g. Zurn Industries, LLC; Commercial Brass and Fixtures.

h. <Insert manufacturer's name>.

3. Fixture:

a. Standard: ASME A112.19.2/CSA B45.1, except without water supply.

b. Trap-Seal Method: Proprietary cartridge with liquid seal.

c. Outlet Size and Location: [NPS 2 (DN 50)] <Insert size> flange; back.

d. Trap-Sealing Liquid: Proprietary.

e. Color: [White] <Insert color>.

4. Waste Fitting:

a. Standard: ASME A112.18.2/CSA B125.2 for transition coupling, trap, and waste pipe.

b. Size: [NPS 2 (DN 50)] <Insert size>.

5. Support: ASME A112.6.1M, Type I, urinal carrier with fixture support plates and coupling with seal and fixture bolts and hardware matching fixture.[ Include rectangular, steel uprights.]

2.3 URINAL FLUSHOMETER VALVES

A. Lever-Handle, Diaphragm Flushometer Valves <Insert designation>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Coyne & Delany Co.

b. Gerber Plumbing Fixtures LLC.

c. Sloan Valve Company.

d. Zurn Industries, LLC; Commercial Brass and Fixtures.

e. <Insert manufacturer's name>.

3. Standard: ASSE 1037.

4. Minimum Pressure Rating: 125 psig (860 kPa).

5. Features: Include integral check stop and backflow-prevention device.

6. Material: Brass body with corrosion-resistant components.

7. Exposed Flushometer-Valve Finish: Chrome plated.

8. Style: Exposed.

9. Consumption: [0.5 gal. (1.9 L)] [1.0 gal. (3.8 L)] <Insert value> per flush.

10. Minimum Inlet: [NPS 3/4 (DN 20)] [NPS 1 (DN 25)].

11. Minimum Outlet: [NPS 3/4 (DN 20)] [NPS 1-1/4 (DN 32)].

B. Solenoid-Actuator, Diaphragm Flushometer Valves <Insert designation>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Coyne & Delany Co.

b. Gerber Plumbing Fixtures LLC.

c. Sloan Valve Company.

d. Zurn Industries, LLC; Commercial Brass and Fixtures.

e. <Insert manufacturer's name>.

3. Standard: ASSE 1037.

4. Minimum Pressure Rating: 125 psig (860 kPa).

5. Features: Include integral check stop and backflow-prevention device.

6. Material: Brass body with corrosion-resistant components.

7. Exposed Flushometer-Valve Finish: Chrome plated.

8. Style: Exposed.

9. Actuator: Solenoid complying with UL 1951; listed and labeled as defined in NFPA 70, by a qualified testing agency; and marked for intended location and application.

10. Trip Mechanism: [Battery-powered] [Hard-wired], electronic sensor complying with UL 1951; listed and labeled as defined in NFPA 70, by a qualified testing agency; and marked for intended location and application.

11. Consumption: [0.5 gal. (1.9 L)] [1.0 gal. (3.8 L)] <Insert value> per flush.

12. Minimum Inlet: [NPS 3/4 (DN 20)] [NPS 1 (DN 25)].

13. Minimum Outlet: [NPS 3/4 (DN 20)] [NPS 1-1/4 (DN 32)].

C. Lever-Handle, Piston Flushometer Valves <Insert designation>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Coyne & Delany Co.

b. Sloan Valve Company.

c. TOTO USA, INC.

d. <Insert manufacturer's name>.

3. Standard: ASSE 1037.

4. Minimum Pressure Rating: 125 psig (860 kPa).

5. Features: Include integral check stop and backflow-prevention device.

6. Material: Brass body with corrosion-resistant components.

7. Exposed Flushometer-Valve Finish: Chrome plated.

8. Style: Exposed.

9. Consumption: [0.5 gal. (1.9 L)] [1.0 gal. (3.8 L)] <Insert value> per flush.

10. Minimum Inlet: [NPS 3/4 (DN 20)] [NPS 1 (DN 25)].

11. Minimum Outlet: [NPS 3/4 (DN 20)] [NPS 1-1/4 (DN 32)].

D. Battery-Powered, Solenoid-Actuator, Piston Flushometer Valves <Insert designation>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

List of manufacturers below is for battery-powered, solenoid-actuator, electronic-sensor, piston flushometer valves.

a. Coyne & Delany Co.

b. Gerber Plumbing Fixtures LLC.

c. Hydrotek International, Inc.

d. Kohler Co.

e. Moen Incorporated.

f. Sloan Valve Company.

g. TOTO USA, INC.

h. Zurn Industries, LLC; Commercial Brass and Fixtures.

i. <Insert manufacturer's name>.

3. Standard: ASSE 1037.

4. Minimum Pressure Rating: 125 psig (860 kPa).

5. Features: Include integral check stop and backflow-prevention device.

6. Material: Brass body with corrosion-resistant components.

7. Exposed Flushometer-Valve Finish: Chrome plated.

8. Style: Exposed.

9. Actuator: Solenoid complying with UL 1951; listed and labeled as defined in NFPA 70, by a qualified testing agency; and marked for intended location and application.

10. Trip Mechanism: Battery-powered electronic sensor complying with UL 1951; listed and labeled as defined in NFPA 70, by a qualified testing agency; and marked for intended location and application.

11. Consumption: [0.5 gal. (1.9 L)] [1.0 gal. (3.8 L)] <Insert value> per flush.

12. Minimum Inlet: [NPS 3/4 (DN 20)] [NPS 1 (DN 25)].

13. Minimum Outlet: [NPS 3/4 (DN 20)] [NPS 1-1/4 (DN 32)].

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine roughing-in of water supply and sanitary drainage and vent piping systems to verify actual locations of piping connections before urinal installation.

B. Examine walls and floors for suitable conditions where urinals will be installed.

C. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 INSTALLATION

A. Urinal Installation:

1. Install urinals level and plumb according to roughing-in drawings.

2. Install wall-hung, back-outlet urinals onto waste fitting seals and attached to supports.

3. Install wall-hung, bottom-outlet urinals with tubular waste piping attached to supports.

Indicate on Drawings those urinals that are required to be accessible.

4. Install accessible, wall-mounted urinals at mounting height for the handicapped/elderly, according to ICC/ANSI A117.1.

5. Install trap-seal liquid in waterless urinals.

B. Support Installation:

1. Install supports, affixed to building substrate, for wall-hung urinals.

2. Use off-floor carriers with waste fitting and seal for back-outlet urinals.

3. Use carriers without waste fitting for urinals with tubular waste piping.

4. Use chair-type carrier supports with rectangular steel uprights for accessible urinals.

C. Flushometer-Valve Installation:

1. Install flushometer-valve water-supply fitting on each supply to each urinal.

2. Attach supply piping to supports or substrate within pipe spaces behind fixtures.

3. Install lever-handle flushometer valves for accessible urinals with handle mounted on open side of compartment.

4. Install fresh batteries in battery-powered, electronic-sensor mechanisms.

D. Wall Flange and Escutcheon Installation:

1. Install wall flanges or escutcheons at piping wall penetrations in exposed, finished locations.

2. Install deep-pattern escutcheons if required to conceal protruding fittings.

3. Comply with escutcheon requirements specified in Section 220518 "Escutcheons for Plumbing Piping."

Retain "Joint Sealing" Paragraph below if sealants are not specified in Section 079200 "Joint Sealants."

E. Joint Sealing:

1. Seal joints between urinals and walls and floors using sanitary-type, one-part, mildew-resistant silicone sealant.

2. Match sealant color to urinal color.

3. Comply with sealant requirements specified in Section 079200 "Joint Sealants."

3.3 CONNECTIONS

Coordinate piping installations and specialty arrangements with Drawings and with requirements specified in piping systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Connect urinals with water supplies and soil, waste, and vent piping. Use size fittings required to match urinals.

B. Comply with water piping requirements specified in Section 221116 "Domestic Water Piping."

C. Comply with soil and waste piping requirements specified in Section 221316 "Sanitary Waste and Vent Piping."

D. Where installing piping adjacent to urinals, allow space for service and maintenance.

3.4 ADJUSTING

A. Operate and adjust urinals and controls. Replace damaged and malfunctioning urinals, fittings, and controls.

B. Adjust water pressure at flushometer valves to produce proper flow.

C. Install fresh batteries in battery-powered, electronic-sensor mechanisms.

3.5 CLEANING AND PROTECTION

A. Clean urinals and fittings with manufacturers' recommended cleaning methods and materials.

B. Install protective covering for installed urinals and fittings.

C. Do not allow use of urinals for temporary facilities unless approved in writing by Owner.

END OF SECTION 224213.16

	COMMERCIAL URINALS
	224213.16 - 1



