Copyright 2010 AIA
MasterSpec Professional
03/10

Copyright 2010 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 224233 - WASH FOUNTAINS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Circular wash fountains.

2. Semicircular wash fountains.

3. Linear wash fountains.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product.

Retain "LEED Submittals" Paragraph below if applying for LEED certification. See the "LEED Rating System" Article in the Evaluations.

B. LEED Submittals:

Retain "Product Data for Prerequisite WE 1( and Credit WE 3) (, Credit WE 2, and Credit WE 3)" Subparagraph below for LEED-NC, LEED-CS, and LEED for Schools for fixtures and equipment that consume water.

1. Product Data for Prerequisite WE 1[ and Credit WE 3] [, Credit WE 2, and Credit WE 3]: Documentation indicating flow and water consumption requirements.

Retain "Product Data for Prerequisite WE 1( and Credit WE 1)" Subparagraph below for LEED-CI for fixtures and equipment that consume water.

2. Product Data for Prerequisite WE 1[ and Credit WE 1]: Documentation indicating flow and water consumption requirements.

Retain "Product Data for Prerequisite WE 1( and Credit WE 2)" Subparagraph below for LEED-EB for fixtures and equipment that consume water.

3. Product Data for Prerequisite WE 1[ and Credit WE 2]: Documentation indicating flow and water consumption requirements.

Retain "Shop Drawings" Paragraph below if fixtures or equipment includes wiring.

C. Shop Drawings: For each type of wash fountain.

1. Include plans, elevations, sections, and [mounting] [attachment] details.

2. Include details of equipment assemblies. Indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

3. Include diagrams for power, signal, and control wiring.

1.3 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

Do not use the same plumbing fixture designation as is used for a plumbing fixture in another plumbing Section.

2.1 SOLID-SURFACE, CIRCULAR WASH FOUNTAINS

Caution: These fixtures require a trap with waste and vent connections for installation in the base and vertical vent piping through top of unit, or they may be installed with trap and vent under the floor below the fixture.

Copy "Wash Fountains" Paragraph below and re-edit for each type of circular wash fountain required.

Insert letter and number combination to complete drawing designation. Use these designations on Drawings to identify each solid-surface, circular wash fountain.

A. Wash Fountains <Insert drawing designation>: Solid-surface, circular receptor.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Bradley Corporation.

b. Intersan Manufacturing Company.

c. Willoughby Industries.

d. <Insert manufacturer's name>.

3. Standard: IAPMO IGC 156.

4. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

5. Receptor:

a. Standard: ICPA SS-1 for solid-surface receptor.

b. Nominal Diameter: [36 to 39 inches (914 to 990 mm)] [39 inches (990 mm)] [42 inches (1067 mm)] [54 inches (1370 mm)].

c. Height to Rim: 34 inches (864 mm) above floor.

d. Color or Finish: [Not applicable] <Insert if required>.

e. Drain: Grid with [NPS 2 (DN 50)] <Insert size> tailpiece.

6. Spray Head:

a. Material: Stainless steel.

b. Number of User Stations: [Five] [Six] [Eight].

c. Spray Nozzles: Chrome-plated brass or stainless steel complying with NSF 61 and ASME A112.18.1/CSA B125.1.

Verify option retained in "Control" Subparagraph below is available from listed manufacturers and for type of wash fountain required.

d. Control: [Collective, foot-rail] [Individual foot-pedal] [Individual push-button] [Individual, hardwired sensor] [Individual, battery-powered sensor] actuation with [pressure-balancing] [thermostatic] mixing valve complying with ASSE 1016 and having check stops; comply with NSF 61.

Retain "Sensor" Subparagraph below if retaining "Individual, hardwired sensor" or "Individual, battery-powered sensor" option in "Control" Subparagraph above.

e. Sensor: ASME A112.18.1/CSA B125.1 and UL 1951.

Verify "Hardwired, sensor actuated" or "Battery powered, sensor actuated" option, if retained in "Liquid-Soap Dispensers" Subparagraph below, is available from listed manufacturers and for type of wash fountain required. Typically, sensor-operated soap dispensers are battery powered; however, they require hardwiring if the nozzles are hardwired.

7. Liquid-Soap Dispensers: [Manual] [Hardwired, sensor actuated] [Battery powered, sensor actuated] [Not required], for each user station.

Retain "Sensor" Subparagraph below if retaining "Hardwired, sensor actuated" or "Battery powered, sensor actuated" option in "Liquid-Soap Dispensers" Subparagraph above.

a. Sensor: ASME A112.18.1/CSA B125.1 and UL 1951.

8. Pedestal: [Manufacturer's standard] [Painted or coated steel] [Stainless steel] with access panel.

9. Supply Fittings:

a. Piping: [NPS 3/4 (DN 20)] [NPS 1 (DN 25)] copper tubing.

b. Valves: Shutoff valve on each supply.

c. Supply Piping: From [bottom] [top].

10. Waste Fittings:

a. Standard: ASME A112.18.2/CSA B125.2.

b. Trap and Drain Piping: [NPS 2 (DN 50)].

c. Vent Piping: [Not required] [NPS 1-1/2 (DN 40) to ceiling].

Retain "Shroud" Subparagraph below if required to conceal vertical supply and vent piping.

11. Shroud: [Not required] [Stainless steel of size to cover supply and vent piping].

12. Mounting: Floor bracket.

2.2 STAINLESS-STEEL, CIRCULAR WASH FOUNTAINS

Caution: These fixtures require a trap with waste and vent connections for installation in the base and vertical vent piping through top of unit, or they may be installed with trap and vent under the floor below the fixture.

Copy "Wash Fountains" Paragraph below and re-edit for each type of circular wash fountain required.

Insert letter and number combination to complete drawing designation. Use these designations on Drawings to identify each stainless-steel, circular wash fountain.

A. Wash Fountains <Insert drawing designation>: Stainless-steel, circular receptor.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Acorn Engineering Company.

b. Bradley Corporation.

c. Intersan Manufacturing Company.

d. Willoughby Industries.

e. <Insert manufacturer's name>.

3. Standard: IAPMO IGC 156.

4. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

5. Receptor:

a. Standard: IAPMO IGC 156 for stainless-steel receptor.

b. Nominal Diameter: [36 to 39 inches (914 to 990 mm)] [39 inches (990 mm)] [42 inches (1067 mm)] [54 inches (1372 mm)].

c. Height to Rim: 34 inches (864 mm) above floor.

d. Color or Finish: [Not applicable] <Insert if required>.

e. Drain: Grid with [NPS 2 (DN 50)] <Insert size> tailpiece.

6. Spray Head:

a. Material: Stainless steel.

b. Number of User Stations: [Five] [Six] [Eight].

c. Spray Nozzles: Chrome-plated brass or stainless steel complying with NSF 61 and ASME A112.18.1/CSA B125.1.

Verify option retained in "Control" Subparagraph below is available from listed manufacturers and for type of wash fountain required.

d. Control: [Collective, foot-rail] [Individual foot-pedal] [Individual push-button] [Individual, hardwired sensor] [Individual, battery-powered sensor] actuation with [pressure-balancing] [thermostatic] mixing valve complying with ASSE 1016 and having check stops; comply with NSF 61.

Retain "Sensor" Subparagraph below if retaining "Individual, hardwired sensor" or "Individual, battery-powered sensor" option in "Control" Subparagraph above.

e. Sensor: ASME A112.18.1/CSA B125.1 and UL 1951.

Verify "Hardwired, sensor actuated" or "Battery powered, sensor actuated" option, if retained in "Liquid-Soap Dispensers" Subparagraph below, is available from listed manufacturers and for type of wash fountain required. Typically, sensor-operated soap dispensers are battery powered; however, they require hardwiring if the nozzles are hardwired.

7. Liquid-Soap Dispensers: [Manual] [Hardwired, sensor actuated] [Battery powered, sensor actuated] [Not required], for each user station.

Retain "Sensor" Subparagraph below if retaining "Hardwired, sensor actuated" or "Battery powered, sensor actuated" option in "Liquid-Soap Dispensers" Subparagraph above.

a. Sensor: ASME A112.18.1/CSA B125.1 and UL 1951.

8. Pedestal: Stainless steel with access panel.

9. Supply Fittings:

a. Piping: [NPS 3/4 (DN 20)] [NPS 1 (DN 25)] copper tubing.

b. Valves: Shutoff valve on each supply.

c. Supply Piping: From [bottom] [top].

10. Waste Fittings:

a. Standard: ASME A112.18.2/CSA B125.2.

b. Trap and Drain Piping: [NPS 2 (DN 50)].

c. Vent Piping: [Not required] [NPS 1-1/2 (DN 40) to ceiling].

Retain "Shroud" Subparagraph below if required to conceal vertical supply and vent piping.

11. Shroud: [Not required] [Stainless steel of size to cover supply and vent piping].

12. Mounting: Floor bracket.

2.3 SOLID-SURFACE, SEMICIRCULAR WASH FOUNTAINS

Copy "Wash Fountains" Paragraph below and re-edit for each type of semicircular wash fountain required.

Insert letter and number combination to complete drawing designation. Use these designations on Drawings to identify each solid-surface, semicircular wash fountain.

A. Wash Fountains <Insert drawing designation>: [Off] [On]-floor, solid-surface, semicircular receptor.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Acorn Engineering Company.

b. Bradley Corporation.

c. Intersan Manufacturing Company.

d. Willoughby Industries.

e. <Insert manufacturer's name>.

3. Standard: IAPMO IGC 156.

4. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

5. Receptor:

a. Standard: ICPA SS-1 for solid-surface receptor.

b. Nominal Diameter: [36 to 39 inches (914 to 990 mm)] [39 inches (990 mm)] [42 inches (1067 mm)] [54 inches (1372 mm)].

c. Height to Rim: 34 inches (864 mm) above floor.

d. Color or Finish: [Not applicable] <Insert if required>.

e. Drain: Grid with [NPS 1-1/2 (DN 40)] [NPS 2 (DN 50)] tailpiece.

6. Spray Head:

a. Material: Stainless steel or integral part of receptor back.

b. Number of User Stations: [Two] [Three] [Four].

c. Spray Nozzles: Chrome-plated brass or stainless steel complying with NSF 61 and ASME A112.18.1/CSA B125.1.

Verify option retained in "Control" Subparagraph below is available from listed manufacturers and for type of wash fountain required.

d. Control: [Collective, foot-rail] [Individual foot-pedal] [Individual push-button] [Individual, hardwired sensor] [Individual, battery-powered sensor] actuation with [pressure-balancing] [thermostatic] mixing valve complying with ASSE 1016 and having check stops; comply with NSF 61.

Retain "Sensor" Subparagraph below if retaining "Individual, hardwired sensor" or "Individual, battery-powered sensor" option in "Control" Subparagraph above.

e. Sensor: ASME A112.18.1/CSA B125.1 and UL 1951.

Verify "Hardwired, sensor actuated" or "Battery powered, sensor actuated" option, if retained in "Liquid-Soap Dispensers" Subparagraph below, is available from listed manufacturers and for type of wash fountain required. Typically, sensor-operated soap dispensers are battery powered; however, they require hardwiring if the nozzles are hardwired.

7. Liquid-Soap Dispensers: [Manual] [Hardwired, sensor actuated] [Battery powered, sensor actuated] [Not required], for each user station.

Retain "Sensor" Subparagraph below if retaining "Hardwired, Sensor actuated" or "Battery powered, sensor actuated" option in "Liquid-Soap Dispensers" Subparagraph above.

a. Sensor: ASME A112.18.1/CSA B125.1 and UL 1951.

8. Supply Fittings:

a. Piping: [NPS 1/2 (DN 15)] [NPS 3/4 (DN 20)] copper tubing.

b. Valves: Shutoff valve on each supply.

c. Supply Piping: From [bottom] [top] [wall].

9. Waste Fittings:

a. Standard: ASME A112.18.2/CSA B125.2.

b. Trap and Drain Piping: [NPS 1-1/2 (DN 40)] [NPS 2 (DN 50)].

c. Vent Piping: [Not required] [NPS 1-1/2 (DN 40) to ceiling].

Retain "Shroud" Subparagraph below if required to conceal vertical supply and vent piping.

10. Shroud: [Not required] [Stainless steel of size to cover supply and vent piping].

Retain "Off-Floor Mounting" Subparagraph below for wall-mounted wash fountains.

11. Off-Floor Mounting: Wall bracket and ASME A112.6.1M, Type II urinal carrier.

Retain "On-Floor Mounting" Subparagraph below for floor-mounted wash fountains.

12. On-Floor Mounting: Floor bracket and wall bracket attached to [reinforcement in wall] [concrete or block wall].

a. Supplies: [NPS 1/2 (DN 15)] [NPS 3/4 (DN 20)] copper tubing with ball, gate, or globe valves.

b. Drain: Grid with [NPS 1-1/2 (DN 40)] [NPS 2 (DN 50)] tailpiece.

c. Drain Piping: [NPS 1-1/2 (DN 40)] [NPS 2 (DN 50)] P-trap, waste to wall, and wall flange.

2.4 STAINLESS-STEEL, SEMICIRCULAR WASH FOUNTAINS

Copy "Wash Fountains" Paragraph below and re-edit for each type of semicircular wash fountain required.

Insert letter and number combination to complete drawing designation. Use these designations on Drawings to identify each stainless-steel, semicircular wash fountain.

A. Wash Fountains <Insert drawing designation>: [Off] [On]-floor, stainless-steel, semicircular receptor.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Acorn Engineering Company.

b. Bradley Corporation.

c. Intersan Manufacturing Company.

d. Willoughby Industries.

e. <Insert manufacturer's name>.

3. Standard: IAPMO IGC 156.

4. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

5. Receptor:

a. Standard: ASME A112.19.3/CSA B45.4 for stainless-steel receptor.

b. Nominal Diameter: [36 to 39 inches (914 to 990 mm)] [39 inches (990 mm)] [42 inches (1067 mm)] [54 inches (1372 mm)].

Retain first option in "Height to Rim" Subparagraph below for on-floor receptors, or insert dimension for off-floor receptors for children and elderly/handicapped persons.

c. Height to Rim: [34 inches (864 mm)] <Insert dimension> above floor.

d. Color or Finish: [Not applicable] <Insert if required>.

e. Drain: Grid with [NPS 1-1/2 (DN 40)] [NPS 2 (DN 50)] tailpiece.

6. Spray Head:

a. Material: Stainless steel or integral part of receptor back.

b. Number of User Stations: [Two] [Three] [Four].

c. Spray Nozzles: Chrome-plated brass or stainless steel complying with NSF 61 and ASME A112.18.1/CSA B125.1.

Verify option retained in "Control" Subparagraph below is available from listed manufacturers and for type of wash fountain required.

d. Control: [Collective, foot-rail] [Individual foot-pedal] [Individual push-button] [Individual, hardwired sensor] [Individual, battery-powered sensor] actuation with [pressure-balancing] [thermostatic] mixing valve complying with ASSE 1016 and having check stops; comply with NSF 61.

Retain "Sensor" Subparagraph below if retaining "Individual, hardwired sensor" or "Individual, battery-powered sensor" option in "Control" Subparagraph above.

e. Sensor: ASME A112.18.1/CSA B125.1 and UL 1951.

Verify "Hardwired, sensor actuated" or "Battery powered, sensor actuated" option, if retained in "Liquid-Soap Dispensers" Subparagraph below, is available from listed manufacturers and for type of wash fountain required. Typically, sensor-operated soap dispensers are battery powered; however, they require hardwiring if the nozzles are hardwired.

7. Liquid-Soap Dispensers: [Manual] [Hardwired, sensor actuated] [Battery powered, sensor actuated] [Not required], for each user station.

Retain "Sensor" Subparagraph below if retaining "Hardwired, sensor actuated" or "Battery powered, sensor actuated" option in "Liquid-Soap Dispensers" Subparagraph above.

a. Sensor: ASME A112.18.1/CSA B125.1 and UL 1951.

8. Supply Fittings:

a. Piping: [NPS 1/2 (DN 15)] [NPS 3/4 (DN 20)] copper tubing.

b. Valves: Shutoff valve on each supply.

c. Supply Piping: From [bottom] [top] [wall].

9. Waste Fittings:

a. Standard: ASME A112.18.2/CSA B125.2.

b. Trap and Drain Piping: [NPS 1-1/2 (DN 40)] [NPS 2 (DN 50)].

c. Vent Piping: [Not required] [NPS 1-1/2 (DN 40) to ceiling].

Retain "Shroud" Subparagraph below if required to conceal vertical supply and vent piping.

10. Shroud: [Not required] [Stainless steel of size to cover supply and vent piping].

Retain "Off-Floor Mounting" Subparagraph below for wall-mounted wash fountains.

11. Off-Floor Mounting: Wall bracket and ASME A112.6.1M, Type II urinal carrier.

Retain "On-Floor Mounting" Subparagraph below for floor-mounted wash fountains.

12. On-Floor Mounting: Floor bracket and wall bracket attached to [reinforcement in wall] [concrete or block wall].

a. Supplies: [NPS 1/2 (DN 15)] [NPS 3/4 (DN 20)] copper tubing with ball, gate, or globe valves.

b. Drain: Grid with [NPS 1-1/2 (DN 40)] [NPS 2 (DN 50)] tailpiece.

c. Drain Piping: [NPS 1-1/2 (DN 40)] [NPS 2 (DN 50)] P-trap, waste to wall, and wall flange.

2.5 SOLID-SURFACE, LINEAR WASH FOUNTAINS

Copy "Wash Fountains" Paragraph below and re-edit for each type of linear wash fountain required.

Insert letter and number combination to complete drawing designation. Use these designations on Drawings to identify each solid-surface, linear (side-by-side) wash fountain.

A. Wash Fountains <Insert drawing designation>: Solid-surface, linear (side-by-side) receptor.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Acorn Engineering Company.

b. Intersan Manufacturing Company.

c. <Insert manufacturer's name>.

3. Standard: IAPMO IGC 156.

4. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

5. Bowl(s) and Counter:

a. Standard: ICPA SS-1 for solid-surface bowls.

b. Height to Rim: [34 inches (864 mm)] <Insert dimension> above floor.

c. Color or Finish: [Not applicable] <Insert if required>.

d. Number of Bowls: [One] [Two] [Three] [Four].

e. Drain: Grid with NPS 1-1/2 (DN 40) tailpiece, each bowl.

6. Pedestal: [Not required] [Required, with access panel].

7. Faucets:

a. Standards: ASME A112.18.1/CSA B125.1 and NSF 61.

b. Type: Manufacturer's standard, chrome-plated solid brass, each bowl.

Verify option retained in "Control" Subparagraph below is available from listed manufacturers and for type of wash fountain required.

c. Control: [Manual, push-button] [Hardwired, sensor-actuated] [Battery-powered, sensor-actuated][, pressure-balancing] mixing valve with check stops for each user station.

Retain "Sensor" Subparagraph below if retaining "Hardwired, sensor-actuated" or "Battery-powered, sensor-actuated" option in "Control" Subparagraph above.

d. Sensor: ASME A112.18.1/CSA B125.1 and UL 1951.

Verify "Hardwired, sensor actuated" or "Battery powered, sensor actuated" option, if retained in "Liquid-Soap Dispensers" Subparagraph below, is available from listed manufacturers and for type of wash fountain required. Typically, sensor-operated soap dispensers are battery powered; however, they require hardwiring if the nozzles are hardwired.

8. Liquid-Soap Dispensers: [Manual] [Hardwired, sensor actuated] [Battery powered, sensor actuated] [Not required], for each user station.

Retain "Sensor" Subparagraph below if retaining "Hardwired, sensor actuated" or "Battery powered, sensor actuated" option in "Liquid-Soap Dispensers" Subparagraph above.

a. Sensor: ASME A112.18.1/CSA B125.1 and UL 1951.

9. Mounting: Off floor on wall brackets and ASME A112.6.1M, Type II urinal carriers[, each bowl].

10. Supply Fittings:

a. Piping: NPS 1/2 (DN 15) copper tubing, each bowl.

b. Valves: Shutoff valve on each supply.

c. Supply Piping: From wall.

11. Waste Fittings:

a. Standard: ASME A112.18.2/CSA B125.2.

b. Trap and Drain Piping: NPS 1-1/2 (DN 40), each bowl.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Install wash fountains level and plumb according to roughing-in drawings.

B. Set freestanding wash fountains on floor.

C. Install off-floor carrier supports, affixed to building substrate, for wall-mounted wash fountains.

D. Install accessible, wall-mounted wash fountains at mounting height for handicapped/elderly according to ICC A117.1.

E. Install water-supply piping with shutoff valve on each supply to each wash fountain to be connected to domestic-water distribution piping. Use ball, gate, or globe valve. Install valves in locations where they can be easily reached for operation. Valves are specified in Section 220523 "General-Duty Valves for Plumbing Piping."

F. Install trap and waste piping on each drain outlet of each wash fountain to be connected to sanitary drainage system.

G. Install wall flanges or escutcheons at piping wall penetrations in exposed, finished locations. Use deep-pattern escutcheons if required to conceal protruding fittings. Comply with escutcheon requirements specified in Section 220518 "Escutcheons for Plumbing Piping."

H. Seal joints between fixtures and walls using sanitary-type, one-part, mildew-resistant, silicone sealant. Match sealant color to fixture color. Comply with sealant requirements specified in Section 079200 "Joint Sealants."

3.2 CONNECTIONS

Coordinate piping installations and specialty arrangements with Drawings and with requirements specified in piping systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Connect wash fountains with water supplies, stops, and risers, and with traps, soil, waste, and vent piping. Use size fittings required to match fixtures.

B. Comply with requirements for water piping specified in Section 221116 "Domestic Water Piping."

C. Comply with requirements for soil and waste drainage piping[ and vent piping] specified in Section 221316 "Sanitary Waste and Vent Piping."

D. Install protective-shielding pipe covers and enclosures on exposed supplies and waste piping of accessible wash fountains. Comply with requirements in Section 220719 "Plumbing Piping Insulation."

3.3 ADJUSTING

A. Operate and adjust wash fountains and controls. Replace damaged and malfunctioning wash fountains, fittings, and controls.

B. Adjust water pressure at faucets to produce proper flow.

C. Install fresh batteries in battery-powered, electronic-sensor mechanisms.

3.4 CLEANING AND PROTECTION

A. After installing wash fountains, inspect and repair damaged finishes.

B. Clean wash fountains, faucets, and other fittings with manufacturers' recommended cleaning methods and materials.

C. Provide protective covering for installed wash fountains and fittings.

D. Do not allow use of wash fountains for temporary facilities unless approved in writing by Owner.

END OF SECTION 224233

	WASH FOUNTAINS
	224233 - 1



