Copyright 2012 AIA
MasterSpec Professional
03/12

Copyright 2012 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 224300 - HEALTHCARE PLUMBING FIXTURES
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section includes the following healthcare fixtures and specialties:

1. Healthcare water closets.

2. Healthcare showers.

3. Healthcare bathing units.

4. Bedpan washers.

5. Clinic sinks.

6. Plaster sinks.

7. Scrub sinks.

B. Related Requirements:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

1. Section 224100 "Residential Plumbing Fixtures" for residential fixtures for use in healthcare facilities, but not requiring special healthcare fixture attributes.

2. Section 224213.13 "Commercial Water Closets" for conventional water closets, flushometer valves, carriers, and seats for use healthcare facilities, but not requiring special healthcare fixture attributes.

3. Section 224213.16 "Commercial Urinals" for urinals for use in healthcare facilities.

4. Section 224216.13 "Commercial Lavatories" for lavatories for use in healthcare facilities, but not requiring special healthcare fixture attributes.

5. Section 224216.16 "Commercial Sinks" for sinks for use in healthcare facilities, but not requiring special healthcare fixture attributes.

6. Section 224223 "Commercial Showers" for showers for use in healthcare facilities, but not requiring special healthcare fixture attributes.

7. Section 224500 "Emergency Plumbing Fixtures" for emergency showers and eye-wash units.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product.

Retain "LEED Submittals" Paragraph below if applying for LEED certification. See the "LEED Rating System" Article in the Evaluations.

B. LEED Submittals:

Retain one of three "Product Data" subparagraphs below. Retain first subparagraph for LEED-NC and LEED-CS.

1. Product Data: Documentation indicating that flow and water consumption requirements comply with [Prerequisite WE 1] [Prerequisite WE 1 and Credit WE 3] [Prerequisite WE 1, Credit WE 2, and Credit WE 3].

Retain first "Product Data" Subparagraph below for LEED-CI.

2. Product Data: Documentation indicating that flow and water consumption requirements comply with Prerequisite WE 1[ and Credit WE 1].

Retain "Product Data" Subparagraph below for LEED-EB.

3. Product Data: Documentation indicating that flow and water consumption requirements comply with Prerequisite WE 1[ and Credit WE 2].

Retain "Shop Drawings" Paragraph below if fixtures or equipment includes wiring.

C. Shop Drawings: Include diagrams for power, signal, and control wiring.

1.3 CLOSEOUT SUBMITTALS

A. Operation and Maintenance Data: For plumbing fixtures and faucets to include in operation and maintenance manuals.

1. In addition to items specified in Section 017823 "Operation and Maintenance Data," include the following:

a. Servicing and adjustments of [flushometer valves] [healthcare bathing units] [and] [bedpan washer/sanitizers].

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

2.1 HEALTHCARE WATER CLOSETS

Copy "Healthcare Water Closets" Paragraph below and re-edit for each type of wall-mounted healthcare water closet required.

Insert letter and number combination to complete drawing designation. Use these designations on Drawings to identify each healthcare water closet.

A. Healthcare Water Closets <Insert drawing designation>: Wall mounted, [top] [back] spud[, accessible].

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. American Standard America.

b. Crane Plumbing, L.L.C.

c. Kohler Co.

d. Zurn Industries, LLC; Commercial Brass and Fixtures.

e. <Insert manufacturer's name>.

3. Bowl:

a. Standards: ASME A112.19.2/CSA B45.1 and ASME A112.19.5.

b. Material: Vitreous china.

c. Type: Siphon jet.

d. Style: Flushometer valve.

e. Height: Standard.

f. Rim Contour: Elongated with bedpan lugs or slots.

g. Water Consumption: [1.28 gal. (4.8 L)] [1.6 gal. (6 L)] per flush.

h. Spud Size: NPS 1-1/2 (DN 40).

Coordinate "Flushometer Valve" Subparagraph below with "Flushometer Valves" Article. To require conventional flushometer valves on healthcare water closets, cross-reference Section 224213.13 "Commercial Water Closets."

4. Flushometer Valve: <Insert flushometer-valve designation>.

Coordinate "Toilet Seat" Subparagraph with "Toilet Seats" Article.

5. Toilet Seat: <Insert toilet-seat designation>.

6. Support:

a. Standard: ASME A112.6.1M.

b. Description: Waste-fitting assembly as required to match drainage piping material and arrangement with faceplates, couplings gaskets, and feet; bolts and hardware matching fixture.[ Include additional extension coupling, faceplate, and feet for installation in wide pipe space.]

c. Water-Closet Mounting Height: [Standard] [Child] [Handicapped/elderly according to ICC A117.1].

Copy "Healthcare Water Closets" Paragraph below and re-edit for each type of floor-mounted, floor-outlet, healthcare water closet required.

Insert letter and number combination to complete drawing designation. Use these designations on Drawings to identify each healthcare water closet.

B. Healthcare Water Closets <Insert drawing designation>: Floor mounted, floor outlet, [top] [back] spud[, accessible].

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. American Standard America.

b. Crane Plumbing, L.L.C.

c. Kohler Co.

d. Zurn Industries, LLC; Commercial Brass and Fixtures.

e. <Insert manufacturer's name>.

3. Bowl:

a. Standards: ASME A112.19.2/CSA B45.1 and ASME A112.19.5.

b. Material: Vitreous china.

c. Type: Siphon jet.

d. Style: Flushometer valve.

e. Height: [Standard] [Handicapped/elderly].

f. Rim Contour: Elongated with bedpan lugs or slots.

g. Water Consumption: [1.28 gal. (4.8 L)] [1.6 gal. (6 L)] per flush.

h. Spud Size: NPS 1-1/2 (DN 40).

Coordinate "Flushometer Valve" Subparagraph below with "Flushometer Valves" Article. To require conventional flushometer valves on healthcare water closets, cross-reference Section 224213.13 "Commercial Water Closets."

4. Flushometer Valve: <Insert flushometer-valve designation>.

Coordinate "Toilet Seat" Subparagraph with "Toilet Seats" Article.

5. Toilet Seat: <Insert toilet-seat designation>.

2.2 FLUSHOMETER VALVES

Caution: Consumption of flushometer valves for healthcare water closets and clinic sinks must match the fixture consumption. Copy "Lever-Handle, Diaphragm Flushometer Valves" Paragraph below and re-edit for each type of lever-handle, diaphragm flushometer valve with bedpan washer required. A separate bedpan washer is unnecessary where this flushometer valve is specified.

Insert letter and number combination number to complete designation. Use these designations on Drawings to identify each flushometer valve.

A. Lever-Handle, Diaphragm Flushometer Valves <Insert designation>.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Delany Flush Valves.

b. Sloan Valve Company.

c. Zurn Industries, LLC; Commercial Brass and Fixtures.

d. <Insert manufacturer's name>.

3. Standard: ASSE 1037.

4. Minimum Pressure Rating: 125 psig (860 kPa).

5. Features: Integral check stop, backflow-prevention device, and outlet-tube-mounted bedpan washer.

6. Material: Brass body with corrosion-resistant components.

7. Exposed Flushometer-Valve Finish: Chrome plated.

8. Style: Exposed.

9. Consumption: [1.28 gal. (4.8 L)] [1.6 gal. (6 L)] [3.5 gal. (13.2 L)] <Insert value> per flush.

10. Minimum Inlet: NPS 1 (DN 25).

11. Minimum Outlet: NPS 1-1/4 (DN 32), extended length.

2.3 TOILET SEATS

Copy "Toilet Seats" Paragraph below and re-edit for each type of toilet seat required.

Insert letter and number combination to complete designation. Use these designations on Drawings to identify each toilet seat.

A. Toilet Seats <Insert designation>.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Centoco Manufacturing Corporation.

b. Church Seats.

c. Kohler Co.

d. Olsonite Seat Co.

e. Sperzel of Lexington.

f. Zurn Industries, LLC; Commercial Brass and Fixtures.

g. <Insert manufacturer's name>.

3. Standard: IAPMO Z124.5.

4. Material: Plastic with antimicrobial agent.

5. Type: [Commercial (standard)] [Commercial (heavy duty)].

6. Shape: Elongated rim, open front.

7. Hinge: Check.

8. Hinge Material: Noncorroding metal.

9. Color: White.

2.4 HEALTHCARE SHOWERS

Copy "Healthcare Showers" Paragraph below and re-edit for each type of healthcare shower required.

Insert letter and number combination to complete drawing designation. Use these designations on Drawings to identify each healthcare shower.

A. Healthcare Showers <Insert drawing designation>: Accessible, [glass-fiber-reinforced plastic] [acrylic].

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

Retain one of two lists of manufacturers below. First list below is for fiber-glass-reinforced plastic showers.

a. Aqua Glass Corporation.

b. Clarion Bathware.

c. Florestone Products Co., Inc.

d. <Insert manufacturer's name>.

List of manufacturers below is for acrylic showers.

e. Aqua Bath Company, Inc.

f. Aqua Glass Corporation.

g. Clarion Bathware.

h. Crane Plumbing, L.L.C.

i. <Insert manufacturer's name>.

3. Standard: ANSI Z124.1.2 and complying with ICC A117.1 for roll-in shower compartments.

4. Nominal Size: [60 by 36 inches (1524 by 915 mm)] <Insert dimensions>.

Retain one of two "Surround" subparagraphs below. Retain first paragraph for fiber-glass-reinforced plastic surround; retain second paragraph for acrylic surround.

5. Surround: One piece[ or sealed, multiple piece].

6. Surround: One piece.

7. Bathing Surface: Slip resistant according to ASTM F 462.

8. Color: [White] <Insert color>.

9. Drain Location: [Left side] [Center] [Right side].

10. Accessibility Options: Include grab bar and bench.

Coordinate "Faucet" Subparagraph with "Healthcare Shower Faucets" Article.

11. Faucet: <Insert healthcare shower-faucet designation>.

12. Drain: Grid, NPS 2 (DN 50), complying with ASME A112.18.2/CSA B125.2.

2.5 HEALTHCARE SHOWER FAUCETS

A. NSF Standard: Comply with NSF 61, "Drinking Water System Components - Health Effects," for faucet materials that will be in contact with potable water.

Copy "Healthcare Shower Faucets" Paragraph below and re-edit for each type of pressure-balance mixing valve, healthcare shower faucet required.

Insert letter and number combination to complete designation. Use these designations on Drawings to identify each healthcare shower faucet.

B. Healthcare Shower Faucets <Insert drawing designation>: Pressure-balance mixing valve.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. American Standard America.

b. Chicago Faucets.

c. Ferguson Enterprises, Inc.; ProFlo Brand.

d. Kohler Co.

e. Lawler Manufacturing Co., Inc.

f. Leonard Valve Company.

g. Matco-Norca.

h. Moen Incorporated.

i. Powers; a division of Watts Water Technologies, Inc.

j. Speakman Company.

k. Zurn Industries, LLC; AquaSpec Commercial Faucet Products.

l. <Insert manufacturer's name>.

3. Faucet:

a. Standards: ASME A112.18.1/CSA B125.1 and ASSE 1016.

b. Body Material: Solid brass.

c. Finish: Polished chrome plate.

d. Maximum Flow Rate: [2.5 gpm (9.5 L/min.)] <Insert value> unless otherwise indicated.

e. Mounting: [Concealed] [Exposed].

f. Operation: Single-handle, [push-pull] [or] [twist or rotate] control.

g. Antiscald Device: [Integral with mixing valve] [Separate unit] [Not required].

h. Check Stops: Check-valve type, integral with or attached to body; on hot- and cold-water-supply connections.

i. Indicators: For hot and cold water.

4. Shower Head:

a. Standard: ASME A112.18.1/CSA B125.1.

b. Type: [Ball joint with arm and flange] [Without ball joint, but with arm and flange] [Ball joint and head integral with mounting flange] [Integral with mounting flange] [Hand held, slide bar mounted] [Hand held, hook mounted] <Insert type>.

c. Shower Head Material: Metallic with chrome-plated finish.

d. Spray Pattern: [Adjustable] [Fixed].

e. Integral Volume Control: [Not required] [Required].

Retain "Shower-Arm, Flow-Control Fitting" Subparagraph below only if option retained in "Type" Subparagraph above includes arm and flange; otherwise, delete "Shower-Arm, Flow-Control Fitting" Subparagraph below.

f. Shower-Arm, Flow-Control Fitting: [Not required] [1.5 gpm (5.7 L/min.)] [2.0 gpm (7.6 L/min.)].

Verify availability of feature in "Temperature Indicator" Subparagraph below if required.

g. Temperature Indicator: [Integral with faucet] [Not required].

2.6 HEALTHCARE BATHING UNITS

Caution: Provide one or more floor drains near bathing units.

Healthcare bathing units in paragraph below may require additional data for optional features or special applications.

Copy "Healthcare Bathing Units" Paragraph below and re-edit for each type of healthcare bathing unit required.

Insert letter and number combination to complete drawing designation. Use these designations on Drawings to identify each healthcare bathing unit.

A. Healthcare Bathing Units <Insert drawing designation>: [Side] [Transfer-lift] [Slide-on] entry, [adjustable] [fixed] height.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. ARJO, Inc.

b. Clarion Bathware.

c. Invacare Continuing Care Group.

d. <Insert manufacturer's name>.

3. Fixture: Plastic-tub, institutional bath fixture with integral controls.

a. Tub Size: [60 by 30 inches (1524 by 762 mm)] <Insert dimensions>.

b. Controls: Vacuum breakers on supplies, thermostatic mixing valve, tub fill spout, and hand-held shower head.

4. Supply Connections: [NPS 3/4 (DN 20)] [NPS 1 (DN 25)] with shutoff valve.

5. Drain: Manufacturer's standard [NPS 1-1/2 (DN 40)] [NPS 2 (DN 50)] with tailpiece.

6. Drain Piping: [NPS 1-1/2 (DN 40)] [NPS 2 (DN 50)] cast-brass P-trap, waste to wall, and wall flange complying with ASME A112.18.2/CSA B125.2. Include combined drain piping if two drains.

7. Lift System: [Not required] <Insert description>.

8. Unit Electrical Characteristics:

a. Volts: [120] [240] [277] [480] <Insert number>.

b. Phase(s): [One] [Three].

c. Hertz: [60] <Insert number>.

d. Full-Load Amperes: <Insert value>.

e. Minimum Circuit Ampacity: <Insert value>.

f. Maximum Overcurrent Protection: <Insert amperage>.

Copy "Healthcare Bathing Units" Paragraph below and re-edit for each type of front-entry shower, healthcare bathing unit required.

Insert letter and number combination to complete drawing designation. Use these designations on Drawings to identify each healthcare bathing unit.

B. Healthcare Bathing Units <Insert drawing designation>: Front-entry shower.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. ARJO, Inc.

b. Invacare Continuing Care Group.

c. <Insert manufacturer's name>.

3. Fixture: Plastic-tub, institutional fixture with integral controls.

a. Cabinet Size: [35 by 41 inches (889 by 1041 mm)] <Insert dimensions>.

b. Controls: Vacuum breakers on supplies, thermostatic mixing valve, tub fill spout, and hand-held shower head.

4. Supply Connections: [NPS 3/4 (DN 20)] [NPS 1 (DN 25)] with shutoff valve.

5. Drain: Manufacturer's standard NPS 2 (DN 50) with tailpiece.

6. Drain Piping: NPS 2 (DN 50) P-trap, waste to wall, and wall flange complying with ASME A112.18.2/CSA B125.2. Include combined drain piping if two drains.

7. Unit Electrical Characteristics:

a. Volts: [120] [240] [277] [480] <Insert number>.

b. Phase(s): [One] [Three].

c. Hertz: [60] <Insert number>.

d. Full-Load Amperes: <Insert value>.

e. Minimum Circuit Ampacity: <Insert value>.

f. Maximum Overcurrent Protection: <Insert amperage>.

2.7 BEDPAN WASHERS

See "Flushometer Valves" Article for flushometer-valve-mounted bedpan washers.

Copy "Bedpan Washers" Paragraph below and re-edit for each type of wall-mounted, compact bedpan washer required.

Insert letter and number combination to complete drawing designation. Use these designations on Drawings to identify each bedpan washer.

A. Bedpan Washers <Insert drawing designation>: Wall mounted, compact.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. American Standard America.

b. Chicago Faucets.

c. Kohler Co.

d. Speakman Company.

e. T & S Brass and Bronze Works, Inc.

f. Whitehall Manufacturing; a division of Acorn Engineering Company.

g. <Insert manufacturer's name>.

3. Standard: ASME A112.18.1/CSA B125.1.

4. Hose Assembly: [48-inch- (1220-mm-)] <Insert dimension> long rubber or vinyl hose with self-closing, hand-held spray nozzle, wall bracket, and hook.

5. Vacuum Breaker: ASSE 1001, atmospheric, wall mounted.

6. Shutoff Valve: Wall-mounted, [cross-handle] <Insert type> supply stop upstream of vacuum breaker.

7. Connecting Piping: Concealed.

8. Finish: Polished chrome-plated finish on exposed metal parts.

9. Supply Connection: [NPS 1/2 (DN 15)] <Insert size>.

2.8 BEDPAN WASHING EQUIPMENT

Units in this article require separate atmospheric and sanitary vents. Do not connect atmospheric-vent to sanitary-vent piping.

Copy "Bedpan Washers/Sanitizers" Paragraph below and re-edit for each type of bedpan washer/sanitizer required.

Insert letter and number combination to complete drawing designation. Use these designations on Drawings to identify each bedpan washer/sanitizer.

A. Bedpan Washers/Sanitizers <Insert drawing designation>: [Recessed] [Wall] mounted.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. STERIS Corporation.

b. <Insert manufacturer's name>.

3. Fixture:

a. Construction: Cast-iron chamber and P-trap waste assembly with spray nozzles and [enameled] [stainless]-steel front panel and cover box.

b. Controls: Electric, 120-V ac, automatic operation with timer, solenoid valves, and circuit breaker.

c. Door Mechanism: Foot-pedal operation.

4. Supply Connections: NPS 1 (DN 25) cold water and NPS 3/8 (DN 10) [hot water] [steam].

5. Drain Piping: NPS 3 (DN 80) P-trap and soil pipe.

6. Atmospheric Vent Connection: NPS 2 (DN 50).

7. Mounting Hardware: Matching fixture-mounting arrangement.

8. Accessories:

a. Bedpan Rack(s): [One] [Two] <Insert number>.

b. Urinal Rack(s): [One] [Two] <Insert number>.

c. Drain Tray(s): [One] [Two] <Insert number>.

2.9 CLINIC SINKS

Copy "Clinic Sinks" Paragraph below and re-edit for each type of floor-mounted clinic sink required.

Insert letter and number combination to complete drawing designation. Use these designations on Drawings to identify each clinic sink.

A. Clinic Sinks <Insert drawing designation>: Floor mounted.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. American Standard America.

b. Crane Plumbing, L.L.C.

c. Kohler Co.

d. Zurn Industries, LLC; Commercial Brass and Fixtures.

e. <Insert manufacturer's name>.

Caution: This fixture may require a raised base to attain correct height. Verify with manufacturer.

3. Fixture: Bottom-outlet, vitreous-china, siphon-jet, flushing-rim, service sink.

a. Standard: ASME A112.19.2/CSA B45.1.

b. Nominal Size: [27 by 20 inches (685 by 510 mm)] <Insert dimensions>.

c. Color: White.

d. Rim Guards: Stainless steel on front.

4. Sink Base: [10 inches (254 mm)] <Insert dimension> high; cast terrazzo if required.

Coordinate "Flushometer Valve" Subparagraph below with "Flushometer Valves" Article. Use flushometer valve designed for 3.5 gal. (13.2 L) per flush.

5. Flushometer Valve: <Insert flushometer-valve designation>.

Coordinate "Faucet" Subparagraph with "Sink Faucets" Article. Use polished, chrome-plated, solid-brass, wall-mounted, service-sink-faucet type in first subparagraph below. Include integral stops in shanks, vacuum breaker, hose-thread outlet, and pail hook.

6. Faucet: <Insert sink-faucet designation>.

7. Supply Fittings: Comply with requirements in "Supply Fittings" Article.

2.10 PLASTER SINKS

Copy "Plaster Sinks" Paragraph below and re-edit for each type of wall-mounted, vitreous-china plaster sink required.

Insert letter and number combination to complete drawing designation. Use these designations on Drawings to identify each plaster sink.

A. Plaster Sinks <Insert drawing designation>: Wall mounted, vitreous china.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2.  Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. American Standard America.

b. Crane Plumbing, L.L.C.

c. Kohler Co.

d. <Insert manufacturer's name>.

3. Fixture:

a. Standard: ASMA A112.19.2/CSA B45.1.

b. Type: Utility sink.

c. Nominal Size: [24 by 22 inches (610 by 560 mm)] [30 by 22 inches (762 by 560 mm)] <Insert dimensions> with back.

d. Color: White.

e. Faucet Holes: [One] [Two] in back.

f. Drain: Grid, NPS 1-1/2 (DN 40)[ with NPS 1-1/2 (DN 40) to NPS 2 (DN 50) adaptor].

Coordinate "Faucet" Subparagraph with "Sink Faucets" Article.

4. Faucet: <Insert sink-faucet designation>.

5. Supply Fittings: Comply with requirements in "Supply Fittings" Article.

6. Drain Piping: [NPS 1-1/2 (DN 40)] [NPS 2 (DN 50)] chrome-plated brass; 0.045-inch- (1.1-mm-) thick waste to interceptor; interceptor to wall; and wall flange complying with ASME A112.18.2/CSA B125.2.

7. Plaster Interceptor:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

a. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

b. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1) Josam Company.

2) MIFAB, Inc.

3) Jay R. Smith Mfg. Co.

4) Tyler Pipe; Wade Div.

5) Watts Drainage Products; a division of Watts Water Technologies, Inc.

6) Zurn Industries, LLC; Specification Drainage Products.

7) <Insert manufacturer's name>.

c. Description: Cast-iron or steel body and removable cover with acid-resistant-enameled interior lining and outside coating; removable, corrosion-resistant metal screens or strainer; and [NPS 1-1/2 (DN 40)] [NPS 2 (DN 50)] inlet and outlet.

8. Support: ASME A112.6.1M, Type III sink carrier with white-enameled-steel brackets.

2.11 SCRUB SINKS

Copy "Scrub Sinks" Paragraph below and re-edit for each type of vitreous-china, wall-mounted scrub sink required.

Insert letter and number combination to complete drawing designation. Use these designations on Drawings to identify each surgeon's scrub sink.

A. Scrub Sinks <Insert drawing designation>: Vitreous china, wall mounted.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. American Standard America.

b. Crane Plumbing, L.L.C.

c. Kohler Co.

d. <Insert manufacturer's name>.

3. Fixture:

a. Standard: ASME A112.19.2/CSA B45.1.

b. Nominal Size: [28 by 22 inches (710 by 560 mm)] [30 by 22 inches (762 by 560 mm)] <Insert dimensions> with back or ledge with one faucet hole.

c. Color: White.

d. Drain: [Grid] <Insert type>, NPS 1-1/2 (DN 40).

Coordinate "Faucet" Subparagraph with "Sink Faucets" Article.

4. Faucet: <Insert sink-faucet designation>.

5. Supply Fittings: Comply with requirements in "Supply Fittings" Article.

6. Waste Fittings: Comply with requirements in "Waste Fittings" Article.

7. Support: ASME A112.6.1M, Type I, Type II, or Type III sink carrier.

2.12 SINK FAUCETS

A. NSF Standard: Comply with NSF 61, "Drinking Water System Components - Health Effects," for faucet-spout materials that will be in contact with potable water.

Copy "Sink Faucets" Paragraph below and re-edit for each type of manual-operation mixing valve, sink faucet required.

Insert letter and number combination to complete drawing designation. Use these designations to identify each sink faucet.

B. Sink Faucets <Insert drawing designation>: Manual-operation mixing valve.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. American Standard America.

b. Chicago Faucets.

c. Delta Faucet Company.

d. Elkay Manufacturing Co.

e. Fisher Manufacturing Co.

f. GROHE America, Inc.

g. Just Manufacturing.

h. Kohler Co.

i. Moen Incorporation.

j. Speakman Company.

k. T & S Brass and Bronze Works, Inc.

l. Zurn Industries, LLC; Commercial Brass and Fixtures.

m. <Insert manufacturer's name>.

3. Standard: ASME A112.18.1/CSA B125.1.

4. Configuration: Hot- and cold-water indicators; coordinate faucet inlets with supplies and fixture hole punchings; coordinate outlet with spout and sink receptor.

Option in "Body Type" Subparagraph below must match fixture hole punching.

5. Body Type: [Centerset] [Widespread] [Single hole] <Insert type>.

6. Body Material: Solid brass.

7. Finish: [Chrome plated] [Polished chrome plate] <Insert finish>.

8. Maximum Flow Rate: [2.2 gpm (8.3 L/min.)] [2.5 gpm (9.5 L/min.)] <Insert value>.

Retain one of two "Control" subparagraphs below.

9. Control: [Lever] [Cross, four-arm] [Wrist-blade, 4-inch (102-mm)] [Elbow, 6-inch (152-mm)] <Insert type> handle(s).

10. Control: [Foot pedal] [Knee action] <Insert type>.

11. Mounting Type: [Deck, concealed] [Deck, exposed] [Back/wall, exposed] <Insert type>.

12. Spout Type: [Rigid] [Swivel], [low profile] [gooseneck] <Insert type>.

Retain first option in "Vacuum Breaker" Subparagraph below for sink faucets with hose-thread outlet.

13. Vacuum Breaker: [Required] [Not required] for hose outlet.

14. Spout Outlet: [Aerator] [Laminar flow] [Hose thread] [Plain end] [Spray] <Insert type>.

2.13 LAMINAR-FLOW, FAUCET-SPOUT OUTLETS

Retain this article if specifying a laminar-flow, faucet-spout outlet for any sink faucet.

Spout outlets in this article are non-aerating, produce less splashing than conventional faucet spouts, and help reduce bacteria growth.

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. AM Conservation Group, Inc.

2. Chronomite Laboratories, Inc.; a division of Acorn Engineering Company.

3. NEOPERL, Inc.

4. <Insert manufacturer's name>.

C. Description: Chrome-plated brass, faucet-spout outlet that produces non-aerating, laminar stream. Include external or internal thread that mates with faucet outlet for attachment to faucets where indicated and flow-rate range that includes faucet flow.

D. NSF Standard: Comply with NSF 61, "Drinking Water System Components - Health Effects," for faucet-spout-outlet materials that will be in contact with potable water.

2.14 SUPPLY FITTINGS

A. NSF Standard: Comply with NSF 61, "Drinking Water System Components - Health Effects," for supply-fitting materials that will be in contact with potable water.

B. Standard: ASME A112.18.1/CSA B125.1.

C. Supply Piping: Chrome-plated brass pipe or chrome-plated copper tube matching water-supply piping size. Include chrome-plated brass or stainless-steel wall flange.

D. Supply Stops: Chrome-plated brass, one-quarter-turn, ball-type or compression valve with inlet connection matching supply piping.

Retain "Wheel handle" option in "Operation" Paragraph below for one-quarter-turn, ball-type stops.

E. Operation: [Loose key] [Wheel handle] <Insert type>.

F. Risers: NPS 1/2 (DN 15) [chrome-plated, rigid-copper pipe and brass straight or offset tailpieces] [chrome-plated, soft-copper flexible tube] [ASME A112.18.6, braided or corrugated stainless-steel, flexible hose].

2.15 WASTE FITTINGS

A. Standard: ASME A112.18.2/CSA B125.2.

B. Drain: [Grid] <Insert type> with NPS 1-1/2 DN 40 tailpiece.

C. Trap:

1. Size: NPS 1-1/2 (DN 40).

Retain one of two "Material" subparagraphs below.

2. Material: Chrome-plated, [two-piece, cast-brass trap and swivel elbow with 0.032-inch- (0.83-mm-) thick brass tube to wall] [two-piece, cast-brass trap and ground-joint swivel elbow with 0.032-inch- (0.83-mm-) thick brass tube to wall] [one-piece, cast-brass trap with swivel 0.029-inch- (73-mm-) thick tubular brass wall bend] <Insert trap type>; and chrome-plated brass or steel wall flange.

3. Material: Stainless-steel, two-piece trap and swivel elbow with 0.012-inch- (0.30-mm-) thick stainless-steel tube to wall; and stainless-steel wall flange.

2.16 GROUT

A. Standard: ASTM C 1107/C 1107M, Grade B, post-hardening and volume-adjusting, dry, hydraulic-cement grout.

B. Characteristics: Nonshrink; recommended for interior and exterior applications.

C. Design Mix: 5000-psi (34.5-MPa), 28-day compressive strength.

D. Packaging: Premixed and factory packaged.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Install healthcare plumbing fixtures level and plumb according to roughing-in drawings.

B. Install supports, affixed to building substrate, for wall-mounted fixtures.

1. Use carrier supports with waste fitting and seal for back-outlet fixtures.

2. Use carrier supports without waste fitting for fixtures with tubular waste piping.

3. Use chair-type carrier supports with rectangular steel uprights for accessible fixtures.

C. Install floor-mounted healthcare water closets on bowl-to-drain, connecting fitting attachments to piping or building substrate.

First paragraph below applies to counter-mounted fixtures such as sinks.

D. Install counter-mounted fixtures in and attached to casework.

E. Install water-supply piping with stop on each supply to each fixture to be connected to water-distribution piping. Attach supplies to supports or substrate within pipe spaces behind fixtures. Install stops in locations where they can be easily reached for operation.

1. Exception: Use ball, gate, or globe valve if supply stops are not specified with fixture. Comply with valve requirements specified in Section 220523 "General-Duty Valves for Plumbing Piping."

F. Install flushometer valves on healthcare water closets.

G. Install flushometer valves for accessible healthcare water closets, with lever handle mounted on wide side of compartment.

H. Install toilet seats on healthcare water closets.

I. Install faucet flow-control fittings with specified flow rates and patterns in faucet spouts, if faucets are not available with required rates and patterns. Include adapters if required.

J. Install laminar-flow, faucet-spout fittings in faucet spouts where laminar-flow fittings are specified.

K. Install shower flow-control fittings with specified maximum flow rates in shower arms.

L. Install traps on fixture outlets.

1. Exception: Omit trap on fixtures with integral traps.

M. Set healthcare showers in leveling bed of cement grout.

Coordinate first paragraph below with Drawings. Indicate on Drawings those fixtures and sinks that are required to be accessible.

N. Install protective shielding pipe covers and enclosures on exposed supplies and waste piping of accessible sinks. Comply with requirements in Section 220719 "Plumbing Piping Insulation."

O. Seal joints between healthcare plumbing fixtures, counters, floors, and walls using sanitary-type, one-part, mildew-resistant silicone sealant. Match sealant color to fixture color. Comply with sealant requirements specified in Section 079200 "Joint Sealants."

P. Install wall flanges or escutcheons at piping wall penetrations in exposed, finished locations. Use deep-pattern escutcheons if required to conceal protruding fittings. Comply with escutcheon requirements specified in Section 220518 "Escutcheons for Plumbing Piping."

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

Q. Connect fixtures with water supplies, stops, and risers, and with traps, soil, waste, and vent piping. Use size fittings required to match fixtures.

R. Comply with requirements for water piping specified in Section 221116 "Domestic Water Piping."

S. Comply with requirements for soil and waste drainage piping[ and vent piping] specified in Section 221316 "Sanitary Waste and Vent Piping."

T. Comply with requirements for atmospheric vent piping specified in Section 221316 "Sanitary Waste and Vent Piping."

U. Install protective shielding pipe covers and enclosures on exposed supplies and waste piping of accessible sinks. Comply with requirements in Section 220719 "Plumbing Piping Insulation."

3.2 ADJUSTING

A. Operate and adjust faucets and controls. Replace damaged and malfunctioning healthcare plumbing fixtures, fittings, and controls.

B. Adjust water pressure at [faucets] [and] [flushometer valves] to produce proper flow.

C. Install fresh batteries in battery-powered, electronic-sensor mechanisms.

3.3 CLEANING AND PROTECTION

A. After installing healthcare plumbing fixtures, inspect and repair damaged finishes.

B. Clean healthcare plumbing fixtures, faucets, and other fittings with manufacturers' recommended cleaning methods and materials.

C. Provide protective covering for installed fixtures and fittings.

D. Do not allow use of healthcare plumbing fixtures for temporary facilities unless approved in writing by Owner.

END OF SECTION 224300

	HEALTHCARE PLUMBING FIXTURES
	224300 - 1



