Copyright 2011 AIA
MasterSpec Professional
06/11

Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 230519 - METERS AND GAGES FOR HVAC PIPING
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Bimetallic-actuated thermometers.

2. Liquid-in-glass thermometers.

3. Thermowells.

4. Dial-type pressure gages.

5. Gage attachments.

6. Pitot-tube flowmeters.

7. Turbine flowmeters.

8. Venturi flowmeters.

9. Impeller-turbine, thermal-energy meters.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product indicated.

B. Wiring Diagrams: For power, signal, and control wiring.

1.3 INFORMATIONAL SUBMITTALS

A. Product certificates.

1.4 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

PART 2 -  PRODUCTS

2.1 BIMETALLIC-ACTUATED THERMOMETERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Ashcroft Inc.

2. Ernst Flow Industries.

3. Marsh Bellofram.

4. Miljoco Corporation.

5. Nanmac Corporation.

6. Noshok.

7. Palmer Wahl Instrumentation Group.

8. REOTEMP Instrument Corporation.

9. Tel-Tru Manufacturing Company.

10. Trerice, H. O. Co.

11. Watts Regulator Co.; a div. of Watts Water Technologies, Inc.

12. Weiss Instruments, Inc.

13. WIKA Instrument Corporation - USA.

14. Winters Instruments - U.S.

15. <Insert manufacturer's name>.

C. Standard: ASME B40.200.

Case in first paragraph below will typically be the sealed (dry) type. Hermetically sealed cases are available.

D. Case: [Liquid-filled] [and] [sealed] type(s); stainless steel with [3-inch (76-mm)] [5-inch (127-mm)] <Insert dimension> nominal diameter.

E. Dial: [Nonreflective aluminum] <Insert material> with permanently etched scale markings and scales in [deg F (deg C)] [deg F and deg C].

F. Connector Type(s): Union joint, [adjustable angle] [rigid, back] [and] [rigid, bottom] <Insert type>, with unified-inch screw threads.

G. Connector Size: [1/2 inch (13 mm)] <Insert dimension>, with ASME B1.1 screw threads.

H. Stem: 0.25 or 0.375 inch (6.4 or 9.4 mm) in diameter; stainless steel.

I. Window: [Plain glass] [or] [plastic] <Insert material>.

J. Ring: Stainless steel.

K. Element: Bimetal coil.

L. Pointer: Dark-colored metal.

M. Accuracy: Plus or minus [1] [1.5] <Insert number> percent of scale range.

2.2 LIQUID-IN-GLASS THERMOMETERS

A. Metal-Case, Industrial-Style, Liquid-in-Glass Thermometers:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2.  Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Flo Fab Inc.

b. Miljoco Corporation.

c. Palmer Wahl Instrumentation Group.

d. Tel-Tru Manufacturing Company.

e. Trerice, H. O. Co.

f. Weiss Instruments, Inc.

g. Winters Instruments - U.S.

h. <Insert manufacturer's name>.

3. Standard: ASME B40.200.

4. Case: [Cast aluminum] <Insert material>; [7-inch (178-mm)] [9-inch (229-mm)] nominal size unless otherwise indicated.

5. Case Form: [Adjustable angle] [Back angle] [Straight] <Insert form> unless otherwise indicated.

6. Tube: Glass with magnifying lens and blue[ or red] organic liquid.

7. Tube Background: Nonreflective aluminum with permanently etched scale markings graduated in [deg F (deg C)] [deg F and deg C].

8. Window: [Glass] [or] [plastic] <Insert material>.

9. Stem: [Aluminum] <Insert material> and of length to suit installation.

a. Design for Air-Duct Installation: With ventilated shroud.

b. Design for Thermowell Installation: Bare stem.

10. Connector: 1-1/4 inches (32 mm), with ASME B1.1 screw threads.

11. Accuracy: Plus or minus 1 percent of scale range or one scale division, to a maximum of 1.5 percent of scale range.

B. Plastic-Case, Industrial-Style, Liquid-in-Glass Thermometers:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Ernst Flow Industries.

b. Marsh Bellofram.

c. Miljoco Corporation.

d. Palmer Wahl Instrumentation Group.

e. REOTEMP Instrument Corporation.

f. Watts Regulator Co.; a div. of Watts Water Technologies, Inc.

g. Weiss Instruments, Inc.

h. WIKA Instrument Corporation - USA.

i. <Insert manufacturer's name>.

3. Standard: ASME B40.200.

4. Case: [Plastic] <Insert material>; [7-inch (178-mm)] [9-inch (229-mm)] nominal size unless otherwise indicated.

5. Case Form: [Adjustable angle] [Back angle] [Straight] <Insert form> unless otherwise indicated.

6. Tube: Glass with magnifying lens and blue[ or red] organic liquid.

7. Tube Background: Nonreflective aluminum with permanently etched scale markings graduated in [deg F (deg C)] [deg F and deg C].

8. Window: [Glass] [or] [plastic] <Insert material>.

9. Stem: [Aluminum] [Brass] [Stainless steel] [Aluminum, brass, or stainless steel] <Insert material> and of length to suit installation.

a. Design for Air-Duct Installation: With ventilated shroud.

b. Design for Thermowell Installation: Bare stem.

10. Connector: 1-1/4 inches (32 mm), with ASME B1.1 screw threads.

11. Accuracy: Plus or minus 1 percent of scale range or one scale division, to a maximum of 1.5 percent of scale range.

2.3 DUCT-THERMOMETER MOUNTING BRACKETS

A. Description: Flanged bracket with screw holes, for attachment to air duct and made to hold thermometer stem.

2.4 THERMOWELLS

ASME B40.200 uses the following symbols for thermowell materials: "CNR" for copper nickel (90-10), "CUNI" for copper nickel (70-30), "CRES" for corrosion-resistant steel, "NICU" for nickel copper, "ALBR" for aluminum bronze, and "CSA" for steel. Other materials are allowed.

A. Thermowells:

1. Standard: ASME B40.200.

2. Description: Pressure-tight, socket-type fitting made for insertion into piping tee fitting.

3. Material for Use with Copper Tubing: [CNR] [or] [CUNI] <Insert material>.

4. Material for Use with Steel Piping: [CRES] [CSA] <Insert material>.

5. Type: Stepped shank unless straight or tapered shank is indicated.

6. External Threads: NPS 1/2, NPS 3/4, or NPS 1, (DN 15, DN 20, or NPS 25,) ASME B1.20.1 pipe threads.

7. Internal Threads: 1/2, 3/4, and 1 inch (13, 19, and 25 mm), with ASME B1.1 screw threads.

8. Bore: Diameter required to match thermometer bulb or stem.

9. Insertion Length: Length required to match thermometer bulb or stem.

10. Lagging Extension: Include on thermowells for insulated piping and tubing.

11. Bushings: For converting size of thermowell's internal screw thread to size of thermometer connection.

B. Heat-Transfer Medium: [Mixture of graphite and glycerin] <Insert material>.

2.5 PRESSURE GAGES

A. Direct-Mounted, Metal-Case, Dial-Type Pressure Gages:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. AMETEK, Inc.; U.S. Gauge.

b. Ashcroft Inc.

c. Ernst Flow Industries.

d. Flo Fab Inc.

e. Marsh Bellofram.

f. Miljoco Corporation.

g. Noshok.

h. Palmer Wahl Instrumentation Group.

i. REOTEMP Instrument Corporation.

j. Tel-Tru Manufacturing Company.

k. Trerice, H. O. Co.

l. Watts Regulator Co.; a div. of Watts Water Technologies, Inc.

m. Weiss Instruments, Inc.

n. WIKA Instrument Corporation - USA.

o. Winters Instruments - U.S.

p. <Insert manufacturer's name>.

3. Standard: ASME B40.100.

4. Case: [Liquid-filled] [Sealed] [Open-front, pressure relief] [Solid-front, pressure relief] <Insert type> type(s); [cast aluminum or drawn steel] <Insert material>; [4-1/2-inch (114-mm)] [6-inch (152-mm)] <Insert dimension> nominal diameter.

5. Pressure-Element Assembly: Bourdon tube unless otherwise indicated.

Match pressure connection size in first subparagraph below with gage attachment size.

6. Pressure Connection: Brass, with [NPS 1/4 (DN 8)] [NPS 1/4 or NPS 1/2 (DN 8 or DN 15)] [NPS 1/2 (DN 15)], ASME B1.20.1 pipe threads and bottom-outlet type unless back-outlet type is indicated.

7. Movement: Mechanical, with link to pressure element and connection to pointer.

8. Dial: Nonreflective aluminum with permanently etched scale markings graduated in [psi (kPa)] [psi and kPa].

9. Pointer: Dark-colored metal.

10. Window: [Glass] [or] [plastic] <Insert material>.

11. Ring: [Metal] [Brass] [Stainless steel].

12. Accuracy: [Grade A, plus or minus 1 percent of middle half of] [Grade B, plus or minus 2 percent of middle half of] [Grade C, plus or minus 3 percent of middle half of] [Grade D, plus or minus 5 percent of whole] scale range.

B. Direct-Mounted, Plastic-Case, Dial-Type Pressure Gages:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. AMETEK, Inc.; U.S. Gauge.

b. Ashcroft Inc.

c. Flo Fab Inc.

d. Marsh Bellofram.

e. Miljoco Corporation.

f. Noshok.

g. Palmer Wahl Instrumentation Group.

h. REOTEMP Instrument Corporation.

i. Tel-Tru Manufacturing Company.

j. Trerice, H. O. Co.

k. Weiss Instruments, Inc.

l. WIKA Instrument Corporation - USA.

m. Winters Instruments - U.S.

n. <Insert manufacturer's name>.

3. Standard: ASME B40.100.

4. Case: [Sealed] <Insert type> type; [plastic] <Insert material>; [4-1/2-inch (114-mm)] [6-inch (152-mm)] <Insert dimension> nominal diameter.

5. Pressure-Element Assembly: Bourdon tube unless otherwise indicated.

Match pressure connection size in first subparagraph below with gage attachment size.

6. Pressure Connection: Brass, with [NPS 1/4 (DN 8)] [NPS 1/4 or NPS 1/2 (DN 8 or DN 15)] [NPS 1/2 (DN 15)], ASME B1.20.1 pipe threads and bottom-outlet type unless back-outlet type is indicated.

7. Movement: Mechanical, with link to pressure element and connection to pointer.

8. Dial: Nonreflective aluminum with permanently etched scale markings graduated in [psi (kPa)] [psi and kPa].

9. Pointer: Dark-colored metal.

10. Window: [Glass] [or] [plastic] <Insert material>.

11. Accuracy: [Grade A, plus or minus 1 percent of middle half of] [Grade B, plus or minus 2 percent of middle half of] [Grade C, plus or minus 3 percent of middle half of] [Grade D, plus or minus 5 percent of whole] scale range.

C. Remote-Mounted, Metal-Case, Dial-Type Pressure Gages:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. AMETEK, Inc.; U.S. Gauge.

b. Ashcroft Inc.

c. Ernst Flow Industries.

d. Flo Fab Inc.

e. Marsh Bellofram.

f. Miljoco Corporation.

g. Noshok.

h. Palmer Wahl Instrumentation Group.

i. REOTEMP Instrument Corporation.

j. Tel-Tru Manufacturing Company.

k. Trerice, H. O. Co.

l. Watts Regulator Co.; a div. of Watts Water Technologies, Inc.

m. Weiss Instruments, Inc.

n. WIKA Instrument Corporation - USA.

o. Winters Instruments - U.S.

p. <Insert manufacturer's name>.

3. Standard: ASME B40.100.

4. Case: [Liquid-filled] [Sealed] <Insert type> type; [cast aluminum or drawn steel] [metal] <Insert material>; [4-1/2-inch (114-mm)] [6-inch (152-mm)] <Insert dimension> nominal diameter with [back] [front] flange and holes for panel mounting.

5. Pressure-Element Assembly: Bourdon tube unless otherwise indicated.

Match pressure connection size in first subparagraph below with gage attachment size.

6. Pressure Connection: Brass, with [NPS 1/4 (DN 8)] [NPS 1/4 or NPS 1/2 (DN 8 or DN 15)] [NPS 1/2 (DN 15)], ASME B1.20.1 pipe threads and bottom-outlet type unless back-outlet type is indicated.

7. Movement: Mechanical, with link to pressure element and connection to pointer.

8. Dial: Nonreflective aluminum with permanently etched scale markings graduated in [psi (kPa)] [psi and kPa].

9. Pointer: Dark-colored metal.

10. Window: [Glass] [or] [plastic] <Insert material>.

11. Ring: [Metal] [Stainless steel] <Insert material>.

12. Accuracy: [Grade A, plus or minus 1 percent of middle half of] [Grade B, plus or minus 2 percent of middle half of] [Grade C, plus or minus 3 percent of middle half of] [Grade D, plus or minus 5 percent of whole] scale range.

D. Remote-Mounted, Plastic-Case, Dial-Type Pressure Gages:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. AMETEK, Inc.; U.S. Gauge.

b. Ashcroft Inc.

c. Miljoco Corporation.

d. Noshok.

e. Palmer Wahl Instrumentation Group.

f. REOTEMP Instrument Corporation.

g. Tel-Tru Manufacturing Company.

h. Trerice, H. O. Co.

i. Weiss Instruments, Inc.

j. WIKA Instrument Corporation - USA.

k. Winters Instruments - U.S.

l. <Insert manufacturer's name>.

3. Standard: ASME B40.100.

4. Case: [Sealed] <Insert type> type; [plastic] <Insert material>; [4-1/2-inch (114-mm)] [6-inch (152-mm)] <Insert dimension> nominal diameter with [back] [front] flange and holes for panel mounting.

5. Pressure-Element Assembly: Bourdon tube unless otherwise indicated.

Match pressure connection size in first subparagraph below with gage attachment size.

6. Pressure Connection: Brass, with [NPS 1/4 (DN 8)] [NPS 1/4 or NPS 1/2 (DN 8 or DN 15)] [NPS 1/2 (DN 15)], ASME B1.20.1 pipe threads and bottom-outlet type unless back-outlet type is indicated.

7. Movement: Mechanical, with link to pressure element and connection to pointer.

8. Dial: Nonreflective aluminum with permanently etched scale markings graduated in [psi (kPa)] [psi and kPa].

9. Pointer: Dark-colored metal.

10. Window: [Glass] [or] [plastic] <Insert material>.

11. Accuracy: [Grade A, plus or minus 1 percent of middle half of] [Grade B, plus or minus 2 percent of middle half of] [Grade C, plus or minus 3 percent of middle half of] [Grade D, plus or minus 5 percent of whole] scale range.

2.6 GAGE ATTACHMENTS

Match attachment size in three paragraphs below with pressure-gage-connection size.

A. Snubbers: ASME B40.100, brass; with [NPS 1/4 (DN 8)] [NPS 1/4 or NPS 1/2 (DN 8 or DN 15)] [NPS 1/2 (DN 15)], ASME B1.20.1 pipe threads and [piston] [porous-metal]-type surge-dampening device. Include extension for use on insulated piping.

B. Siphons: Loop-shaped section of [brass] [stainless-steel] [steel] pipe with [NPS 1/4 (DN 8)] [NPS 1/4 or NPS 1/2 (DN 8 or DN 15)] [NPS 1/2 (DN 15)] pipe threads.

C. Valves: [Brass ball] [Brass or stainless-steel needle], with [NPS 1/4 (DN 8)] [NPS 1/4 or NPS 1/2 (DN 8 or DN 15)] [NPS 1/2 (DN 15)], ASME B1.20.1 pipe threads.

2.7 FLOWMETERS

Indicate flowmeter capacity and operating conditions on Drawings.

A. Pitot-Tube Flowmeters:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. ABB; Instrumentation and Analytical.

b. Emerson Process Management; Rosemount.

c. Meriam Process Technologies.

d. Preso Meters; a division of Racine Federated Inc.

e. TACO Incorporated.

f. Veris Industries, Inc.

g. <Insert manufacturer's name>.

3. Description: Flowmeter with sensor and indicator.

4. Flow Range: Sensor and indicator shall cover operating range of equipment or system served.

5. Sensor: Insertion type; for inserting probe into piping and measuring flow directly in gallons per minute (liters per second).

a. Design: Differential-pressure-type measurement for [oil] [water] <Insert fluid>.

b. Construction: Stainless-steel probe of length to span inside of pipe, with integral transmitter and direct-reading scale.

c. Minimum Pressure Rating: [150 psig (1035 kPa)] <Insert value>.

d. Minimum Temperature Rating: [250 deg F (121 deg C)] <Insert temperature>.

6. Indicator: Hand-held meter; either an integral part of sensor or a separate meter.

7. Integral Transformer: For low-voltage power connection.

8. Accuracy: Plus or minus [3] <Insert number> percent.

9. Display: Shows rate of flow[, with register to indicate total volume in gallons (liters)].

10. Operating Instructions: Include complete instructions with each flowmeter.

B. Turbine Flowmeters:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. ABB; Instrumentation and Analytical.

b. Data Industrial Corp.

c. EMCO Flow Systems; a division of Spirax Sarco, Inc.

d. ERDCO Engineering Corp.

e. Hoffer Flow Controls, Inc.

f. Liquid Controls; a unit of IDEX Corporation.

g. McCrometer, Inc.

h. Midwest Instruments & Controls Corp.

i. ONICON Incorporated.

j. SeaMetrics, Inc.

k. Sponsler, Inc.; a unit of IDEX Corporation.

l. <Insert manufacturer's name>.

3. Description: Flowmeter with sensor and indicator.

4. Flow Range: Sensor and indicator shall cover operating range of equipment or system served.

5. Sensor: Impeller turbine; for inserting into pipe fitting or for installing in piping and measuring flow directly in gallons per minute (liters per second).

a. Design: Device or pipe fitting with inline turbine and integral direct-reading scale for [gas] [oil] [steam] [water] <Insert fluid>.

b. Construction: Bronze or stainless-steel body, with plastic turbine or impeller.

c. Minimum Pressure Rating: [150 psig (1035 kPa)] <Insert value>.

d. Minimum Temperature Rating: [180 deg F (82 deg C)] <Insert temperature>.

6. Indicator: Hand-held meter; either an integral part of sensor or a separate meter.

7. Accuracy: Plus or minus [1-1/2] <Insert number> percent.

8. Display: Shows rate of flow[, with register to indicate total volume in gallons (liters)].

9. Operating Instructions: Include complete instructions with each flowmeter.

C. Venturi Flowmeters:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. ABB; Instrumentation and Analytical.

b. Gerand Engineering Co.

c. Hyspan Precision Products, Inc.

d. Preso Meters; a division of Racine Federated Inc.

e. S. A. Armstrong Limited; Armstrong Pumps Inc.

f. Victaulic Company.

g. <Insert manufacturer's name>.

3. Description: Flowmeter with calibrated flow-measuring element, hoses or tubing, fittings, valves, indicator, and conversion chart.

4. Flow Range: Sensor and indicator shall cover operating range of equipment or system served.

5. Sensor: Venturi-type, calibrated, flow-measuring element; for installation in piping.

a. Design: Differential-pressure-type measurement for [gas] [oil] [steam] [water] <Insert fluid>.

b. Construction: Bronze, brass, or factory-primed steel, with brass fittings and attached tag with flow conversion data.

c. Minimum Pressure Rating: [250 psig (1725 kPa)] <Insert value>.

d. Minimum Temperature Rating: [250 deg F (121 deg C)] <Insert temperature>.

e. End Connections for NPS 2 (DN 50) and Smaller: Threaded.

f. End Connections for NPS 2-1/2 (DN 65) and Larger: Flanged or welded.

g. Flow Range: Flow-measuring element and flowmeter shall cover operating range of equipment or system served.

Retain one of first two subparagraphs below.

6. Permanent Indicators: Meter suitable for wall or bracket mounting, calibrated for connected flowmeter element, and having 6-inch- (152-mm-) diameter, or equivalent, dial with fittings and copper tubing for connecting to flowmeter element.

a. Scale: Gallons per minute (Liters per second).

b. Accuracy: Plus or minus [1 percent between 20 and 80 percent of scale range] <Insert accuracy>.

7. Portable Indicators: Hand-held, differential-pressure type, calibrated for connected flowmeter element and having two 12-foot (3.7-m) hoses, with carrying case.

a. Scale: Gallons per minute (Liters per second).

b. Accuracy: Plus or minus 2 percent between 20 and 80 percent of scale range.

8. Display: Shows rate of flow[, with register to indicate total volume in gallons (liters)].

9. Conversion Chart: Flow rate data compatible with sensor.

10. Operating Instructions: Include complete instructions with each flowmeter.

2.8 THERMAL-ENERGY METERS

Indicate capacity and operating conditions of thermal-energy meters on Drawings.

A. Impeller-Turbine, Thermal-Energy Meters:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Data Industrial Corp.

b. Hoffer Flow Controls, Inc.

c. ISTEC Corporation.

d. ONICON Incorporated.

e. <Insert manufacturer's name>.

3. Description: System with[ strainer,] flow sensor, temperature sensors, transmitter, indicator, and connecting wiring.

4. Flow Sensor: Impeller turbine with corrosion-resistant-metal body and transmitter; for installing in piping.

a. Design: Total thermal-energy measurement.

b. Minimum Pressure Rating: [150 psig (1035 kPa)] <Insert value>.

c. Minimum Temperature Range: [40 to 250 deg F (5 to 121 deg C)] <Insert temperature range>.

5. Temperature Sensors: Insertion-type transducer.

6. Indicator: Solid-state, integrating-type meter[ with integral battery pack]; for wall mounting.

a. Data Output: Six-digit electromechanical counter with readout in kilowatts per hour or British thermal units (joules).

b. Battery Pack: Five-year lithium battery.

7. Accuracy: Plus or minus [1] <Insert number> percent.

8. Display: Visually indicates total fluid volume in gallons (liters) and thermal-energy flow in kilowatts per hour or British thermal units (joules).

9. Strainer: Full size of main line piping.

10. Operating Instructions: Include complete instructions with each thermal-energy meter system.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Install thermowells with socket extending [a minimum of 2 inches (51 mm) into fluid] [one-third of pipe diameter] [to center of pipe] and in vertical position in piping tees.

B. Install thermowells of sizes required to match thermometer connectors. Include bushings if required to match sizes.

C. Install thermowells with extension on insulated piping.

D. Fill thermowells with heat-transfer medium.

E. Install direct-mounted thermometers in thermowells and adjust vertical and tilted positions.

F. Install remote-mounted thermometer bulbs in thermowells and install cases on panels; connect cases with tubing and support tubing to prevent kinks. Use minimum tubing length.

G. Install duct-thermometer mounting brackets in walls of ducts. Attach to duct with screws.

H. Install direct-mounted pressure gages in piping tees with pressure gage located on pipe at the most readable position.

I. Install remote-mounted pressure gages on panel.

J. Install valve and snubber in piping for each pressure gage for fluids (except steam).

K. Install valve and syphon fitting in piping for each pressure gage for steam.

L. Install flow indicators in piping systems in accessible positions for easy viewing.

M. Assemble and install connections, tubing, and accessories between flow-measuring elements and flowmeters according to manufacturer's written instructions.

N. Install flowmeter elements in accessible positions in piping systems.

O. Install differential-pressure-type flowmeter elements, with at least minimum straight lengths of pipe, upstream and downstream from element according to manufacturer's written instructions.

P. Install permanent indicators on walls or brackets in accessible and readable positions.

Q. Install connection fittings in accessible locations for attachment to portable indicators.

R. Mount thermal-energy meters on wall if accessible; if not, provide brackets to support meters.

S. Install thermometers in the following locations:

1. Inlet and outlet of each hydronic zone.

2. Inlet and outlet of each hydronic boiler.

3. Two inlets and two outlets of each chiller.

4. Inlet and outlet of each hydronic coil in air-handling units.

5. Two inlets and two outlets of each hydronic heat exchanger.

6. Inlet and outlet of each thermal-storage tank.

7. Outside-, return-, supply-, and mixed-air ducts.

8. <Insert location>.

T. Install pressure gages in the following locations:

1. Discharge of each pressure-reducing valve.

2. Inlet and outlet of each chiller chilled-water and condenser-water connection.

3. Suction and discharge of each pump.

4. <Insert location>.

3.2 CONNECTIONS

A. Install meters and gages adjacent to machines and equipment to allow service and maintenance of meters, gages, machines, and equipment.

B. Connect flowmeter-system elements to meters.

C. Connect flowmeter transmitters to meters.

D. Connect thermal-energy meter transmitters to meters.

3.3 ADJUSTING

A. After installation, calibrate meters according to manufacturer's written instructions.

B. Adjust faces of meters and gages to proper angle for best visibility.

3.4 THERMOMETER SCHEDULE

Retain this article if more than one type of thermometer is required; delete if all thermometers are the same type.

Retain and revise applicable thermometer applications. Coordinate with materials specified in Part 2.

Retain "one of" option in first paragraph below to allow Contractor to select thermometer materials from those retained.

A. Thermometers at inlet and outlet of each hydronic zone shall be[ one of] the following:

Retain one or both subparagraphs below. If retaining more than one type of thermometer, indicate location of each on Drawings.

1. [Liquid-filled] [Sealed], bimetallic-actuated type.

2. Industrial-style, liquid-in-glass type.

Retain "one of" option in first paragraph below to allow Contractor to select thermometer materials from those retained.

B. Thermometers at inlet and outlet of each hydronic boiler shall be[ one of] the following:

Retain one or both subparagraphs below. If retaining more than one type of thermometer, indicate location of each on Drawings.

1. [Liquid-filled] [Sealed], bimetallic-actuated type.

2. Industrial-style, liquid-in-glass type.

Retain "one of" option in first paragraph below to allow Contractor to select thermometer materials from those retained.

C. Thermometers at inlets and outlets of each chiller shall be[ one of] the following:

Retain one or both subparagraphs below. If retaining more than one type of thermometer, indicate location of each on Drawings.

1. [Liquid-filled] [Sealed], bimetallic-actuated type.

2. Industrial-style, liquid-in-glass type.

Retain "one of" option in first paragraph below to allow Contractor to select thermometer materials from those retained.

D. Thermometers at inlet and outlet of each hydronic coil in air-handling units and built-up central systems shall be[ one of] the following:

Retain one or both subparagraphs below. If retaining more than one type of thermometer, indicate location of each on Drawings.

1. [Liquid-filled] [Sealed], bimetallic-actuated type.

2. Industrial-style, liquid-in-glass type.

Retain "one of" option in first paragraph below to allow Contractor to select thermometer materials from those retained.

E. Thermometers at inlets and outlets of each hydronic heat exchanger shall be[ one of] the following:

Retain one or both subparagraphs below. If retaining more than one type of thermometer, indicate location of each on Drawings.

1. [Liquid-filled] [Sealed], bimetallic-actuated type.

2. Industrial-style, liquid-in-glass type.

Retain "one of" option in first paragraph below to allow Contractor to select thermometer materials from those retained.

F. Thermometers at inlet and outlet of each hydronic heat-recovery unit shall be[ one of] the following:

Retain one or both subparagraphs below. If retaining more than one type of thermometer, indicate location of each on Drawings.

1. [Liquid-filled] [Sealed], bimetallic-actuated type.

2. Industrial-style, liquid-in-glass type.

Retain "one of" option in first paragraph below to allow Contractor to select thermometer materials from those retained.

G. Thermometers at inlet and outlet of each thermal-storage tank shall be[ one of] the following:

Retain one or both subparagraphs below. If retaining more than one type of thermometer, indicate location of each on Drawings.

1. [Liquid-filled] [Sealed], bimetallic-actuated type.

2. Industrial-style, liquid-in-glass type.

Retain "one of" option in first paragraph below to allow Contractor to select thermometer materials from those retained.

H. Thermometers at outside-, return-, supply-, and mixed-air ducts shall be[ one of] the following:

Retain one or both subparagraphs below. If retaining more than one type of thermometer, indicate location of each on Drawings.

1. [Liquid-filled] [Sealed], bimetallic-actuated type.

2. Industrial-style, liquid-in-glass type.

Insert additional paragraphs for thermometer applications here.

I. Thermometer stems shall be of length to match thermowell insertion length.

3.5 THERMOMETER SCALE-RANGE SCHEDULE

The IP and SI temperature values for the scale ranges presented in this article are not mathematical, rounded, conversions from IP to SI; rather they are the temperature ranges within each specific unit of measure that are available from most manufacturers.

Retain the first option in each paragraph for thermometers with a single scale in either deg F or deg C; retain the second option for thermometers with dual scales.

Scale ranges vary among types of thermometers and among manufacturers. Retain a scale range that covers more than service-fluid temperature range. Exact ranges listed are not mandatory.

Retain one or more of first three paragraphs below. If retaining more than one scale range, indicate location of each on Drawings.

A. Scale Range for Chilled-Water Piping: [Minus 40 to plus 160 deg F (Minus 40 to plus 100 deg C)] [Minus 40 to plus 160 deg F and minus 40 to plus 100 deg C].

B. Scale Range for Chilled-Water Piping: [0 to 100 deg F (Minus 20 to plus 50 deg C)] [0 to 100 deg F and minus 20 to plus 50 deg C].

C. Scale Range for Chilled-Water Piping: [0 to 150 deg F (Minus 20 to plus 70 deg C)] [0 to 150 deg F and minus 20 to plus 70 deg C].

Retain one or more of first three paragraphs below. If retaining more than one scale range, indicate location of each on Drawings.

D. Scale Range for Condenser-Water Piping: [0 to 100 deg F (Minus 20 to plus 50 deg C)] [0 to 100 deg F and minus 20 to plus 50 deg C].

E. Scale Range for Condenser-Water Piping: [0 to 150 deg F (Minus 20 to plus 70 deg C)] [0 to 150 deg F and minus 20 to plus 70 deg C].

F. Scale Range for Condenser-Water Piping: [0 to 250 deg F (0 to 150 deg C)] [0 to 250 deg F and 0 to 150 deg C].

Retain one or more of first three paragraphs below. If retaining more than one scale range, indicate location of each on Drawings.

G. Scale Range for Heating, Hot-Water Piping: [0 to 250 deg F (0 to 150 deg C)] [0 to 250 deg F and 0 to 150 deg C].

H. Scale Range for Heating, Hot-Water Piping: [20 to 240 deg F (0 to 150 deg C)] [20 to 240 deg F and 0 to 150 deg C].

I. Scale Range for Heating, Hot-Water Piping: [50 to 400 deg F (0 to 200 deg C)] [50 to 400 deg F and 0 to 200 deg C].

Retain one or more of first two paragraphs below. If retaining more than one scale range, indicate location of each on Drawings.

J. Scale Range for Steam and Steam-Condensate Piping: [0 to 250 deg F (0 to 150 deg C)] [0 to 250 deg F and 0 to 150 deg C].

K. Scale Range for Steam and Steam-Condensate Piping: [20 to 240 deg F (0 to 150 deg C)] [20 to 240 deg F and 0 to 150 deg C].

Retain one or more of four paragraphs below. If retaining more than one scale range, indicate location of each on Drawings.

L. Scale Range for Air Ducts: [Minus 40 to plus 160 deg F (Minus 40 to plus 100 deg C)] [Minus 40 to plus 160 deg F and minus 40 to plus 100 deg C].

M. Scale Range for Air Ducts: [0 to 100 deg F (Minus 20 to plus 50 deg C)] [0 to 100 deg F and minus 20 to plus 50 deg C].

N. Scale Range for Air Ducts: [0 to 150 deg F (Minus 20 to plus 70 deg C)] [0 to 150 deg F and minus 20 to plus 70 deg C].

O. Scale Range for Air Ducts: [20 to 240 deg F (0 to 150 deg C)] [20 to 240 deg F and 0 to 150 deg C].

Insert additional paragraphs for thermometer scale ranges and applications here.

3.6 PRESSURE-GAGE SCHEDULE

Retain this article if more than one type of pressure gage is required; delete if all pressure gages are the same type.

Retain and revise applicable pressure gage applications. Coordinate with materials specified in Part 2.

Retain "one of" option in first paragraph below to allow Contractor to select pressure-gage materials from those retained.

A. Pressure gages at discharge of each pressure-reducing valve shall be[ one of] the following:

Retain one or both subparagraphs below. If retaining more than one type of pressure gage, indicate location of each on Drawings.

1. [Liquid-filled] [Sealed] [Open-front, pressure-relief] [Solid-front, pressure-relief] <Insert type>, [direct] [remote]-mounted, metal case.

2. [Sealed] <Insert type>, [direct] [remote]-mounted, plastic case.

Retain "one of" option in first paragraph below to allow Contractor to select pressure-gage materials from those retained.

B. Pressure gages at inlet and outlet of each chiller chilled-water and condenser-water connection shall be[ one of] the following:

Retain one or both subparagraphs below. If retaining more than one type of pressure gage, indicate location of each on Drawings.

1. [Liquid-filled] [Sealed] [Open-front, pressure-relief] [Solid-front, pressure-relief] <Insert type>, [direct] [remote]-mounted, metal case.

2. [Sealed] <Insert type>, [direct] [remote]-mounted, plastic case.

Retain "one of" option in paragraph below to allow Contractor to select pressure-gage materials from those retained.

C. Pressure gages at suction and discharge of each pump shall be[ one of] the following:

Retain one or both subparagraphs below. If retaining more than one type of pressure gage, indicate location of each on Drawings.

1. [Liquid-filled] [Sealed] [Open-front, pressure-relief] [Solid-front, pressure-relief] <Insert type>, [direct] [remote]-mounted, metal case.

2. [Sealed] <Insert type>, [direct] [remote]-mounted, plastic case.

Insert additional paragraphs for pressure-gage applications here.

3.7 PRESSURE-GAGE SCALE-RANGE SCHEDULE

The IP and SI pressure values for the scale ranges presented in this article are not mathematical, rounded, conversions from IP to SI; rather they are the pressure ranges within each specific unit of measure that are available from most manufacturers.

Retain the first option in each paragraph for pressure gages with a single scale in either psi or kPa; retain the second option for pressure gages with dual scales.

Scale ranges vary among types of pressure gages and among manufacturers. Retain a scale range that covers more than service-fluid pressure range. Exact ranges listed are not mandatory.

Retain one or more of first three paragraphs below. If retaining more than one scale range, indicate location of each on Drawings.

A. Scale Range for Chilled-Water Piping: [0 to 100 psi (0 to 600 kPa)] [0 to 100 psi and 0 to 600 kPa].

B. Scale Range for Chilled-Water Piping: [0 to 160 psi (0 to 1100 kPa)] [0 to 160 psi and 0 to 1100 kPa].

C. Scale Range for Chilled-Water Piping: [0 to 300 psi (0 to 2500 kPa)] [0 to 300 psi and 0 to 2500 kPa].

Retain one or more of first three paragraphs below. If retaining more than one scale range, indicate location of each on Drawings.

D. Scale Range for Condenser-Water Piping: [0 to 100 psi (0 to 600 kPa)] [0 to 100 psi and 0 to 600 kPa].

E. Scale Range for Condenser-Water Piping: [0 to 160 psi (0 to 1100 kPa)] [0 to 160 psi and 0 to 1100 kPa].

F. Scale Range for Condenser-Water Piping: [0 to 300 psi (0 to 2500 kPa)] [0 to 300 psi and 0 to 2500 kPa].

Retain one or more of first three paragraphs below. If retaining more than one scale range, indicate location of each on Drawings.

G. Scale Range for Heating, Hot-Water Piping: [0 to 100 psi (0 to 600 kPa)] [0 to 100 psi and 0 to 600 kPa].

H. Scale Range for Heating, Hot-Water Piping: [0 to 160 psi (0 to 1100 kPa)] [0 to 160 psi and 0 to 1100 kPa].

I. Scale Range for Heating, Hot-Water Piping: [0 to 300 psi (0 to 2500 kPa)] [0 to 300 psi and 0 to 2500 kPa].

Retain one or more of three paragraphs below. If retaining more than one scale range, indicate location of each on Drawings.

J. Scale Range for Steam Piping: [0 to 100 psi (0 to 600 kPa)] [0 to 100 psi and 0 to 600 kPa].

K. Scale Range for Steam Piping: [0 to 160 psi (0 to 1100 kPa)] [0 to 160 psi and 0 to 1100 kPa].

L. Scale Range for Steam Piping: [0 to 200 psi (0 to 1400 kPa)] [0 to 200 psi and 0 to 1400 kPa].

Insert additional paragraphs for pressure-gage scale ranges and applications here.

3.8 FLOWMETER SCHEDULE

Retain and revise applicable flowmeter applications. Coordinate with materials specified in Part 2.

A. Flowmeters for Chilled-Water Piping: [Pitot-tube] [Turbine] [Venturi] type.

B. Flowmeters for Condenser-Water Piping: [Pitot-tube] [Turbine] [Venturi] type.

C. Flowmeters for Heating, Hot-Water Piping: [Pitot-tube] [Turbine] [Venturi] type.

D. Flowmeters for Steam and Steam-Condensate Piping: [Turbine] [Venturi] type.

3.9 THERMAL-ENERGY METER SCHEDULE

A. Thermal-Energy Meters: Impeller-turbine type.

END OF SECTION 230519

	METERS AND GAGES FOR HVAC PIPING
	230519 - 1



