Copyright 2011 AIA
MasterSpec Professional
09/11

Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 230900 - INSTRUMENTATION AND CONTROL FOR HVAC
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. This Section includes control equipment for HVAC systems and components, including control components for terminal heating and cooling units not supplied with factory-wired controls.

B. See Section 230993 "Sequence of Operations for HVAC Controls" for requirements that relate to this Section.

1.2 ACTION SUBMITTALS

A. Product Data: For each control device indicated.

B. Shop Drawings:

1. Schematic flow diagrams.

2. Power, signal, and control wiring diagrams.

3. Details of control panel faces.

4. Damper schedule.

5. Valve schedule.

Retain two subparagraphs below for DDC systems.

6. DDC System Hardware: Wiring diagrams, schematic floor plans, and schematic control diagrams.

7. Control System Software: Schematic diagrams, written descriptions, and points list.

1.3 INFORMATIONAL SUBMITTALS

A. Field quality-control test reports.

1.4 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

B. Software and firmware operational documentation.

1.5 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

Edit this Article with other Part 2 articles in which manufacturers are named. See Section 016000 "Product Requirements" for an explanation of the terms "Available Manufacturers" and "Manufacturers" and the effect these terms have on "Comparable Product" and "Product Substitution" requirements.

A. In other Part 2 articles where titles below introduce lists, the following requirements apply to product selection:

1. Available Manufacturers: Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, manufacturers specified.

2. Manufacturers: Subject to compliance with requirements, provide products by one of the manufacturers specified.

2.2 CONTROL SYSTEM

Coordinate first paragraph and list below with Part 2 "Manufacturers" Article. Retain "Available" for nonproprietary and delete for semiproprietary specifications.

A. [Available ]Manufacturers:

1. Alerton Inc.

2. American Auto-Matrix.

3. Andover Controls Corporation.

4. Automated Logic Corporation.

5. Carel.

6. Delta Controls Inc.

7. EDA Controls Corp.

8. Electronic Systems USA, Inc.

9. Functional Devices Inc.

Retain first subparagraph below for electronic control systems only.

10. Heat-Timer Corporation.

11. Honeywell International Inc.; Home & Building Control.

12. Impact Energy Controls Corp.

13. Invensys Building Systems.

14. Johnson Controls, Inc.; Controls Group.

15. KMC Controls/Kreuter Manufacturing Company.

16. Luwa USA, Inc.; Textile Air Engineering.

17. McQuay International.

18. Siemens Building Technologies, Inc.

19. Solidyne Corp.

20. Staefa Control System Inc.; Siemens Building Technologies, Inc.

21. TAC Americas, INC.

22. TCS/Basys Controls.

23. tekmar Control Systems, Inc.

24. Teletrol Systems Incorporated.

25. Temco Controls Ltd. USA.

26. Tour & Andersson Control, Inc.

27. Trane; Worldwide Applied Systems Group.

28. Triangle MicroSystems, Inc.

29. Voltec, Inc.

30. <Insert manufacturer's name.>

B. Control system shall consist of sensors, indicators, actuators, final control elements, interface equipment, other apparatus, and accessories to control mechanical systems.

Retain paragraph below and delete paragraph above for distributed control systems.

C. Control system shall consist of sensors, indicators, actuators, final control elements, interface equipment, other apparatus, accessories, and software connected to distributed controllers operating in multiuser, multitasking environment on token-passing network and programmed to control mechanical systems. An operator workstation permits interface with the network via dynamic color graphics with each mechanical system, building floor plan, and control device depicted by point-and-click graphics.

2.3 DDC EQUIPMENT

A. Operator Workstation: PC-based microcomputer with minimum configuration as follows:

1. Motherboard: With 8 integrated USB 2.0 ports, integrated Intel Pro 10/100 (Ethernet), integrated audio, bios, and hardware monitoring.

2. Processor: [Intel Pentium 4] <Insert name>, <Insert clock speed> MHz.

3. Random-Access Memory: [512] <Insert number> MB.

4. Graphics: Video adapter, minimum [1280 x 1024] [1600 x 1200] <Insert value> pixels, [64] <Insert number>-MB video memory, with TV out.

5. Monitor: [17 inches (430 mm)] [19 inches (480 mm)] <Insert size>, LCD color.

6. Keyboard: QWERTY, 105 keys in ergonomic shape.

7. Floppy-Disk Drive: 1.44 MB.

8. Hard-Disk Drive: [80 GB] <Insert capacity>.

9. CD-ROM Read/Write Drive: [48x24x48] <Insert value>.

10. Mouse: Three button, optical.

11. Uninterruptible Power Supply: [2] <Insert capacity> kVa.

12. Operating System: [Microsoft Windows XP Professional] <Insert system name> with high-speed Internet access.

13. Printer: Color, ink-jet type as follows:

a. Print Head: [4800 x 1200] <Insert value> dpi optimized color resolution.

b. Paper Handling: Minimum of [100] <Insert number> sheets.

c. Print Speed: Minimum of [17] <Insert number> ppm in black and [12] <Insert number> ppm in color.

d. Application Software.

B. Control Units: Modular, comprising processor board with programmable, nonvolatile, random-access memory; local operator access and display panel; integral interface equipment; and backup power source.

1. Units monitor or control each I/O point; process information; execute commands from other control units, devices, and operator stations; and download from or upload to operator workstation.

2. Stand-alone mode control functions operate regardless of network status. Functions include the following:

a. Global communications.

b. Discrete/digital, analog, and pulse I/O.

c. Monitoring, controlling, or addressing data points.

d. Software applications, scheduling, and alarm processing.

e. Testing and developing control algorithms without disrupting field hardware and controlled environment.

C. Local Control Units: Modular, comprising processor board with electronically programmable, nonvolatile, read-only memory; and backup power source.

1. Units monitor or control each I/O point, process information, and download from or upload to operator workstation or diagnostic terminal unit.

2. Stand-alone mode control functions operate regardless of network status. Functions include the following:

a. Global communications.

b. Discrete/digital, analog, and pulse I/O.

c. Monitoring, controlling, or addressing data points.

3. Local operator interface provides for download from or upload to operator workstation.

D. I/O Interface: Hardwired inputs and outputs may tie into system through controllers. Protect points so that shorting will cause no damage to controllers.

1. Binary Inputs: Allow monitoring of on-off signals without external power.

2. Pulse Accumulation Inputs: Accept up to 10 pulses per second.

3. Analog Inputs: Allow monitoring of low-voltage (0- to 10-V dc), current (4 to 20 mA), or resistance signals.

4. Binary Outputs: Provide on-off or pulsed low-voltage signal, selectable for normally open or normally closed operation[ with three-position (on-off-auto) override switches and status lights].

5. Analog Outputs: Provide modulating signal, either low voltage (0- to 10-V dc) or current (4 to 20 mA)[ with status lights, two-position (auto-manual) switch, and manually adjustable potentiometer].

6. Tri-State Outputs: Provide two coordinated binary outputs for control of three-point, floating-type electronic actuators.

7. Universal I/Os: Provide software selectable binary or analog outputs.

E. Power Supplies: Transformers with Class 2 current-limiting type or overcurrent protection; limit connected loads to 80 percent of rated capacity. DC power supply shall match output current and voltage requirements and be full-wave rectifier type with the following:

1. Output ripple of 5.0 mV maximum peak to peak.

2. Combined 1 percent line and load regulation with 100-mic.sec. response time for 50 percent load changes.

3. Built-in overvoltage and overcurrent protection and be able to withstand 150 percent overload for at least 3 seconds without failure.

F. Power Line Filtering: Internal or external transient voltage and surge suppression for workstations or controllers with the following:

1. Minimum dielectric strength of 1000 V.

2. Maximum response time of 10 nanoseconds.

3. Minimum transverse-mode noise attenuation of 65 dB.

4. Minimum common-mode noise attenuation of 150 dB at 40 to 100 Hz.

2.4 UNITARY CONTROLLERS

A. Unitized, capable of stand-alone operation with sufficient memory to support its operating system, database, and programming requirements, and with sufficient I/O capacity for the application.

1. Configuration: Local keypad and display; diagnostic LEDs for power, communication, and processor; wiring termination to terminal strip or card connected with ribbon cable; memory with bios; and [72] <Insert number>-hour battery backup.

2. Operating System: Manage I/O communication to allow distributed controllers to share real and virtual object information and allow central monitoring and alarms. [Perform scheduling with real-time clock. ]Perform automatic system diagnostics; monitor system and report failures.

3. Enclosure: Dustproof rated for operation at 32 to 120 deg F (0 to 50 deg C).

2.5 ANALOG CONTROLLERS

A. Step Controllers: 6- or 10-stage type, with heavy-duty switching rated to handle loads and operated by electric motor.

B. Electric, Outdoor-Reset Controllers: Remote-bulb or bimetal rod-and-tube type, proportioning action with adjustable throttling range, adjustable set point, scale range minus 10 to plus 70 deg F (minus 23 to plus 21 deg C), and single- or double-pole contacts.

C. Electronic Controllers: Wheatstone-bridge-amplifier type, in steel enclosure with provision for remote-resistance readjustment. Identify adjustments on controllers, including proportional band and authority.

Retain subparagraph below if applicable.

1. Single controllers can be integral with control motor if provided with accessible control readjustment potentiometer.

Verify that fan-speed controller is compatible with fan motor.

D. Fan-Speed Controllers: Solid-state model providing field-adjustable proportional control of motor speed from maximum to minimum of 55 percent and on-off action below minimum fan speed. Controller shall briefly apply full voltage, when motor is started, to rapidly bring motor up to minimum speed. Equip with filtered circuit to eliminate radio interference.

2.6 TIME CLOCKS

This Article contains two examples of time clocks. Edit to suit Project.

Coordinate first paragraph and list below with Part 2 "Manufacturers" Article. Retain "Available" for nonproprietary and delete for semiproprietary specifications.

A. [Available ]Manufacturers:

1. ATC-Diversified Electronics.

2. Grasslin Controls Corporation.

3. Paragon Electric Co., Inc.

4. Precision Multiple Controls, Inc.

5. SSAC Inc.; ABB USA.

6. TCS/Basys Controls.

7. Theben AG - Lumilite Control Technology, Inc.

8. Time Mark Corporation.

9. <Insert manufacturer's name.>

B. Seven-day, programming-switch timer with synchronous-timing motor and seven-day dial; continuously charged, nickel-cadmium-battery-driven, eight-hour, power-failure carryover; multiple-switch trippers; minimum of two and maximum of eight signals per day with two normally open and two normally closed output contacts.

Programmable clock is available for applications requiring more than one time clock. Consider using Section 275313 "Clock Systems" as a source for time-programmed on-off commands.

C. Solid-state, programmable time control with [4] [8] <Insert number> separate programs each with up to 100 on-off operations; 1-second resolution; lithium battery backup; keyboard interface and manual override; individual on-off-auto switches for each program; 365-day calendar with 20 programmable holidays; choice of fail-safe operation for each program; system fault alarm; and communications package allowing networking of time controls and programming from PC.

2.7 ELECTRONIC SENSORS

A. Description: Vibration and corrosion resistant; for wall, immersion, or duct mounting as required.

B. Thermistor Temperature Sensors and Transmitters:

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article. Retain "Available" for nonproprietary and delete for semiproprietary specifications. If list does not include manufacturers of systems that make or market this equipment under their own name, those manufacturers' names may be added. List can be deleted if it is not important that specific manufacturers be named for this product.

1. [Available ]Manufacturers:

a. BEC Controls Corporation.

b. Ebtron, Inc.

c. Heat-Timer Corporation.

d. I.T.M. Instruments Inc.

e. MAMAC Systems, Inc.

f. RDF Corporation.

g. <Insert manufacturer's name.>

2. Accuracy: Plus or minus [0.5 deg F (0.3 deg C)] [0.36 deg F (0.2 deg C)] at calibration point.

3. Wire: Twisted, shielded-pair cable.

4. Insertion Elements in Ducts: Single point, [8 inches (200 mm)] [18 inches (460 mm)] long; use where not affected by temperature stratification or where ducts are smaller than 9 sq. ft. (0.84 sq. m).

5. Averaging Elements in Ducts: [36 inches (915 mm) long, flexible] [72 inches (1830 mm) long, flexible] [18 inches (460 mm) long, rigid]; use where prone to temperature stratification or where ducts are larger than 10 sq. ft. (1 sq. m).

6. Insertion Elements for Liquids: Brass or stainless-steel socket with minimum insertion length of 2-1/2 inches (64 mm).

7. Room Sensor Cover Construction: Manufacturer's standard locking covers.

First five subparagraphs below are optional features.

a. Set-Point Adjustment: [Concealed] [Exposed].

b. Set-Point Indication: [Concealed] [Keyed] [Exposed].

c. Thermometer: [Concealed] [Exposed] [Red-reading glass] [Spiral bimetal].

d. Color: <Insert color from manufacturer's full range.>

e. Orientation: [Vertical] [Horizontal].

8. Outside-Air Sensors: Watertight inlet fitting, shielded from direct sunlight.

9. Room Security Sensors: Stainless-steel cover plate with insulated back and security screws.

C. RTDs and Transmitters:

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article. Retain "Available" for nonproprietary and delete for semiproprietary specifications. If list does not include manufacturers of systems that make or market this equipment under their own name, those manufacturers' names may be added. List can be deleted if it is not important that specific manufacturers be named for this product.

1. [Available ]Manufacturers:

a. BEC Controls Corporation.

b. MAMAC Systems, Inc.

c. RDF Corporation.

d. <Insert manufacturer's name.>

2. Accuracy: Plus or minus 0.2 percent at calibration point.

3. Wire: Twisted, shielded-pair cable.

4. Insertion Elements in Ducts: Single point, [8 inches (200 mm)] [18 inches (460 mm)] long; use where not affected by temperature stratification or where ducts are smaller than 9 sq. ft. (0.84 sq. m).

5. Averaging Elements in Ducts: [18 inches (460 mm) long, rigid] [24 inches (610 mm) long, rigid] [48 inches (1200 mm) long, rigid] [24 feet (7.3 m) long, flexible]; use where prone to temperature stratification or where ducts are larger than 9 sq. ft. (0.84 sq. m); length as required.

6. Insertion Elements for Liquids: Brass socket with minimum insertion length of 2-1/2 inches (64 mm).

7. Room Sensor Cover Construction: Manufacturer's standard locking covers.

First five subparagraphs below are optional features.

a. Set-Point Adjustment: [Concealed] [Exposed].

b. Set-Point Indication: [Concealed] [Keyed] [Exposed].

c. Thermometer: [Concealed] [Exposed] [Red-reading glass] [Spiral bimetal].

d. Color: <Insert color from manufacturer's full range.>

e. Orientation: [Vertical] [Horizontal].

8. Outside-Air Sensors: Watertight inlet fitting, shielded from direct sunlight.

9. Room Security Sensors: Stainless-steel cover plate with insulated back and security screws.

D. Humidity Sensors: Bulk polymer sensor element.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article. Retain "Available" for nonproprietary and delete for semiproprietary specifications. If list does not include manufacturers of systems that make or market this equipment under their own name, those manufacturers' names may be added. List can be deleted if it is not important that specific manufacturers be named for this product.

1. [Available ]Manufacturers:

a. BEC Controls Corporation.

b. General Eastern Instruments.

c. MAMAC Systems, Inc.

d. ROTRONIC Instrument Corp.

e. TCS/Basys Controls.

f. Vaisala.

g. <Insert manufacturer's name.>

2. Accuracy: [5] [2] percent full range with linear output.

3. Room Sensor Range: 20 to 80 percent relative humidity.

4. Room Sensor Cover Construction: Manufacturer's standard locking covers.

First five subparagraphs below are optional features.

a. Set-Point Adjustment: [Concealed] [Exposed].

b. Set-Point Indication: [Concealed] [Keyed] [Exposed].

c. Thermometer: [Concealed] [Exposed] [Red-reading glass] [Spiral bimetal].

d. Color: <Insert color from manufacturer's full range.>

e. Orientation: [Vertical] [Horizontal].

5. Duct Sensor: 20 to 80 percent relative humidity range with element guard and mounting plate.

6. Outside-Air Sensor: 20 to 80 percent relative humidity range with mounting enclosure, suitable for operation at outdoor temperatures of [32 to 120 deg F (0 to 50 deg C)] [minus 22 to plus 185 deg F (minus 30 to plus 85 deg C)] [minus 40 to plus 170 deg F (minus 40 to plus 76 deg C)].

7. Duct and Sensors: With element guard and mounting plate, range of 0 to 100 percent relative humidity.

E. Pressure Transmitters/Transducers:

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article. Retain "Available" for nonproprietary and delete for semiproprietary specifications. If list does not include manufacturers of systems that make or market this equipment under their own name, those manufacturers' names may be added. List can be deleted if it is not important that specific manufacturers be named for this product.

1. [Available ]Manufacturers:

a. BEC Controls Corporation.

b. General Eastern Instruments.

c. MAMAC Systems, Inc.

d. ROTRONIC Instrument Corp.

e. TCS/Basys Controls.

f. Vaisala.

g. <Insert manufacturer's name.>

2. Static-Pressure Transmitter: Nondirectional sensor with suitable range for expected input, and temperature compensated.

a. Accuracy: 2 percent of full scale with repeatability of 0.5 percent.

b. Output: 4 to 20 mA.

c. Building Static-Pressure Range: 0- to 0.25-inch wg (0 to 62 Pa).

d. Duct Static-Pressure Range: 0- to 5-inch wg (0 to 1240 Pa).

3. Water Pressure Transducers: Stainless-steel diaphragm construction, suitable for service; minimum 150-psig (1034-kPa) operating pressure; linear output 4 to 20 mA.

4. Water Differential-Pressure Transducers: Stainless-steel diaphragm construction, suitable for service; minimum 150-psig (1034-kPa) operating pressure and tested to 300-psig (2070-kPa); linear output 4 to 20 mA.

5. Differential-Pressure Switch (Air or Water): Snap acting, with pilot-duty rating and with suitable scale range and differential.

6. Pressure Transmitters: Direct acting for gas or liquid service; range suitable for system; linear output 4 to 20 mA.

F. Room Sensor Cover Construction: Manufacturer's standard locking covers.

Subparagraphs below are optional features.

1. Set-Point Adjustment: [Concealed] [Exposed].

2. Set-Point Indication: [Concealed] [Keyed] [Exposed].

3. Thermometer: [Concealed] [Exposed] [Red-reading glass] [Spiral bimetal].

4. Color: <Insert color from manufacturer's full range.>

5. Orientation: [Vertical] [Horizontal].

G. Room sensor accessories include the following:

Select accessories from subparagraphs below or insert others if required. Possibly insert a listing of areas (by categories) to receive accessories.

1. Insulating Bases: For sensors located on exterior walls.

2. Guards: [Locking; heavy-duty, transparent plastic; mounted on separate base] [Metal wire, tamperproof] [Locking, solid metal, ventilated].

3. Adjusting Key: As required for calibration and cover screws.

2.8 STATUS SENSORS

A. Status Inputs for Fans: Differential-pressure switch with pilot-duty rating and with adjustable range of 0- to 5-inch wg (0 to 1240 Pa).

B. Status Inputs for Pumps: Differential-pressure switch with pilot-duty rating and with adjustable pressure-differential range of 8 to 60 psig (55 to 414 kPa), piped across pump.

C. Status Inputs for Electric Motors: Comply with ISA 50.00.01, current-sensing fixed- or split-core transformers with self-powered transmitter, adjustable and suitable for 175 percent of rated motor current.

D. Voltage Transmitter (100- to 600-V ac): Comply with ISA 50.00.01, single-loop, self-powered transmitter, adjustable, with suitable range and 1 percent full-scale accuracy.

E. Power Monitor: 3-phase type with disconnect/shorting switch assembly, listed voltage and current transformers, with pulse kilowatt hour output and 4- to 20-mA kW output, with maximum 2 percent error at 1.0 power factor and 2.5 percent error at 0.5 power factor.

F. Current Switches: Self-powered, solid-state with adjustable trip current, selected to match current and system output requirements.

G. Electronic Valve/Damper Position Indicator: Visual scale indicating percent of travel and 2- to 10-V dc, feedback signal.

H. Water-Flow Switches: Bellows-actuated mercury or snap-acting type with pilot-duty rating, stainless-steel or bronze paddle, with appropriate range and differential adjustment, in NEMA 250, Type 1 enclosure.

Coordinate subparagraph and list below with Part 2 "Manufacturers" Article. Retain "Available" for nonproprietary and delete for semiproprietary specifications. If list does not include manufacturers of systems that make or market this equipment under their own name, those manufacturers' names may be added. List can be deleted if it is not important that specific manufacturers be named for this product.

1. [Available ]Manufacturers:

a. BEC Controls Corporation.

b. I.T.M. Instruments Inc.

c. <Insert manufacturer's name.>

2.9 GAS DETECTION EQUIPMENT

Coordinate first paragraph and list below with Part 2 "Manufacturers" Article. Retain "Available" for nonproprietary and delete for semiproprietary specifications.

A. [Available ]Manufacturers:

1. B. W. Technologies.

2. CEA Instruments, Inc.

3. Ebtron, Inc.

4. Gems Sensors Inc.

5. Greystone Energy Systems Inc.

6. Honeywell International Inc.; Home & Building Control.

7. INTEC Controls, Inc.

8. I.T.M. Instruments Inc.

9. MSA Canada Inc.

10. QEL/Quatrosense Environmental Limited.

11. Sauter Controls Corporation.

12. Sensidyne, Inc.

13. TSI Incorporated.

14. Vaisala.

15. Vulcain Inc.

16. <Insert manufacturer's name.>

B. Carbon Monoxide Detectors: Single or multichannel, dual-level detectors using solid-state plug-in sensors with a 3-year minimum life; suitable over a temperature range of 32 to 104 deg F (0 to 40 deg C); with 2 factory-calibrated alarm levels at [50 and 100] [35 and 200] ppm.

C. Carbon Dioxide Sensor and Transmitter: Single detectors using solid-state infrared sensors; suitable over a temperature range of 23 to 130 deg F (minus 5 to plus 55 deg C) and calibrated for 0 to 2 percent, with continuous or averaged reading, 4- to 20-mA output;, for wall mounting.

D. Occupancy Sensor: Passive infrared, with time delay, daylight sensor lockout, sensitivity control, and 180-degree field of view with vertical sensing adjustment; for flush mounting.

2.10 THERMOSTATS

Coordinate first paragraph and list below with Part 2 "Manufacturers" Article. Retain "Available" for nonproprietary and delete for semiproprietary specifications. If list does not include manufacturers of systems that make or market this equipment under their own name, those manufacturers' names may be added. List can be deleted if it is not important that specific manufacturers be named for this product.

A. [Available ]Manufacturers:

1. Erie Controls.

2. Danfoss Inc.; Air-Conditioning and Refrigeration Div.

3. Heat-Timer Corporation.

4. Sauter Controls Corporation.

5. tekmar Control Systems, Inc.

6. Theben AG - Lumilite Control Technology, Inc.

7. <Insert manufacturer's name.>

B. Electric, solid-state, microcomputer-based room thermostat with remote sensor.

1. Automatic switching from heating to cooling.

2. Preferential rate control to minimize overshoot and deviation from set point.

3. Set up for four separate temperatures per day.

4. Instant override of set point for continuous or timed period from 1 hour to 31 days.

5. Short-cycle protection.

6. Programming based on [weekday, Saturday, and Sunday] [every day of week].

7. Selection features include degree F or degree C display, 12- or 24-hour clock, keyboard disable, remote sensor, and fan on-auto.

8. Battery replacement without program loss.

9. Thermostat display features include the following:

a. Time of day.

b. Actual room temperature.

c. Programmed temperature.

d. Programmed time.

e. Duration of timed override.

f. Day of week.

g. System mode indications include "heating," "off," "fan auto," and "fan on."

C. Low-Voltage, On-Off Thermostats: NEMA DC 3, 24-V, bimetal-operated, mercury-switch type, with adjustable or fixed anticipation heater, concealed set-point adjustment, 55 to 85 deg F (13 to 30 deg C) set-point range, and 2 deg F (1 deg C) maximum differential.

D. Line-Voltage, On-Off Thermostats: Bimetal-actuated, open contact or bellows-actuated, enclosed, snap-switch or equivalent solid-state type, with heat anticipator; listed for electrical rating; with concealed set-point adjustment, 55 to 85 deg F (13 to 30 deg C) set-point range, and 2 deg F (1 deg C) maximum differential.

1. Electric Heating Thermostats: Equip with off position on dial wired to break ungrounded conductors.

2. Selector Switch: Integral, manual on-off-auto.

E. Remote-Bulb Thermostats: On-off or modulating type, liquid filled to compensate for changes in ambient temperature; with copper capillary and bulb, unless otherwise indicated.

1. Bulbs in water lines with separate wells of same material as bulb.

2. Bulbs in air ducts with flanges and shields.

3. Averaging Elements: Copper tubing with either single- or multiple-unit elements, extended to cover full width of duct or unit; adequately supported.

4. Scale settings and differential settings are clearly visible and adjustable from front of instrument.

5. On-Off Thermostat: With precision snap switches and with electrical ratings required by application.

6. Modulating Thermostats: Construct so complete potentiometer coil and wiper assembly is removable for inspection or replacement without disturbing calibration of instrument.

Coordinate first paragraph below with latest edition of NFPA 90A.

F. Fire-Protection Thermostats: Listed and labeled by an NRTL acceptable to authorities having jurisdiction; with fixed or adjustable settings to operate at not less than 75 deg F (24 deg C) above normal maximum operating temperature, and the following:

1. Reset: Manual.

Retain subparagraph above or below.

2. Reset: Automatic, with control circuit arranged to require manual reset at central control panel; with pilot light and reset switch on panel labeled to indicate operation.

G. Room Thermostat Cover Construction: Manufacturer's standard locking covers.

Subparagraphs below are optional features.

1. Set-Point Adjustment: [Concealed] [Exposed].

2. Set-Point Indication: [Concealed] [Keyed] [Exposed].

3. Thermometer: [Concealed] [Exposed] [Red-reading glass] [Spiral bimetal].

4. Color: <Insert color from manufacturer's full range.>

5. Orientation: [Vertical] [Horizontal].

H. Room thermostat accessories include the following:

Select accessories from subparagraphs below or insert others if required. Possibly insert a listing of areas (by categories) to receive accessories.

1. Insulating Bases: For thermostats located on exterior walls.

2. Thermostat Guards: [Locking; heavy-duty, transparent plastic; mounted on separate base] [Metal wire, tamperproof] [Locking, solid metal, ventilated].

3. Adjusting Key: As required for calibration and cover screws.

4. Set-Point Adjustment: 1/2-inch- (13-mm-) diameter, adjustment knob.

I. Immersion Thermostat: Remote-bulb or bimetal rod-and-tube type, proportioning action with adjustable throttling range and adjustable set point.

J. Airstream Thermostats: Two-pipe, fully proportional, single-temperature type; with adjustable set point in middle of range, adjustable throttling range, plug-in test fitting or permanent pressure gage, remote bulb, bimetal rod and tube, or averaging element.

K. Electric, Low-Limit Duct Thermostat: Snap-acting, single-pole, single-throw, manual- [or automatic- ]reset switch that trips if temperature sensed across any 12 inches (300 mm) of bulb length is equal to or below set point.

1. Bulb Length: Minimum 20 feet (6 m).

2. Quantity: One thermostat for every 20 sq. ft. (2 sq. m) of coil surface.

L. Electric, High-Limit Duct Thermostat: Snap-acting, single-pole, single-throw, manual- [or automatic- ]reset switch that trips if temperature sensed across any 12 inches (300 mm) of bulb length is equal to or above set point.

1. Bulb Length: Minimum 20 feet (6 m).

2. Quantity: One thermostat for every 20 sq. ft. (2 sq. m) of coil surface.

M. Heating/Cooling Valve-Top Thermostats: Proportional acting for proportional flow, with molded-rubber diaphragm, remote-bulb liquid-filled element, direct and reverse acting at minimum shutoff pressure of 25 psig (172 kPa), and cast housing with position indicator and adjusting knob.

2.11 HUMIDISTATS

Coordinate first paragraph and list below with Part 2 "Manufacturers" Article. Retain "Available" for nonproprietary and delete for semiproprietary specifications. If list does not include manufacturers of systems that make or market this equipment under their own name, those manufacturers' names may be added. List can be deleted if it is not important that specific manufacturers be named for this product.

A. [Available ]Manufacturers:

1. MAMAC Systems, Inc.

2. ROTRONIC Instrument Corp.

3. <Insert manufacturer's name.>

B. Duct-Mounting Humidistats: Electric insertion, 2-position type with adjustable, 2 percent throttling range, 20 to 80 percent operating range, and single- or double-pole contacts.

2.12 ACTUATORS

A. Electric Motors: Size to operate with sufficient reserve power to provide smooth modulating action or two-position action.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Section 230513 "Common Motor Requirements for HVAC Equipment." If different characteristics are required, insert additional subparagraphs below to suit Project.

1. Comply with requirements in Section 230513 "Common Motor Requirements for HVAC Equipment."

2. Permanent Split-Capacitor or Shaded-Pole Type: Gear trains completely oil immersed and sealed. Equip spring-return motors with integral spiral-spring mechanism in housings designed for easy removal for service or adjustment of limit switches, auxiliary switches, or feedback potentiometer.

3. Nonspring-Return Motors for Valves Larger Than NPS 2-1/2 (DN 65): Size for running torque of 150 in. x lbf (16.9 N x m) and breakaway torque of 300 in. x lbf (33.9 N x m).

4. Spring-Return Motors for Valves Larger Than NPS 2-1/2 (DN 65): Size for running and breakaway torque of 150 in. x lbf (16.9 N x m).

5. Nonspring-Return Motors for Dampers Larger Than 25 Sq. Ft. (2.3 sq. m): Size for running torque of 150 in. x lbf (16.9 N x m) and breakaway torque of 300 in. x lbf (33.9 N x m).

6. Spring-Return Motors for Dampers Larger Than 25 Sq. Ft. (2.3 sq. m): Size for running and breakaway torque of 150 in. x lbf (16.9 N x m).

B. Electronic Actuators: Direct-coupled type designed for minimum 60,000 full-stroke cycles at rated torque.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article. Retain "Available" for nonproprietary and delete for semiproprietary specifications. If list does not include manufacturers of systems that make or market this equipment under their own name, those manufacturers' names may be added. List can be deleted if it is not important that specific manufacturers be named for this product.

1. [Available ]Manufacturers:

a. Belimo Aircontrols (USA), Inc.

b. <Insert manufacturer's name.>

2. Valves: Size for torque required for valve close off at maximum pump differential pressure.

3. Dampers: Size for running torque calculated as follows:

a. Parallel-Blade Damper with Edge Seals: 7 inch-lb/sq. ft. (86.8 kg-cm/sq. m) of damper.

b. Opposed-Blade Damper with Edge Seals: 5 inch-lb/sq. ft. (62 kg-cm/sq. m) of damper.

c. Parallel-Blade Damper without Edge Seals: 4 inch-lb/sq. ft (49.6 kg-cm/sq. m) of damper.

d. Opposed-Blade Damper without Edge Seals: 3 inch-lb/sq. ft. (37.2 kg-cm/sq. m) of damper.

e. Dampers with 2- to 3-Inch wg (500 to 750 Pa) of Pressure Drop or Face Velocities of 1000 to 2500 fpm (5 to 13 m/s): Increase running torque by 1.5.

f. Dampers with 3- to 4-Inch wg (750 to 1000 Pa) of Pressure Drop or Face Velocities of 2500 to 3000 fpm (13 to 15 m/s): Increase running torque by 2.0.

4. Coupling: V-bolt and V-shaped, toothed cradle.

5. Overload Protection: Electronic overload or digital rotation-sensing circuitry.

6. Fail-Safe Operation: Mechanical, spring-return mechanism. Provide external, manual gear release on nonspring-return actuators.

7. Power Requirements (Two-Position Spring Return): [24] [120] [230]-V ac.

8. Power Requirements (Modulating): Maximum 10 VA at 24-V ac or 8 W at 24-V dc.

9. Proportional Signal: 2- to 10-V dc or 4 to 20 mA, and 2- to 10-V dc position feedback signal.

10. Temperature Rating: [Minus 22 to plus 122 deg F (Minus 30 to plus 50 deg C)] [40 to 104 deg F (5 to 40 deg C)].

11. Temperature Rating (Smoke Dampers): Minus 22 to plus 250 deg F (Minus 30 to plus 121 deg C).

12. Run Time: [12 seconds open, 5 seconds closed] [30 seconds] [60 seconds] [120 seconds].

2.13 CONTROL VALVES

Coordinate first paragraph and list below with Part 2 "Manufacturers" Article. Retain "Available" for nonproprietary and delete for semiproprietary specifications. If list does not include manufacturers of systems that make or market this equipment under their own name, those manufacturers' names may be added. List can be deleted if it is not important that specific manufacturers be named for this product.

A. [Available ]Manufacturers:

1. Danfoss Inc.; Air Conditioning & Refrigeration Div.

2. Erie Controls.

3. Hayward Industrial Products, Inc.

4. Magnatrol Valve Corporation.

5. Neles-Jamesbury.

6. Parker Hannifin Corporation; Skinner Valve Division.

7. Pneuline Controls.

8. Sauter Controls Corporation.

9. <Insert manufacturer's name.>

B. Control Valves: Factory fabricated, of type, body material, and pressure class based on maximum pressure and temperature rating of piping system, unless otherwise indicated.

C. Hydronic system globe valves shall have the following characteristics:

1. NPS 2 (DN 50) and Smaller: Class [125] [250] bronze body, bronze trim, rising stem, renewable composition disc, and screwed ends with backseating capacity repackable under pressure.

2. NPS 2-1/2 (DN 65) and Larger: Class 125 iron body, bronze trim, rising stem, plug-type disc, flanged ends, and renewable seat and disc.

3. Internal Construction: Replaceable plugs and stainless-steel or brass seats.

Retain one or both subparagraphs below.

a. Single-Seated Valves: Cage trim provides seating and guiding surfaces for plug on top and bottom.

b. Double-Seated Valves: Balanced plug; cage trim provides seating and guiding surfaces for plugs on top and bottom.

Maximum pressure drop of up to 5 psig (35 kPa) is usually acceptable. Show pressure drop on Drawings where critical.

4. Sizing: [3-psig (21-kPa)] [5-psig (35-kPa)] <Insert value> maximum pressure drop at design flow rate or the following:

a. Two Position: Line size.

b. Two-Way Modulating: Either the value specified above or twice the load pressure drop, whichever is more.

c. Three-Way Modulating: Twice the load pressure drop, but not more than value specified above.

5. Flow Characteristics: Two-way valves shall have equal percentage characteristics; three-way valves shall have linear characteristics.

6. Close-Off (Differential) Pressure Rating: Combination of actuator and trim shall provide minimum close-off pressure rating of 150 percent of total system (pump) head for two-way valves and 100 percent of pressure differential across valve or 100 percent of total system (pump) head.

Butterfly valves in paragraph below can also be rated up to 250 deg F (121 deg C).

D. Butterfly Valves: 200-psig (1380-kPa), 150-psig (1034-kPa) maximum pressure differential, ASTM A 126 cast-iron or ASTM A 536 ductile-iron body and bonnet, extended neck, stainless-steel stem, field-replaceable EPDM or Buna N sleeve and stem seals.

1. Body Style: [Wafer] [Lug] [Grooved].

2. Disc Type: [Nickel-plated ductile iron] [Aluminum bronze] [Elastomer-coated ductile iron] [Epoxy-coated ductile iron].

3. Sizing: 1-psig (7-kPa) maximum pressure drop at design flow rate.

Coordinate number of ports for terminal unit control valves in first paragraph below with Drawings.

E. Terminal Unit Control Valves: Bronze body, bronze trim, two or three ports as indicated, replaceable plugs and seats, and union and threaded ends.

1. Rating: Class 125 for service at 125 psig (860 kPa) and 250 deg F (121 deg C) operating conditions.

2. Sizing: 3-psig (21-kPa) maximum pressure drop at design flow rate, to close against pump shutoff head.

3. Flow Characteristics: Two-way valves shall have equal percentage characteristics; three-way valves shall have linear characteristics.

F. Self-Contained Control Valves: Bronze body, bronze trim, two or three ports as indicated, replaceable plugs and seats, and union and threaded ends.

1. Rating: Class 125 for service at 125 psig (860 kPa) and 250 deg F (121 deg C) operating conditions.

2. Thermostatic Operator: [Wax] [Liquid]-filled [integral] [remote] sensor with [integral] [remote] adjustable dial.

2.14 DAMPERS

Coordinate first paragraph and list below with Part 2 "Manufacturers" Article. Retain "Available" for nonproprietary and delete for semiproprietary specifications. If list does not include manufacturers of systems that make or market this equipment under their own name, those manufacturers' names may be added. List can be deleted if it is not important that specific manufacturers be named for this product.

A. [Available ]Manufacturers:

1. Air Balance Inc.

2. Don Park Inc.; Autodamp Div.

3. TAMCO (T. A. Morrison & Co. Inc.).

4. United Enertech Corp.

5. Vent Products Company, Inc.

6. <Insert manufacturer's name.>

B. Dampers: AMCA-rated, [parallel] [opposed]-blade design; 0.108-inch- (2.8-mm-) minimum thick, galvanized-steel or 0.125-inch- (3.2-mm-) minimum thick, extruded-aluminum frames with holes for duct mounting; damper blades shall not be less than 0.064-inch- (1.6-mm-) thick galvanized steel with maximum blade width of 8 inches (200 mm) and length of 48 inches (1220 mm).

1. Secure blades to 1/2-inch- (13-mm-) diameter, zinc-plated axles using zinc-plated hardware, with [oil-impregnated sintered bronze] [nylon] blade bearings, blade-linkage hardware of zinc-plated steel and brass, ends sealed against spring-stainless-steel blade bearings, and thrust bearings at each end of every blade.

2. Operating Temperature Range: From minus 40 to plus 200 deg F (minus 40 to plus 93 deg C).

3. Edge Seals, Standard Pressure Applications: Closed-cell neoprene.

Retain subparagraph above or below.

4. Edge Seals, Low-Leakage Applications: Use inflatable blade edging or replaceable rubber blade seals and spring-loaded stainless-steel side seals, rated for leakage at less than 10 cfm per sq. ft. (50 L/s per sq. m) of damper area, at differential pressure of 4-inch wg (1000 Pa) when damper is held by torque of 50 in. x lbf (5.6 N x m); when tested according to AMCA 500D.

2.15 CONTROL CABLE

A. Electronic and fiber-optic cables for control wiring are specified in Section 271500 "Communications Horizontal Cabling."

PART 3 -  EXECUTION

3.1 INSTALLATION

Verify mounting heights in first paragraph below with authorities having jurisdiction to comply with requirements of the Americans with Disabilities Act.

A. Verify location of thermostats, humidistats, and other exposed control sensors with Drawings and room details before installation. Install devices [48 inches (1220 mm)] [60 inches (1530 mm)] <Insert dimension> above the floor.

1. Install averaging elements in ducts and plenums in crossing or zigzag pattern.

B. Install guards on thermostats in the following locations:

Expand list of locations below or clearly indicate on Drawings.

1. Entrances.

2. Public areas.

3. Where indicated.

C. Install automatic dampers according to Section 233300 "Air Duct Accessories."

D. Install damper motors on outside of duct in warm areas, not in locations exposed to outdoor temperatures.

E. Install labels and nameplates to identify control components according to Section 230553 "Identification for HVAC Piping and Equipment."

F. Install hydronic instrument wells, valves, and other accessories according to Section 232116 "Hydronic Piping Specialties."Section 15179 "Hydronic Piping Specialties."

G. Install refrigerant instrument wells, valves, and other accessories according to Section 232300 "Refrigerant Piping."

H. Install duct volume-control dampers according to Section 233113 "Metal Ducts" and Section 233116 "Nonmetal Ducts."

I. Install electronic and fiber-optic cables according to Section 271500 "Communications Horizontal Cabling."

3.2 ELECTRICAL WIRING AND CONNECTION INSTALLATION

A. Install raceways, boxes, and cabinets according to Section 260533 "Raceways and Boxes for Electrical Systems."

B. Install building wire and cable according to Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

C. Install signal and communication cable according to Section 271500 "Communications Horizontal Cabling."

1. Conceal cable, except in mechanical rooms and areas where other conduit and piping are exposed.

2. Install exposed cable in raceway.

3. Install concealed cable in raceway.

4. Bundle and harness multiconductor instrument cable in place of single cables where several cables follow a common path.

5. Fasten flexible conductors, bridging cabinets and doors, along hinge side; protect against abrasion. Tie and support conductors.

6. Number-code or color-code conductors for future identification and service of control system, except local individual room control cables.

7. Install wire and cable with sufficient slack and flexible connections to allow for vibration of piping and equipment.

D. Connect manual-reset limit controls independent of manual-control switch positions. Automatic duct heater resets may be connected in interlock circuit of power controllers.

E. Connect hand-off-auto selector switches to override automatic interlock controls when switch is in hand position.

3.3 FIELD QUALITY CONTROL

Retain first paragraph below to require a factory-authorized service representative to perform, or assist Contractor with, field inspections, tests, and adjustments. Retain one of two options to suit Project; delete both to require only an inspection before field testing.

A. Manufacturer's Field Service: Engage a factory-authorized service representative to inspect[, test, and adjust] field-assembled components and equipment installation, including connections[, and to assist in field testing]. Report results in writing.

B. Perform the following field tests and inspections and prepare test reports:

1. Operational Test: After electrical circuitry has been energized, start units to confirm proper unit operation. Remove and replace malfunctioning units and retest.

2. Test and adjust controls and safeties.

3. Test calibration of controllers by disconnecting input sensors and stimulating operation with compatible signal generator.

4. Test each point through its full operating range to verify that safety and operating control set points are as required.

5. Test each control loop to verify stable mode of operation and compliance with sequence of operation. Adjust PID actions.

6. Test each system for compliance with sequence of operation.

7. Test software and hardware interlocks.

C. DDC Verification:

1. Verify that instruments are installed before calibration, testing, and loop or leak checks.

2. Check instruments for proper location and accessibility.

3. Check instrument installation for direction of flow, elevation, orientation, insertion depth, and other applicable considerations.

4. Check instrument tubing for proper fittings, slope, material, and support.

5. Check pressure instruments, piping slope, installation of valve manifold, and self-contained pressure regulators.

6. Check temperature instruments and material and length of sensing elements.

7. Check control valves. Verify that they are in correct direction.

8. Check air-operated dampers. Verify that pressure gages are provided and that proper blade alignment, either parallel or opposed, has been provided.

9. Check DDC system as follows:

a. Verify that DDC controller power supply is from emergency power supply, if applicable.

b. Verify that wires at control panels are tagged with their service designation and approved tagging system.

c. Verify that spare I/O capacity has been provided.

d. Verify that DDC controllers are protected from power supply surges.

D. Replace damaged or malfunctioning controls and equipment and repeat testing procedures.

3.4 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain HVAC instrumentation and controls. Refer to Section 017900 "Demonstration and Training."

END OF SECTION 230900

	INSTRUMENTATION AND CONTROL FOR HVAC
	230900 - 1



