Copyright 2011 AIA
MasterSpec Professional
03/11

Copyright 2011 by The American Institute of Architects (AIA)
Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA
SECTION 231113 - FACILITY FUEL-OIL PIPING
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.
This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.
PART 1 -  GENERAL

1.1 SUMMARY

A. This Section includes [fuel-oil] [fuel-oil and diesel-fuel-oil] [diesel-fuel-oil] distribution systems Section and the following:

1. Pipes, tubes, and fittings.

2. Piping and tubing joining materials.

3. Piping specialties.

4. Valves.

5. FRP fuel-oil USTs.

6. Fuel-oil UST accessories.

7. Fuel-oil storage tank piping specialties.

8. Fuel-transfer pumps.

9. Leak-detection and monitoring system.

10. Concrete bases.

1.2 PERFORMANCE REQUIREMENTS

A. Maximum Operating-Pressure Ratings: 3-psig (21-kPa) fuel-oil supply pressure at oil-fired appliances.

Retain paragraph below if Contractor is required to assume responsibility for design.
B. Delegated Design: Design restraint and anchors for fuel-oil piping and equipment, including comprehensive engineering analysis by a qualified professional engineer, using performance requirements and design criteria indicated.

1.3 ACTION SUBMITTALS

A. Product Data: For each type of product indicated.

B. Shop Drawings: For facility fuel-oil piping layout. Include plans, piping layout and elevations, sections, and details for fabrication of pipe anchors, hangers, supports for multiple pipes, alignment guides, expansion joints and loops, and attachments of the same to building structure. Detail location of anchors, alignment guides, and expansion joints and loops.

Paragraph below is defined in SECTION 013300 "Submittal Procedures" as a "Delegated-Design Submittal." Retain if Work of this Section is required to withstand specific design loads and design responsibilities have been delegated to Contractor or if structural data are required as another way to verify compliance with performance requirements. Professional engineer qualifications are specified in Section 014000 "Quality Requirements."
C. Delegated-Design Submittal: For fuel-oil piping and equipment indicated to comply with performance requirements and design criteria, including analysis data signed and sealed by the qualified professional engineer responsible for their preparation.

1. Detail fabrication and assembly of anchors and seismic restraints.

2. Design Calculations: Calculate requirements for selecting seismic restraints.

3. Detail fabrication and assembly of pipe anchors, hangers, supports for multiple pipes, and attachments of the same to building structure.

1.4 INFORMATIONAL SUBMITTALS

Retain first paragraph below if retaining procedures for brazing certification in "Quality Assurance" Article.
A. Brazing certificates.

B. Welding certificates.

C. Field quality-control reports.

D. Warranty: Sample of special warranty.

1.5 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

1.6 QUALITY ASSURANCE

Retain "Brazing certificates" Paragraph in "Informational Submittals" Article if retaining first paragraph below.
A. Brazing: Qualify processes and operators according to ASME Boiler and Pressure Vessel Code: Section IX.

Retain one or both of first two paragraphs below for welding supports. Retain first paragraph for welded piping supports; retain second for welded steel pipe joints. Also retain "Welding certificates" Paragraph in "Informational Submittals" Article.
B. Steel Support Welding Qualifications: Qualify procedures and personnel according to AWS D1.1/D1.1M, "Structural Welding Code - Steel."

C. Pipe Welding Qualifications: Qualify procedures and operators according to ASME Boiler and Pressure Vessel Code.

D. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

E. Comply with ASME B31.9, "Building Services Piping," for fuel-oil piping materials, installation, testing, and inspecting.

F. Comply with requirements of the EPA and of state and local authorities having jurisdiction. Include recording of fuel-oil storage tanks and monitoring of tanks and piping.

1.7 WARRANTY

A. Special Warranty: Manufacturer's standard form in which manufacturer agrees to repair or replace components of fuel-oil storage tanks and flexible, double-containment piping and related equipment that fail in materials or workmanship within specified warranty period.

1. Storage Tanks:

a. Failures include, but are not limited to, the following when used for storage of fuel oil at temperatures not exceeding [150 deg F (66 deg C)] <Insert temperature>:

1) Structural failures including cracking, breakup, and collapse.

Retain first subparagraph below for steel tanks.
2) Corrosion failure including external and internal corrosion of steel tanks.

Verify available warranties and warranty periods for units and components with manufacturers listed in Part 2 articles.
b. Warranty Period: [30] <Insert number> years from date of Substantial Completion.

2. Flexible, Double-Containment Piping and Related Equipment:

a. Failures due to defective materials or workmanship for materials installed together, including piping, dispenser sumps, entry boots, and sump mounting adapters.

Verify available warranties and warranty periods for units and components with manufacturers listed in Part 2 articles.
b. Warranty Period: [10] [30] <Insert number> years from date of Substantial Completion.

PART 2 -  PRODUCTS

2.1 PIPES, TUBES, AND FITTINGS

This article includes examples of materials listed in NFPA 30, "Flammable and Combustible Liquids Code." Coordinate piping materials in this article with piping schedules in Part 3. See "Writing Guide" Article in the Evaluations for a discussion of how this Section is organized and the most efficient way to edit this Section.
A. See Part 3 piping schedule articles for where pipes, tubes, fittings, and joining materials are applied in various services.

B. Steel Pipe: ASTM A 53/A 53M, black steel, Schedule 40, Type E or S, Grade B.

1. Malleable-Iron Threaded Fittings: ASME B16.3, Class 150, standard pattern.

2. Wrought-Steel Welding Fittings: ASTM A 234/A 234M, for butt and socket welding.

3. Unions: ASME B16.39, Class 150, malleable iron with brass-to-iron seat, ground joint, and threaded ends.

Retain subparagraph below for underground steel pipe. Cathodic protection may be required in addition to protective coating. Coordinate with requirements in Section 264200 "Cathodic Protection."
4. Protective Coating for Underground Piping: Factory-applied, three-layer coating of epoxy, adhesive, and PE.

a. Joint Cover Kits: Epoxy paint, adhesive, and heat-shrink PE sleeves.

C. Annealed-Temper Copper Tube: Comply with [ASTM B 88, Type K (ASTM B 88M, Type A)] [ASTM B 88, Type L (ASTM B 88M, Type B)].

1. Copper Fittings: ASME B16.22, wrought copper, streamlined pattern.

Verify acceptability of fittings in subparagraph below with authorities having jurisdiction before retaining.
2. Flare Fittings: Comply with ASME B16.26 and SAE J513.

a. Copper fittings with long nuts.

b. Metal-to-metal compression seal without gasket.

c. Dryseal threads complying with ASME B1.20.3.

2.2 DOUBLE-CONTAINMENT PIPE AND FITTINGS

A. Flexible, Double-Containment Piping: Comply with UL 971.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain first subparagraph and list of manufacturers below. See Section 016000 "Product Requirements."
1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Environ Products, Inc.

b. OPW.

c. <Insert manufacturer's name>.

2. Pipe Materials: PVDF complying with ASTM D 3222 for carrier pipe with mechanical couplings to seal carrier, and PE pipe complying with ASTM D 4976 for containment piping.

3. [Fiberglass] [PE] sumps.

4. Watertight sump entry boots, pipe adapters with test ports and tubes, coaxial fittings, and couplings.

5. Minimum Operating Pressure Rating: 10 psig (69 kPa).

6. Plastic to Steel Pipe Transition Fittings: Factory-fabricated fittings with plastic end matching or compatible with carrier piping, and steel pipe end complying with ASTM A 53/A 53M, black steel, Schedule 40, Type E or S, Grade B.

Retain subparagraph below if double-containment piping will have cable leak-detection system installed in annular space.
7. Include design and fabrication of double-containment pipe and fitting assemblies with provision for field installation of cable leak-detection system in annular space between carrier and containment piping.

2.3 PIPING SPECIALTIES

A. Y-Pattern Strainers:

1. Body: ASTM A 126, Class B, cast iron with bolted cover and bottom drain connection.

2. End Connections: Threaded ends for NPS 2 (DN 50) and smaller.

3. Strainer Screen: [60] [80]-mesh startup strainer, and perforated stainless-steel basket with 50 percent free area.

4. CWP Rating: 125 psig (860 kPa).

B. Manual Air Vents:

1. Body: Bronze.

2. Internal Parts: Nonferrous.

3. Operator: Screwdriver or thumbscrew.

4. Inlet Connection: NPS 1/2 (DN 15).

5. Discharge Connection: NPS 1/8 (DN 6).

6. CWP Rating: 150 psig (1035 kPa).

7. Maximum Operating Temperature: 225 deg F (107 deg C).

2.4 JOINING MATERIALS

A. Joint Compound and Tape: Suitable for fuel oil.

B. Welding Filler Metals: Comply with AWS D10.12/D10.12M for welding materials appropriate for wall thickness and chemical analysis of steel pipe being welded.

C. Brazing Filler Metals: Alloy with melting point greater than 1000 deg F (540 deg C) complying with AWS A5.8/A5.8M. Brazing alloys containing more than 0.05 percent phosphorus are prohibited.

2.5 MANUAL FUEL-OIL SHUTOFF VALVES

Coordinate valve materials in this article with the valve schedule in Part 3. See "Writing Guide" Article in the Evaluations for a discussion of how this Section is organized and the most efficient way to edit this Section.
Shutoff valves for fuel-oil service must comply with one or more standards. Revise this article if compliance with specific standards apply. If locking devices are required, verify that they are available from listed manufacturers.
A. See valve schedule in Part 3 for where each valve type is applied in various services.

B. General Requirements for Metallic Valves: Comply with UL 842.

1. CWP Rating: [125 psig (860 kPa)] <Insert pressure>.

2. Threaded Ends: Comply with ASME B1.20.1.

3. Dryseal Threads on Flare Ends: Comply with ASME B1.20.3.

4. Tamperproof Feature: Locking feature for valves indicated in the valve schedule.

5. Service Mark: Initials "WOG" shall be permanently marked on valve body.

Caution: Two-piece ball valves with a full or regular port are recommended for most services. One-piece ball valves have a reduced port but one fewer leak path.
C. One-Piece, Bronze Ball Valve with Bronze Trim: MSS SP-110.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain first subparagraph and list of manufacturers below. See Section 016000 "Product Requirements."
1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. BrassCraft Manufacturing Company; a Masco company.

b. Conbraco Industries, Inc.; Apollo Div.

c. Lyall, R. W. & Company, Inc.

d. McDonald, A. Y. Mfg. Co.

e. Perfection Corporation; A Subsidiary of American Meter Company.

f. <Insert manufacturer's name>.

2. Body: Bronze, complying with ASTM B 584.

3. Ball: Chrome-plated brass.

4. Stem: Bronze; blowout proof.

5. Seats: Reinforced TFE; blowout proof.

6. Packing: Separate packnut with adjustable-stem packing threaded ends.

7. Ends: Threaded, flared, or socket as indicated in the valve schedule.

8. CWP Rating: 600 psig (4140 kPa).

9. Service Mark: Initials "WOG" shall be permanently marked on valve body.

Where pressure drop is a concern, use full-port ball valves. For corrosive or high-temperature applications, use stainless-steel trim ball valves.
D. Two-Piece, Full-Port, Bronze Ball Valves with Bronze Trim: MSS SP-110.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain first subparagraph and list of manufacturers below. See Section 016000 "Product Requirements."
1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. BrassCraft Manufacturing Company; a Masco company.

b. Conbraco Industries, Inc.; Apollo Div.

c. Lyall, R. W. & Company, Inc.

d. McDonald, A. Y. Mfg. Co.

e. Perfection Corporation; A Subsidiary of American Meter Company.

f. <Insert manufacturer's name>.

2. Body: Bronze, complying with ASTM B 584.

3. Ball: Chrome-plated bronze.

4. Stem: Bronze; blowout proof.

5. Seats: Reinforced TFE; blowout proof.

6. Packing: Threaded-body packnut design with adjustable-stem packing.

7. Ends: Threaded, flared, or socket as indicated in the valve schedule.

8. CWP Rating: 600 psig (4140 kPa).

9. Service Mark: Initials "WOG" shall be permanently marked on valve body.

E. Two-Piece, Regular-Port Bronze Ball Valves with Bronze Trim: MSS SP-110.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain first subparagraph and list of manufacturers below. See Section 016000 "Product Requirements."
1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. BrassCraft Manufacturing Company; a Masco company.

b. Conbraco Industries, Inc.; Apollo Div.

c. Lyall, R. W. & Company, Inc.

d. McDonald, A. Y. Mfg. Co.

e. Perfection Corporation; A Subsidiary of American Meter Company.

f. <Insert manufacturer's name>.

2. Body: Bronze, complying with ASTM B 584.

3. Ball: Chrome-plated bronze.

4. Stem: Bronze; blowout proof.

5. Seats: Reinforced TFE.

6. Packing: Threaded-body packnut design with adjustable-stem packing.

7. Ends: Threaded, flared, or socket as indicated in the valve schedule.

8. CWP Rating: 600 psig (4140 kPa).

9. Service Mark: Initials "WOG" shall be permanently marked on valve body.

2.6 SPECIALTY VALVES

A. Pressure Relief Valves: Comply with UL 842.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain first subparagraph and list of manufacturers below. See Section 016000 "Product Requirements."
1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Anderson Greenwood; Division of Tyco Flow Control.

b. Fulflo Specialties, Inc.

c. Webster Fuel Pumps & Valves; a division of Capital City Tool, Inc.

d. <Insert manufacturer's name>.

2. Listed and labeled for fuel-oil service by an NRTL acceptable to authorities having jurisdiction.

3. Body: Brass, bronze, or cast steel.

4. Springs: Stainless steel, interchangeable.

5. Seat and Seal: Nitrile rubber.

6. Orifice: Stainless steel, interchangeable.

7. Factory-Applied Finish: Baked enamel.

8. Maximum Inlet Pressure: [150 psig (1035 kPa)] <Insert pressure>.

9. Relief Pressure Setting: [60 psig (414 kPa)] <Insert pressure>.

B. Oil Safety Valves: Comply with UL 842.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain first subparagraph and list of manufacturers below. See Section 016000 "Product Requirements."
1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Anderson Greenwood; Division of Tyco Flow Control.

b. Suntec Industries Incorporated.

c. Webster Fuel Pumps & Valves; a division of Capital City Tool, Inc.

d. <Insert manufacturer's name>.

2. Listed and labeled for fuel-oil service by an NRTL acceptable to authorities having jurisdiction.

3. Body: Brass, bronze, or cast steel.

4. Springs: Stainless steel.

5. Seat and Diaphragm: Nitrile rubber.

6. Orifice: Stainless steel, interchangeable.

7. Factory-Applied Finish: Baked enamel.

8. Manual override port.

9. Maximum Inlet Pressure: [60 psig (414 kPa)] <Insert pressure>.

10. Maximum Outlet Pressure: [3 psig (21 kPa)] <Insert pressure>.

2.7 FRP FUEL-OIL UST

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."
A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Containment Solutions, Inc.

2. Xerxes Corporation.

3. <Insert manufacturer's name>.

C. Description: Horizontal, FRP UST; UL 1316, double wall, with interstitial space.

D. Construction: Fabricated with fiberglass-reinforced polyester resins; suitable for operation at atmospheric pressure; fabricated for the following loads:

1. Depth of Bury: 3 feet (1 m) from top of tank to finished surface.

2. External Hydrostatic Pressure: To withstand general buckling with safety factor of 2:1 if hole is fully flooded.

3. Surface Loads: AASHTO's "Specifications for Highway Bridges," H-20 axle loads of 32,000 lb (14 515 kg).

If Project has more than one type or configuration of FRP fuel-oil UST, delete paragraph below and schedule tanks on Drawings.
E. Capacities and Characteristics:

1. Capacity: <Insert gal. (L)>.

2. Diameter: <Insert feet (m)>.

3. Length: <Insert feet (m)>.

4. Connection Sizes:

a. Fill Line: <Insert NPS (DN)>.

b. Vent Line: <Insert NPS (DN)>.

c. Outlet: <Insert NPS (DN)>.

d. Return: <Insert NPS (DN)>.

e. Gage: <Insert NPS (DN)>.

5. Manholes:

a. Number Required: <Insert number>.

b. Diameter: <Insert inches (mm)>.

2.8 FUEL-OIL UST ACCESSORIES

Retain this article for USTs. Show fittings and accessories on plans, details, and piping schematics.
A. Tank Manholes: 22-inch- (560-mm-) minimum diameter; bolted, flanged, and gasketed, with extension collar; for access to inside of tank.

Retain first paragraph below for steel tanks.
B. Steel Tank Masonry Supports: Two [6-by-6-by-3/8-inch (150-by-150-by-10-mm)] <Insert dimensions> steel angles, [72 inches (1800 mm)] <Insert dimension> long, located longitudinally on tank on each side of manholes and continuously welded in place.

C. Threaded pipe connection fittings on top of tank for fill, supply, return, vent, sounding, and gaging, in locations and of sizes indicated. Include cast-iron plugs for shipping.

D. Striker Plates: Inside tank, on bottom below fill, vent, sounding, gage, and other tube openings.

E. Lifting Lugs: For handling and installation.

F. Ladders: Carbon-steel ladder inside tank, anchored to top and bottom. Include reinforcement of tank at bottom of ladder.

G. Supply Tube: Extension of supply piping fitting into tank, terminating 6 inches (150 mm) above tank bottom and cut at a 45-degree angle (1:1 slope).

H. Sounding and Gage Tubes: Extension of fitting into tank, terminating 6 inches (150 mm) above tank bottom and cut at a 45-degree angle (1:1 slope).

I. Containment Sumps: [Fiberglass] [PE] with sump base, add-on extension pieces as required, sump top, lid, and gasket-seal joints. Include sump entry boots for pipe penetrations through sidewalls.

J. Sump Entry Boots: Two-part pipe fitting for field assembly and of size required to fit over pipe. Include gaskets shaped to fit sump sidewall, sleeves, seals, and clamps as required for liquid-tight pipe penetrations.

K. Anchor Straps: Storage tank manufacturer's standard anchoring system, with straps, strap-insulating material, cables and turnbuckles, of strength at least one and one-half times maximum uplift force of empty tank without backfill in place.

L. Filter Mat: Geotextile woven or spun filter fabric, in 1 or more layers, for minimum total weight of [3 oz./sq. yd. (101.7 g/sq. m)] <Insert dimension>.

M. Overfill Prevention Valves: Factory fabricated or shop or field assembled from manufacturer's standard components. Include drop tube, cap, fill nozzle adaptor, check valve mechanism or other devices, and vent if required to restrict flow at 95 percent of tank capacity and to provide complete shutoff of filling at [98] [99] <Insert other> percent of tank capacity.

2.9 FUEL-OIL STORAGE TANK PIPING SPECIALTIES

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain first paragraph and list of manufacturers below. See Section 016000 "Product Requirements."
A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1. EBW, Inc.

2. Environ Products, Inc.

3. Morrison Bros. Co.

4. OPW.

5. Preferred Utilities Manufacturing Corporation.

6. Universal Valve Company.

7. <Insert manufacturer's name>.

Show fuel-oil tank specialty fittings on plans, details, and piping schematics.
B. Fitting Materials: Cast iron, malleable iron, brass, or corrosion-resistant metal; suitable for fuel-oil service.

1. Surface, Flush-Mounted Fittings: Waterproof and suitable for truck traffic.

2. Aboveground-Mounted Fittings: Weatherproof.

Retain one of first three paragraphs below.
C. Spill-Containment Fill Boxes: Flush mounting, with drainage feature to drain oil into tank, threaded fill-pipe connection, and wrench operation.

D. Fill Boxes: Flush mounting, with threaded fill-pipe connection and wrench operation.

E. Locking Fill Boxes: Flush mounting, with locking-type inner fill cap for standard padlock and threaded fill-pipe connection.

F. Supply and Sounding Drop Tubes: Fuel-oil supply piping or fitting, inside tank, terminating 6 inches (150 mm) above bottom of tank, and with end cut at a 45-degree angle (1:1 slope).

G. Pipe Adapters and Extensions: Compatible with piping and fittings.

H. Suction Strainers and Check Valves: Bronze or corrosion-resistant metal components.

I. Foot Valves and Antisiphon Valves: Poppet-type, bronze or corrosion-resistant metal components.

J. Weatherproof Vent Cap: Cast- or malleable-iron increaser fitting with corrosion-resistant wire screen, with free area at least equal to cross-sectional area of connecting pipe and threaded-end connection.

K. Metal Manholes: [22-inch- (560-mm-)] <Insert dimension> minimum diameter frame and cover. Furnish manhole units of adequate size for access to fittings if size is not indicated.

L. Monitoring Well Caps: Locking pipe plug and manhole.

M. <Insert required fittings here>.

2.10 SIMPLEX FUEL-OIL TRANSFER PUMPS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."
A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. DESMI INC./Rotan Pumps.

2. Haight Pumps; Division of Baker Mfg.

3. Preferred Utilities Manufacturing Corporation.

4. Suntec Industries Incorporated.

5. Tuthill Corporation; Tuthill Pump Div.

6. Viking Pump Inc.; a Unit of IDEX Corporation.

7. Webster Fuel Pumps & Valves; a division of Capital City Tool, Inc.

8. <Insert manufacturer's name>.

C. Description: Comply with UL 343, and HI M109.

1. Listed and labeled for fuel-oil service by an NRTL acceptable to authorities having jurisdiction.

2. Type: Positive-displacement, rotary type.

3. Impeller: [Steel gear with crescent] [Carbon vane].

4. Housing: Cast-iron foot mounted.

5. Bearings: Bronze, self-lubricating.

6. Shaft: Polished steel.

7. Seals: Mechanical.

8. Base: Steel.

9. Pressure Relief: Built in.

10. Discharge Check Valve: Built in.

Some manufacturers provide close-coupled pumps in first paragraph below only in certain size ranges.
D. Drive: [V-belt with guard; gear reducer; or direct, close coupled] [V-belt with guard] [Gear reducer] [Direct, close coupled].

E. Controls:

Select desired control features from subparagraphs below.
1. Run pump to maintain minimum manifold pressure with outdoor-air temperature less than [60 deg F (16 deg C)] <Insert temperature>.

2. Run pump on seven-day schedule.

3. Alarm motor failure.

4. Manual reset dry-run protection. Stop pump if fuel level falls below pump suction.

5. Deenergize and alarm pump locked rotor condition.

6. Alarm open circuit, high and low voltage.

7. Indicating lights for power on, run, and off normal conditions.

8. Interface with automatic control system is specified in Section 230900 "Instrumentation and Control for HVAC" to control and indicate the following:

a. Start/stop pump when required by schedule, fuel-fired appliance operation, day tank level control, or weather conditions.

b. Operating status.

c. Alarm off-normal status.

Default motor characteristics are specified in Section 230513 "Common Motor Requirements for HVAC Equipment."
F. Motor: Comply with NEMA designation, temperature rating, service factor, enclosure type, and efficiency requirements for motors specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

1. Motor Sizes: Minimum size as indicated. If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

2. Controllers, Electrical Devices, and Wiring: Comply with requirements for electrical devices and connections specified in electrical Sections.

If Project has more than one simplex fuel-oil transfer pump, delete paragraph below and schedule pumps on Drawings.
G. Capacities and Characteristics:

1. Number of Stages: <Insert number>.

2. Capacity: <Insert gph (L/s)>.

3. Inlet Vacuum: <Insert inches Hg (kPa)>.

4. Discharge Pressure: <Insert psig (kPa)>.

5. Inlet and Outlet Size: <Insert NPS (DN)>.

6. Motor Speed: <Insert rpm>.

7. Motor Horsepower: <Insert value>.

8. Electrical Characteristics:

a. Volts: [120] [208] [240] <Insert value>.

b. Phase: [Single] [Three].

c. Hertz: 60.

d. Full-Load Amperes: <Insert value>.

e. Minimum Circuit Ampacity: <Insert value>.

f. Maximum Overcurrent Protection: <Insert amperage>.

2.11 LEAK-DETECTION AND MONITORING SYSTEM

A. Cable and Sensor System: Comply with UL 1238.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."
1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Caldwell Systems Corporation.

b. Containment Solutions, Inc.

c. EBW, Inc.

d. Gems Sensors Inc.

e. Highland Tank & Manufacturing Company, Inc.

f. INCON, Inc.

g. In-Situ, Inc.

h. MSA; Instrument Div.

i. Perma-Pipe, Inc.

j. Pneumercator Inc.

k. Raychem Corp; Tyco Electronics Corporation.

l. Tuthill Corporation; Tuthill Transfer Systems; Sotera Systems.

m. Veeder-Root; a Danaher Corporation Company.

n. <Insert manufacturer's name>.

3. Calibrated, leak-detection and monitoring system with probes and other sensors and remote alarm panel for fuel-oil storage tanks and fuel-oil piping.

4. Include fittings and devices required for testing.

5. Controls: Electrical, operating on [120] <Insert voltage>-V ac.

6. Calibrated, liquid-level gage complying with [UL 180 with floats] [UL 1238 with probes] or other sensors and remote annunciator panel.

7. Remote Annunciator Panel: With visual and audible, high-tank-level and low-tank-level alarms, fuel indicator with registration in gallons (liters), and overfill alarm. Include gage volume range that covers fuel-oil storage capacity.

8. Controls: Electrical, operating on [120] <Insert voltage>-V ac.

2.12 LABELING AND IDENTIFYING

A. Detectable Warning Tape: Acid- and alkali-resistant, PE film warning tape manufactured for marking and identifying underground utilities, a minimum of 6 inches (152 mm) wide and 4 mils (0.1 mm) thick, continuously inscribed with a description of utility, with metallic core encased in a protective jacket for corrosion protection, detectable by metal detector when tape is buried up to 30 inches (762 mm) deep; colored yellow.

2.13 SOURCE QUALITY CONTROL

A. Pressure test and inspect fuel-oil storage tanks, after fabrication and before shipment, according to ASME and UL 1316.

B. Affix standards organization's code stamp.

PART 3 -  EXECUTION

3.1 EARTHWORK

A. Comply with requirements in Section 312000 "Earth Moving" for excavating, trenching, and backfilling.

3.2 OUTDOOR PIPING INSTALLATION

NFPA 30 requires a minimum of 18 inches (457 mm) of compacted backfill, 8 inches (203 mm) under asphalt 2 inches (51 mm) thick, or 4 inches (102 mm) under 4 inches (102 mm) of reinforced concrete in areas subject to vehicle traffic; 6 inches (152 mm) of compacted backfill in areas without traffic. Greater depth is required as recommended by pipe and equipment manufacturers where frost conditions may occur.
A. Install underground fuel-oil piping buried at least [18 inches (457 mm)] <Insert dimension> below finished grade. Comply with requirements in Section 312000 "Earth Moving" for excavating, trenching, and backfilling.

1. If fuel-oil piping is installed with less than [12 inches (305 mm)] <Insert dimension> of cover to finished grade, install in containment piping.

B. Steel Piping with Protective Coating:

1. Apply joint cover kits to pipe after joining, to cover, seal, and protect joints.

Retain one of two subparagraphs below. Verify acceptability of repaired coating systems with authorities having jurisdiction.
2. Repair damage to PE coating on pipe as recommended in writing by protective coating manufacturer. Review protective coating damage with Architect prior to repair.

3. Replace pipe having damaged PE coating with new pipe.

C. Install double-containment, fuel-oil pipe at a minimum slope of 1 percent downward toward fuel-oil storage tank sump.

D. Install vent pipe at a minimum slope of 2 percent downward toward fuel-oil storage tank sump.

E. Assemble and install entry boots for pipe penetrations through sump sidewalls for liquid-tight joints.

F. Install metal pipes and tubes, fittings, and valves at piping connections to UST.

G. Install fittings for changes in direction in rigid pipe.

H. Install system components with pressure rating equal to or greater than system operating pressure.

I. Install pressure gage on suction[ and discharge] from each pump. Pressure gages are specified in Section 230519 "Meters and Gages for HVAC Piping."

3.3 INDOOR PIPING INSTALLATION

A. Arrange for pipe spaces, chases, slots, sleeves, and openings in building structure during progress of construction, to allow for mechanical installations.

B. Install piping in concealed locations unless otherwise indicated and except in equipment rooms and service areas.

C. Install piping indicated to be exposed and piping in equipment rooms and service areas at right angles or parallel to building walls. Diagonal runs are prohibited unless specifically indicated otherwise.

D. Install piping above accessible ceilings to allow sufficient space for ceiling panel removal.

E. Install piping free of sags and bends.

F. Install fittings for changes in direction and branch connections.

G. Verify final equipment locations for roughing-in.

H. Comply with requirements for equipment specifications in plumbing and HVAC Sections for roughing-in requirements.

I. Conceal pipe installations in walls, pipe spaces, or utility spaces; above ceilings; below grade or floors; and in floor channels unless indicated to be exposed to view.

J. Prohibited Locations:

1. Do not install fuel-oil piping in or through circulating air ducts, clothes or trash chutes, chimneys or gas vents (flues), ventilating ducts, or dumbwaiter or elevator shafts.

2. Do not install fuel-oil piping in solid walls or partitions.

K. Use eccentric reducer fittings to make reductions in pipe sizes. Install fittings with level side down.

L. Connect branch piping from top or side of horizontal piping.

M. Install unions in pipes NPS 2 (DN 50) and smaller at final connection to each piece of equipment and elsewhere as indicated. Unions are not required on flanged devices.

N. Do not use fuel-oil piping as grounding electrode.

O. Install strainer on inlet side of fuel-oil pump.

P. Install sleeves for piping penetrations of walls, ceilings, and floors. Comply with requirements for sleeves specified in Section 230517 "Sleeves and Sleeve Seals for HVAC Piping."

Retain first paragraph below for piping that penetrates an exterior concrete wall or concrete slab.
Q. Install sleeve seals for piping penetrations of concrete walls and slabs. Comply with requirements for sleeve seals specified in Section 230517 "Sleeves and Sleeve Seals for HVAC Piping."

R. Install escutcheons for piping penetrations of walls, ceilings, and floors. Comply with requirements for escutcheons specified in Section 230518 "Escutcheons for HVAC Piping."

3.4 VALVE INSTALLATION

A. Install manual fuel-oil shutoff valves on branch connections to fuel-oil appliance.

B. Install valves in accessible locations.

C. Protect valves from physical damage.

D. Install metal tag attached with metal chain indicating fuel-oil piping systems.

E. Identify valves as specified in Section 230553 "Identification for HVAC Piping and Equipment."

F. Install oil safety valves at inlet of each oil-fired appliance.

G. Install pressure relief valves in distribution piping between the supply and return lines.

H. Install one-piece, bronze ball valve with hose end connection at low points in fuel-oil piping.

I. Install manual air vents at high points in fuel-oil piping.

3.5 PIPING JOINT CONSTRUCTION

A. Ream ends of pipes and tubes and remove burrs.

B. Remove scale, slag, dirt, and debris from inside and outside of pipe and fittings before assembly.

C. Threaded Joints: Thread pipe with tapered pipe threads according to ASME B1.20.1. Cut threads full and clean using sharp dies. Ream threaded pipe ends to remove burrs and restore full ID. Join pipe fittings and valves as follows:

1. Apply appropriate tape or thread compound to external pipe threads unless dry seal threading is specified.

2. Damaged Threads: Do not use pipe or pipe fittings with threads that are corroded or damaged. Do not use pipe sections that have cracked or open welds.

D. Welded Joints: Construct joints according to AWS D10.12/D10.12M, using qualified processes and welding operators according to "Quality Assurance" Article.

1. Bevel plain ends of steel pipe.

2. Patch factory-applied protective coating as recommended by manufacturer at field welds and where damage to coating occurs during construction.

E. Brazed Joints: Construct joints according to AWS's "Brazing Handbook," "Pipe and Tube" Chapter.

F. Flared Joints: Comply with SAE J513. Tighten finger tight, then use wrench according to fitting manufacturer's written recommendations. Do not overtighten.

3.6 FUEL-OIL UST INSTALLATION

A. Excavate to sufficient depth for a minimum of 3 feet (1 m) of earth cover from top of tank to finished grade. Allow for cast-in-place, concrete-ballast base plus 6 inches (150 mm) of sand or pea gravel between ballast base and tank. Extend excavation at least 12 inches (300 mm) around perimeter of tank.

B. Set tie-down eyelets for hold-down straps in concrete-ballast base and tie to reinforcing steel.

C. Place 6 inches (152 mm) of clean sand or pea gravel on top of concrete-ballast base.

D. Set tank on fill materials and install hold-down straps.

E. Connect piping.

F. Install tank leak-detection and monitoring devices.

G. Install containment sumps.

H. Backfill excavation with clean sand or pea gravel in 12-inch (305-mm) lifts and tamp backfill lift to consolidate.

I. Install filter mat between top of backfill material and earth fill.

J. Install FRP USTs with FRP hold-down straps, manhole extensions, and manhole risers.

3.7 HANGER AND SUPPORT INSTALLATION

A. Pipe hanger and support and equipment support materials and installation requirements are specified in Section 230529 "Hangers and Supports for HVAC Piping and Equipment."

Maximum spans below are from MSS SP-69 (water service).
B. Install hangers for horizontal steel piping with the following maximum spacing and minimum rod sizes:

1. NPS 1-1/4 (DN 32) and Smaller: Maximum span, 84 inches (2130 mm); minimum rod size, 3/8 inch (10 mm).

2. NPS 1-1/2 (DN 40): Maximum span, 108 inches (2740 mm); minimum rod size, 3/8 inch (10 mm).

3. NPS 2 (DN 50): Maximum span, 10 feet (3 m); minimum rod size, 3/8 inch (10 mm).

C. Support vertical steel pipe at each floor and at spacing not greater than 15 feet (4.5 m).

D. Support vertical copper tube at each floor and at spacing not greater than 10 feet (3 m).

3.8 FUEL-OIL PUMP INSTALLATION

A. Transfer Pumps:

1. Install pumps with access space for periodic maintenance including removal of motors, impellers, and accessories.

2. Set pumps on and anchor to concrete base.

B. Install two-piece, full-port ball valves at suction and discharge of pumps.

C. Install strainer on inlet side of simplex fuel-oil pumps.

D. Install check valve on discharge of simplex fuel-oil pumps.

E. Install suction piping with minimum fittings and change of direction.

F. Install vacuum and pressure gage, upstream and downstream respectively, at each pump to measure the differential pressure across the pump. Pressure gages are specified in Section 230519 "Meters and Gages for HVAC Piping."

3.9 LEAK-DETECTION AND MONITORING SYSTEM INSTALLATION

Coordinate this article with fuel-oil storage tank and piping.
A. Install leak-detection and monitoring system. Install alarm panel inside building where indicated.

1. Double-Wall, Fuel-Oil Storage Tanks: [Install probes] [Install probes or use factory-installed integral probes] [Use factory-installed integral probes] in interstitial space.

Float-type probes in tank containment sumps and at piping low points, if required, are the most often used. Cable sensors are also available.
2. Double-Containment, Fuel-Oil Piping: Install leak-detection sensor [probes in fuel-oil storage tank containment sumps and at low points in piping] [cable probes in interstitial space of double-containment piping].

Retain subparagraph below for liquid-level gage that is part of leak-detection and monitoring system.
3. Install liquid-level gage.

3.10 CONNECTIONS

A. Install piping adjacent to equipment to allow service and maintenance.

B. Install unions, in piping NPS 2 (DN 50) and smaller, adjacent to each valve and at final connection to each piece of equipment having threaded pipe connection.

C. Connect piping to equipment with ball valve and union. Install union between valve and equipment.

D. Install flexible piping connectors at final connection to burners or oil-fired appliances that must be moved for maintenance access.

3.11 LABELING AND IDENTIFYING

A. Nameplates, pipe identification, and signs are specified in Section 230553 "Identification for HVAC Piping and Equipment."

Coordinate dimensions in paragraph below with depth of bury for fuel-oil piping.
B. Install detectable warning tape directly above fuel-oil piping, [12 inches (304 mm)] <Insert dimension> below finished grade, except [6 inches (152 mm)] <Insert dimension> below subgrade under pavements and slabs. Terminate tracer wire in an accessible area, and identify as "tracer wire" for future use with plastic-laminate sign.

1. Piping: Over underground fuel-oil distribution piping.

2. Fuel-Oil Storage Tanks: Over edges of each UST.

3.12 CONCRETE BASES

Coordinate concrete work in this article with Section 033000 "Cast-in-Place Concrete" or Section 033053 "Miscellaneous Cast-in-Place Concrete."
A. Concrete Bases: Anchor equipment to concrete base according to equipment manufacturer's written instructions and according to seismic codes at Project.

1. Construct concrete bases of dimensions indicated, but not less than 4 inches (100 mm) larger in both directions than supported unit.

2. Install dowel rods to connect concrete base to concrete floor. Unless otherwise indicated, install dowel rods on [18-inch (457-mm)] <Insert dimension> centers around the full perimeter of the base.

3. Install epoxy-coated anchor bolts for supported equipment that extend through concrete base, and anchor into structural concrete floor.

4. Place and secure anchorage devices. Use supported equipment manufacturer's setting drawings, templates, diagrams, instructions, and directions furnished with items to be embedded.

5. Install anchor bolts to elevations required for proper attachment to supported equipment.

6. Use [3000-psig (20.7-MPa)] <Insert dimension>, 28-day, compressive-strength concrete and reinforcement as specified in [Section 033000 "Cast-in-Place Concrete."] [Section 033053 "Miscellaneous Cast-in-Place Concrete."]

3.13 FIELD QUALITY CONTROL

Tank and pipe test pressures in this article are required by NFPA 31. Verify requirements with authorities having jurisdiction.
Retain first paragraph below if storage tanks do not bear the ASME code stamp as required in "Source Quality Control" Article.
A. Tanks: Minimum hydrostatic or compressed-air test pressures for fuel-oil storage tanks that have not been factory tested and do not bear the ASME code stamp or a listing mark acceptable to authorities having jurisdiction:

1. Inner Tanks: Minimum 3 psig (20.7 kPa) and maximum 5 psig (34.5 kPa).

2. Interstitial Space: Minimum 3 psig (20.7 kPa) and maximum 5 psig (34.5 kPa), or 5.3-in. Hg (18-kPa) vacuum.

3. Where vertical height of fill and vent pipes is such that the static head imposed on the bottom of the tank is greater than 10 psig (69 kPa), hydrostatically test the tank and fill and vent pipes to a pressure equal to the static head thus imposed.

4. Maintain the test pressure for one hour.

B. Piping: Minimum hydrostatic or pneumatic test-pressures measured at highest point in system:

1. Fuel-Oil Distribution Piping: Minimum [5 psig (34.5 kPa)] <Insert dimension> for minimum [30] <Insert time> minutes.

2. Fuel-Oil, Double-Containment Piping:

a. Carrier Pipe: Minimum [5 psig (34.5 kPa)] <Insert dimension> for minimum [30] <Insert time> minutes.

b. Containment Conduit: Minimum [5 psig (34.5 kPa)] <Insert dimension> for minimum [60] <Insert time> minutes.

3. Suction Piping: Minimum 20-in. Hg (68 kPa) for minimum [30] <Insert time> minutes.

4. Isolate storage tanks if test pressure in piping will cause pressure in storage tanks to exceed 10 psig (69 kPa).

C. Inspect and test fuel-oil piping according to NFPA 31, "Tests of Piping" Paragraph; and according to requirements of authorities having jurisdiction.

D. Test liquid-level gage for accuracy by manually measuring fuel-oil levels at not less than [three] [four] [five] <Insert number or describe procedure> different depths while filling tank and checking against gage indication.

E. Test leak-detection and monitoring system for accuracy by manually operating sensors and checking against alarm panel indication.

F. Start fuel-oil transfer pumps to verify for proper operation of pump and check for leaks.

G. Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.

H. Bleed air from fuel-oil piping using manual air vents.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.
I. Fuel-oil piping and equipment will be considered defective if it does not pass tests and inspections.

J. Prepare test and inspection reports.

3.14 OUTDOOR PIPING SCHEDULE

Retain and revise applicable piping applications. Coordinate with materials specified in Part 2. Retain multiple materials for Contractor's option.
A. Underground Fuel-Oil Piping: Flexible, double-containment piping; size indicated is carrier-pipe size.

Fill and vent piping are not generally filled with fuel oil; therefore, they are not usually required to be double contained. Verify this installation practice with authorities having jurisdiction.
B. Underground Fuel-Oil-tank Fill and Vent Piping: Steel pipe, steel or malleable-iron threaded fittings, and threaded joints. Coat pipe and fittings with protective coating for steel piping.

Indicate extent of containment conduit on Drawings. Containment conduit is required for piping with insufficient depth of bury.
C. Containment Conduit: Steel pipe with wrought-steel fittings and welded joints. Coat pipe and fittings with protective coating for steel piping.

Retain "one of" option in paragraph below to allow Contractor to select piping materials from those retained.
D. Aboveground fuel-oil piping shall be[ one of] the following:

Because fill and vent piping do not generally contain fuel oil, double-containment piping is usually not required. Verify requirements with authorities having jurisdiction.
1. Steel pipe, steel or malleable-iron threaded fittings, and threaded joints.

2. Annealed-temper copper tube with wrought-copper fittings and brazed joints.

3.15 INDOOR PIPING SCHEDULE

Retain and revise applicable piping applications. Coordinate with materials specified in Part 2.
A. Aboveground Fuel-Oil Piping:

1. [NPS 1/2 (DN 15)] <Insert pipe size> and Smaller: [Steel pipe, steel or malleable-iron threaded fittings, and threaded joints] [Annealed-temper copper pipe, wrought copper fittings, and brazed or flared joints].

2. [NPS 5/8 to NPS 2 (DN 18 to DN 50)] <Insert pipe size>: Steel pipe, steel or malleable-iron threaded fittings, and threaded joints.

3.16 ABOVEGROUND MANUAL FUEL-OIL SHUTOFF VALVE SCHEDULE

Retain and revise applicable piping applications. Coordinate with materials specified in Part 2.
Retain "one of" option in first paragraph below to allow Contractor to select piping materials from those retained.
A. Distribution piping valves for pipe NPS 2 (DN 50) and smaller shall be[ one of] the following:

1. One-piece, bronze ball valve with bronze trim.

2. Two-piece, [full] [regular]-port, bronze ball valves with bronze trim.

Retain "one of" option in paragraph below to allow Contractor to select piping materials from those retained.
B. Valves in branch piping for single appliance shall be[ one of] the following:

1. One-piece, bronze ball valve with bronze trim.

2. Two-piece, [full] [regular]-port, bronze ball valves with bronze trim.

END OF SECTION 231113

	FACILITY FUEL-OIL PIPING
	231113 - 1



