Copyright 2011 AIA
MasterSpec Professional
03/11

Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 232113.33 - GROUND-LOOP HEAT-PUMP PIPING
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section includes piping for [horizontal] [vertical], direct-buried, ground-loop, heat-pump systems.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product.

1.3 INFORMATIONAL SUBMITTALS

A. Field quality-control reports.

B. Startup performance results.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 01600 "Product Requirements."

2.1 PIPES AND FITTINGS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Centennial Plastics, LLC.

2. Chevron-Phillips Chemical Company; Performance Pipe Division.

3. Lamson Pipe Company.

4. <Insert manufacturer's name>.

C. HDPE Pipe: ASTM D 3035.

D. Molded PE Fittings: ASTM D 2683 or ASTM D 3261, ASTM F 1055 PE resin, socket, butt-fusion or electro-fusion type, made to match PE pipe dimensions and class.

E. U-Bend Assembly: Factory fabricated with embossed depth stamp every [24 inches (600 mm)] [36 inches (900 mm)] <Insert dimension> from U-bend.

F. Ground-Loop, Heat-Pump Piping Minimum Working Pressure: [160 psig (1100 kPa)] [200 psig (1380 kPa)] <Insert value>.

G. Ground-Loop, Heat-Pump Piping Operating Temperature: Between 23 and 104 deg F (minus 5 and plus 40 deg C).

2.2 BOREHOLE BACKFILL

A. Seal Material: Bentonite clay with thermal conductivity greater than 1.07 Btu/h x sq. ft. x deg F (0.7 W/sq. m x K) according to ASTM D 5334.

B. Permeability: Not more than 1 nm/s according to ASTM D 5084

2.3 ANTIFREEZE SOLUTION

A. Propylene glycol with corrosion inhibitors and environmental stabilizer additives.

PART 3 -  EXECUTION

3.1 EARTHWORK

A. Excavating, trenching, warning tape, and backfilling are specified in Section 312000 "Earth Moving."

3.2 HORIZONTAL PIPING INSTALLATION

A. Separate trenches by 10 feet (3 m) minimum unless otherwise indicated. Remove rocks in trenches that could contact pipe.

B. Backfill

C. Extend pipe from trench onto bottom of body of water at an elevation that is at least 12 inches (300 mm) below frost line. Seal membrane or impervious liner under body of water after installing piping.

D. Install HDPE piping in trenches according to ASTM D 2774 or ASTM F 645.

1. Clean HDPE pipe and fittings and make heat-fusion joints according to ASTM D 2657. Minimize number of joints.

E. Purge, flush, and pressure test piping before backfilling trenches.

F. Install continuous detectable warning tape for underground piping. Locate tape a minimum of [24 inches (600 mm)] <Insert dimension> below finished grade, directly over piping. Underground warning tapes are specified in Section 312000 "Earth Moving."

3.3 VERTICAL PIPING INSTALLATION

A. Install HDPE piping in boreholes according to ASTM D 2774 or ASTM F 645.

1. Clean HDPE pipe and fittings and make heat-fusion joints according to ASTM D 2657. Minimize number of joints.

B. Purge, flush, and pressure test piping before backfilling boreholes.

C. Completely fill the borehole from bottom to top with backfill material.

D. Install the header piping 4 to 6 inches (100 to 150 mm) deep and install the horizontal piping from the header to the boreholes.

E. Extend the horizontal piping and connect to ground-loop heat-pump piping systems at outside face of building wall in locations and pipe sizes indicated.

1. Terminate water-service piping at building wall until building ground-loop heat-pump piping systems are installed. Terminate piping with caps. Make connections to building ground-loop heat-pump piping systems when those systems are installed.

F. Backfill the horizontal piping and header trenches.

G. Fill the entire piping loop with water or antifreeze solution.

H. Maintain records of backfilling on-site.

I. Mark borehole locations, header pipes, and horizontal runs with metallic locator tape as specified in Section 230553 "Identification for HVAC Piping and Equipment."

J. Seal penetrations through building walls.

K. Wall sleeves are specified in Section 230517 "Sleeves and Sleeve Seals for HVAC Piping."

L. Mechanical sleeve seals are specified in Section 230517 "Sleeves and Sleeve Seals for HVAC Piping."

3.4 ANTIFREEZE SOLUTION FILL

A. Fill system with required quantity of propylene glycol and water to provide [minus 10 deg F (minus 23 deg C)] <Insert temperature> freezing temperature.

3.5 CONNECTIONS

A. Drawings indicate general arrangement of piping, fittings, and specialties.

3.6 FIELD QUALITY CONTROL

A. Piping Tests: Fill piping 24 hours before testing and apply test pressure to stabilize piping. Use potable water only.

B. Hydrostatic Tests: Test at not less than 1-1/2 times the pipe working-pressure rating or 300 percent of system design pressure, whichever is more[, allowing for static pressure of borehole depth].

1. Increase pressure in 50-psig (345-kPa) increments and inspect each joint between increments. Hold at test pressure for 30 minutes. Slowly increase to next test pressure increment and hold for 30 minutes. After testing at maximum test pressure, reduce pressure to 30 psig (207 kPa). Hold for 90 minutes, and measure pressure at 30-minute intervals. Repair leaks and retest until no leaks exist.

2. Maintain a minimum pipe velocity of 24 in./s (610 mm/s) for a minimum of 15 minutes to remove all air.

C. Prepare test and inspection reports.

END OF SECTION 232113.33

	GROUND-LOOP HEAT-PUMP PIPING
	232113.33 - 1



