Copyright 2011 AIA
MasterSpec Professional
09/11

Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 232223 - STEAM CONDENSATE PUMPS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

PART 1 -  GENERAL

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

1.1 SUMMARY

A. Section includes steam condensate pumps.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product.

B. Shop Drawings: For each pump.

1. Show pump layout and connections.

2. Include setting drawings with templates for installing foundation and anchor bolts and other anchorages.

3. Include diagrams for power, signal, and control wiring.

1.3 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

2.1 SINGLE-STAGE, CENTRIFUGAL PUMPS WITH FLOOR-MOUNTED RECEIVER

Retain this article for small simplex or duplex pumps with 12,000-sq. ft. EDR (845-kW) maximum capacity and up to 20-psig (140-kPa) discharge pressure.

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Alyan Pump Company; Div. of Hannmann Machinery Systems, Inc.

2. Armstrong Fluid Handling; Div. of Armstrong International, Inc.

3. ITT Corporation; Domestic Pump Division.

4. Nicholson Steam Trap; a division of Spence Engineering Company, Inc.

5. Pentair Pump Group.

6. Roth Pump Company.

7. Skidmore Pump.

8. Spence Engineering Company, Inc.; Division of Circor International, Inc.

9. Spirax-Sarco Inc.

10. Sterling.

11. <Insert manufacturer's name>.

C. Description: Factory-fabricated, packaged, electric-driven pumps; with receiver, pumps, controls, and accessories suitable for operation with steam condensate.

1. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

2. ASME Compliance: Fabricate and label steam condensate receivers to comply with ASME Boiler and Pressure Vessel Code: Section VIII, Division 1.

D. Configuration: [Simplex] [Duplex] floor-mounted pump with receiver and float switches; rated to pump 200 deg F (93 deg C) steam condensate.

E. Receiver:

1. Floor mounted.

2. [Close-grained cast iron] [Welded steel].

3. Externally adjustable float switches.

4. Flanges for pump mounting.

5. Water-level gage and dial thermometer.

6. Pressure gage at pump discharge.

7. Bronze fitting isolation valve between pump and receiver.

8. Lifting eyebolts.

9. Inlet vent and an overflow.

10. Cast-iron inlet strainer with vertical self-cleaning bronze screen and large dirt pocket.

F. Pumps:

1. Centrifugal, close coupled, vertical design.

2. Permanently aligned.

3. Bronze fitted.

4. Replaceable bronze case ring.

5. Mechanical seals rated at 250 deg F (120 deg C).

6. Mounted on receiver flange.

G. Motor:

Default motor characteristics are specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

1. Comply with NEMA designation, temperature rating, service factor, and efficiency requirements for motors specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

Verify enclosure types with manufacturer of specified equipment. Delete "Enclosure" Subparagraph below if included in schedule on Drawings or in "Capacities and Characteristics" Paragraph.

2. Enclosure: [Open, dripproof] [Totally enclosed, fan cooled] [Totally enclosed, air over] [Open, externally ventilated] [Totally enclosed, nonventilated] [Severe duty] [Explosion proof] [Dust-ignition-proof machine].

Retain "Enclosure Materials," "Motor Bearings," "Unusual Service Conditions," "Efficiency," "NEMA Design," and "Service Factor" subparagraphs below if options are available from pump manufacturers and are different from default requirements specified in Section 230513 "Common Motor Requirements for HVAC Equipment." Consider each subparagraph and retain only those that vary from default requirements.

3. Enclosure Materials: [Cast iron] [Cast aluminum] [Rolled steel].

Permanently lubricated ball bearings are available up through 5 hp. Larger motors have grease-lubricated ball bearings.

4. Motor Bearings: [Permanently lubricated] [Grease-lubricated] ball bearings.

5. Unusual Service Conditions:

a. Ambient Temperature: <Insert deg C>.

b. Altitude: <Insert feet (meters)> above sea level.

c. High humidity.

d. <Insert conditions>.

6. Efficiency: Premium efficient.

7. NEMA Design: <Insert designation>.

8. Service Factor: <Insert value>.

H. Control Panel:

1. Factory wired between pumps and float switches, for single external electrical connection.

2. Provide fused, control-power transformer if voltage exceeds 230 V ac.

3. NEMA 250, [Type 1] [Type 3] [Type 12] <Insert type> enclosure with hinged door and grounding lug, mounted on pump.

4. Motor controller for each pump.

Retain first two subparagraphs below for duplex units.

5. Electrical pump alternator to operate pumps in lead-lag sequence and allow both pumps to operate on receiver high level.

6. Manual lead-lag control to override electrical pump alternator and manually select the lead pump.

7. Momentary-contact "TEST" push button on cover for each pump.

8. Numbered terminal strip.

9. Disconnect switch.

If Project has more than one type or configuration of small floor-mounted pump with receiver and float switches, delete "Capacities and Characteristics" Paragraph below and schedule pumps on Drawings.

I. Capacities and Characteristics:

1. Unit Total Capacity: <Insert sq. ft. EDR (kW)>.

2. Capacity, Each Pump:

a. Flow: <Insert gpm (L/s)>.

b. Discharge Head: <Insert psig (kPa)>.

c. Discharge Size: <Insert NPS (DN)>.

d. Speed: <Insert rpm>.

e. Motor Horsepower: <Insert value>.

3. Receiver:

a. Capacity: <Insert gal. (L)>.

b. Inlet Size: <Insert NPS (DN)>.

c. Height to Inlet: <Insert inches (mm)>.

4. Electrical Characteristics:

a. Volts: [120] [230] [240] <Insert value>.

b. Phase: Single.

c. Hertz: 60.

d. Full-Load Amperes: <Insert value>.

e. Minimum Circuit Ampacity: <Insert value>.

f. Maximum Overcurrent Protection: <Insert amperage>.

2.2 TWO-STAGE, CENTRIFUGAL PUMPS WITH FLOOR-MOUNTED RECEIVER

Retain this article for large duplex floor-mounted pumps with approximately 150,000-sq. ft. EDR (10 545-kW) maximum capacity and up to 75-psig (520-kPa) discharge pressure.

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Alyan Pump Company; Div. of Hannmann Machinery Systems, Inc.

2. ITT Corporation; Domestic Pump Division.

3. Nicholson Steam Trap; a division of Spence Engineering Company, Inc.

4. Pentair Pump Group.

5. Roth Pump Company.

6. Skidmore Pump.

7. Spence Engineering Company, Inc.; Division of Circor International, Inc.

8. Spirax-Sarco Inc.

9. Sterling.

10. <Insert manufacturer's name>.

C. Description: Factory-fabricated, packaged, electric-driven pumps; with receiver, pumps, controls, and accessories suitable for operation with steam condensate.

1. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

2. ASME Compliance: Fabricate and label steam condensate receivers to comply with ASME Boiler and Pressure Vessel Code: Section VIII, Division 1.

D. Configuration: Duplex floor-mounted pumps with receiver and float switches; rated to pump minimum 210 deg F (99 deg C) steam condensate with a minimum of 2 feet (6 kPa) of NPSH.

E. Receiver:

1. Floor mounted.

2. [Close-grained cast iron] [Welded steel].

3. Externally adjustable float switches.

4. Flanges for pump mounting.

5. Water-level gage and dial thermometer.

6. Pressure gage at pump discharge.

7. Bronze gate valves between receiver and pump discharge.

8. Lifting eyebolts.

9. Inlet vent and an overflow.

10. Cast-iron inlet strainer with self-cleaning bronze screen, dirt pocket, and cleanout plug on receiver inlet.

F. Pumps:

1. Centrifugal, two stage, close coupled.

2. Vertical design, permanently aligned, and bronze fitted.

3. Axial-flow first-stage bronze impeller.

4. Enclosed second-stage bronze impeller with replaceable bronze case rings.

5. Stainless-steel shafts.

6. Mechanical seals rated at250 deg F (120 deg C).

7. Rated to operate with a minimum of 2 feet (6 kPa) of NPSH.

8. Mounted on receiver flanges.

G. Motor:

Default motor characteristics are specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

1. Comply with NEMA designation, temperature rating, service factor, and efficiency requirements for motors specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

Verify enclosure types with manufacturer of specified equipment. Delete "Enclosure" Subparagraph below if included in schedule on Drawings or in "Capacities and Characteristics" Paragraph.

2. Enclosure: [Open, dripproof] [Totally enclosed, fan cooled] [Totally enclosed, air over] [Open, externally ventilated] [Totally enclosed, nonventilated] [Severe duty] [Explosion proof] [Dust-ignition-proof machine].

Retain "Enclosure Materials," "Motor Bearings," "Unusual Service Conditions," "Efficiency," "NEMA Design," and "Service Factor" subparagraphs below if options are available from pump manufacturers and are different from default requirements specified in Section 230513 "Common Motor Requirements for HVAC Equipment." Consider each subparagraph and retain only those that vary from default requirements.

3. Enclosure Materials: [Cast iron] [Cast aluminum] [Rolled steel].

Permanently lubricated ball bearings are available up through 5 hp. Larger motors have grease-lubricated ball bearings.

4. Motor Bearings: [Permanently lubricated] [Grease-lubricated] ball bearings.

5. Unusual Service Conditions:

a. Ambient Temperature: <Insert deg C>.

b. Altitude: <Insert feet (meters)> above sea level.

c. High humidity.

d. <Insert conditions>.

6. Efficiency: Premium efficient.

7. NEMA Design: <Insert designation>.

8. Service Factor: <Insert value>.

H. Control Panel:

1. Factory wired between pumps and float switches, for single external electrical connection.

2. Provide fused, control-power transformer if voltage exceeds 230 V ac.

3. NEMA 250, [Type 1] [Type 3] [Type 12] <Insert type> enclosure with hinged door and grounding lug, mounted on pump.

4. Motor controller for each pump.

5. Electrical pump alternator to operate pumps in lead-lag sequence and allow both pumps to operate on receiver high level.

6. Manual lead-lag control to override electrical pump alternator and manually select the lead pump.

7. Momentary-contact "TEST" push button on cover for each pump.

8. Numbered terminal strip.

9. Disconnect switch.

If Project has more than one type or configuration of large duplex floor-mounted pump, delete "Capacities and Characteristics" Paragraph below and schedule pumps on Drawings.

I. Capacities and Characteristics:

1. Unit Total Capacity: <Insert sq. ft. EDR (kW)>.

2. Capacity, Each Pump:

a. Flow: <Insert gpm (L/s)>.

b. Discharge Head: <Insert psig (kPa)>.

c. Discharge Size: <Insert NPS (DN)>.

d. Speed: <Insert rpm>.

e. Motor Horsepower: <Insert value>.

3. Receiver:

a. Capacity: <Insert gal. (L)>.

b. Inlet Size: <Insert NPS (DN)>.

c. Height to Inlet: <Insert inches (mm)>.

4. Electrical Characteristics:

a. Volts: [120] [208] [230] [240] [480] <Insert value>.

b. Phase: [Single] [Three].

c. Hertz: 60.

d. Full-Load Amperes: <Insert value>.

e. Minimum Circuit Ampacity: <Insert value>.

f. Maximum Overcurrent Protection: <Insert amperage>.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Install pumps according to HI 1.1-1.2, HI 1.3, and HI 1.4.

B. Install pumps to provide access for periodic maintenance including removing motors, impellers, couplings, and accessories.

C. Support pumps and piping separately so piping is not supported by pumps.

D. Install thermometers and pressure gages.

E. Equipment Mounting:

Retain first subparagraph below to require equipment to be installed on cast-in-place concrete equipment bases.

1. Install pumps on cast-in-place concrete equipment base(s). Comply with requirements for equipment bases and foundations specified in [Section 033000 "Cast-in-Place Concrete."] [Section 033053 "Miscellaneous Cast-in-Place Concrete."]

Retain one of two subparagraphs below if vibration isolation is required. Retain first for projects in seismic areas; retain second for projects not in seismic areas. Indicate vibration isolation and seismic-control device type and minimum deflection in supported equipment schedule on Drawings.

2. Comply with requirements for vibration isolation and seismic control devices specified in Section 220548 "Vibration and Seismic Controls for Plumbing Piping and Equipment"

3. Comply with requirements for vibration isolation devices specified in Section 220548.13 "Vibration Controls for Plumbing Piping and Equipment."

3.2 CONNECTIONS

Coordinate piping installations and specialty arrangements with Drawings and with requirements specified in piping systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Comply with requirements for piping specified in Section 232213 "Steam and Condensate Heating Piping" and Section 232216 "Steam and Condensate Piping Specialties."

B. Where installing piping adjacent to machine, allow space for service and maintenance.

Coordinate first paragraph below with Section 230900 "Instrumentation and Control for HVAC" for controls to provide sufficient back pressure during low-load operations.

C. Install a globe and check valve and pressure gage before inlet of each pump and a gate and check valve at pump outlet.

D. Pipe drain to nearest floor drain for overflow and drain piping connections.

E. Install full-size vent piping to outdoors, terminating in 180-degree elbow at point above highest steam system connection or as indicated.

F. Ground equipment according to Section 260526 "Grounding and Bonding for Electrical Systems."

G. Connect wiring according to Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

END OF SECTION 232223

	STEAM CONDENSATE PUMPS
	232223 - 1



