Copyright 2011 AIA
MasterSpec Professional
09/11

Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 233116 - NONMETAL DUCTS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Fibrous-glass ducts and fittings.

2. Phenolic-foam ducts and fittings.

B. Related Sections:

Retain Sections in subparagraphs below that contain requirements Contractor might expect to find in this Section but are specified in other Sections.

1. Section 230593 "Testing, Adjusting, and Balancing for HVAC" for testing, adjusting, and balancing requirements for nonmetal ducts.

2. Section 233113 "Metal Ducts" for single- and double-wall, rectangular and round ducts.

3. Section 233119 "HVAC Casings" for factory- and field-fabricated casings for mechanical equipment.

4. Section 233300 "Air Duct Accessories" for dampers, duct-mounting access doors and panels, turning vanes, and flexible ducts.

1.2 PERFORMANCE REQUIREMENTS

Retain paragraph below to comply with LEED Prerequisite IEQ 1.

A. Airstream Surfaces: Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1.

1.3 ACTION SUBMITTALS

A. Product Data: For each type of product indicated.

B. LEED Submittals:

1. Product Data for Prerequisite IEQ 1: Documentation indicating that duct systems comply with ASHRAE 62.1, Section 5 - "Systems and Equipment."

2. Product Data for Prerequisite EA 2: Documentation indicating that duct systems comply with ASHRAE/IESNA 90.1, Section 6.4.4 - "HVAC System Construction and Insulation."

Retain first subparagraph below if retaining "Duct Cleaning" Article.

3. Duct-Cleaning Test Report for Prerequisite IEQ 1: Documentation of work performed for compliance with ASHRAE 62.1, Section 7.2.4 - "Ventilation System Start-up."

"Product Data for Credit IEQ 4.1" Subparagraph below applies to LEED-NC, LEED-CI, and LEED-CS; coordinate with requirements for adhesives and sealants.

4. Product Data for Credit IEQ 4.1: For adhesives and sealants, documentation including printed statement of VOC content.

"Laboratory Test Reports for Credit IEQ 4" Subparagraph below applies to LEED for Schools.

5. Laboratory Test Reports for Credit IEQ 4: For adhesives and sealants, documentation indicating that products comply with the testing and product requirements of the California Department of Health Services' "Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers."

C. Shop Drawings:

1. Fabrication, assembly, and installation, including plans, elevations, sections, components, and attachments to other work.

2. Duct layout indicating sizes and pressure classes.

3. Elevation of top of ducts.

4. Dimensions of main duct runs from building grid lines.

5. Fittings.

6. Reinforcement and spacing.

7. Seam and joint construction.

8. Penetrations through fire-rated and other partitions.

9. Equipment installation based on equipment being used on Project.

10. Hangers and supports, including methods for duct and building attachment and vibration isolation.

1.4 INFORMATIONAL SUBMITTALS

Retain paragraph below if Drawings do not include detailed plans or if Project involves unusual coordination requirements.

A. Coordination Drawings: Plans, drawn to scale, on which the following items are shown and coordinated with each other, using input from installers of the items involved:

1. Duct installation in congested spaces, indicating coordination with general construction, building components, and other building services. Indicate proposed changes to duct layout.

2. Suspended ceiling components.

3. Structural members to which duct will be attached.

4. Size and location of initial access modules for acoustical tile.

5. Penetrations of smoke barriers and fire-rated construction.

6. Items penetrating finished ceiling including the following:

a. Lighting fixtures.

b. Air outlets and inlets.

c. Speakers.

d. Sprinklers.

e. Access panels.

f. Perimeter moldings.

g. <Insert item>.

1.5 QUALITY ASSURANCE

Retain first two paragraphs below if applying for LEED certification or if requiring compliance with ASHRAE or ASHRAE/IESNA.

Retain "ASHRAE Compliance" Paragraph below for LEED Prerequisite IEQ 1, which requires compliance with requirements in ASHRAE 62.1.

A. ASHRAE Compliance: Applicable requirements in ASHRAE 62.1, Section 5 - "Systems and Equipment" and Section 7 - "Construction and System Start-up."

Retain "ASHRAE/IESNA Compliance" Paragraph below for LEED Prerequisite EA 2, which requires compliance with requirements in ASHRAE/IESNA 90.1.

B. ASHRAE/IESNA Compliance: Applicable requirements in ASHRAE/IESNA 90.1, Section 6.4.4 - "HVAC System Construction and Insulation."

C. NFPA Compliance:

1. NFPA 90A, "Installation of Air Conditioning and Ventilating Systems."

2. NFPA 90B, "Installation of Warm Air Heating and Air Conditioning Systems."

PART 2 -  PRODUCTS

2.1 FIBROUS-GLASS DUCTS AND FITTINGS

Maximum performance parameters are static-pressure classes from minus 2- to plus 2-inch wg (minus 500 to plus 500 Pa), velocity up to 2400 fpm (12.2 m/s), and leakage class 6 cfm/100 sq. ft. at 1-inch wg (0.29 L/s per sq. m at 250 Pa) with all joints sealed. Fibrous-glass ducts are not appropriate for outdoor installation.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain first paragraph and list of manufacturers below. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1. CertainTeed Corporation; Insulation Group.

2. Johns Manville.

3. Knauf Insulation.

4. Owens Corning.

5. <Insert manufacturer's name>.

B. Fibrous-Glass Duct Materials: Resin-bonded fiberglass, faced on the outside surface with fire-resistive FSK vapor retarder and with a smooth fiberglass mat finish on the air-side surface.

1. Duct Board: Factory molded into rectangular boards.

2. Round Duct: Factory molded into straight round duct and smooth fittings.

3. Temperature Limits: 40 to 250 deg F (5 to 121 deg C) inside ducts; 150 deg F (66 deg C) ambient temperature surrounding ducts.

4. Maximum Thermal Conductivity: [0.24 Btu x in./h x sq. ft. x deg F (0.035 W/m x K)] <Insert conductivity> at 75 deg F (24 deg C) mean temperature.

5. Moisture Absorption: Not exceeding 5 percent by weight at 120 deg F (49 deg C) and 95 percent relative humidity for 96 hours when tested according to ASTM C 1104/C 1104M.

6. Permeability: 0.02 perms (1.15 ng/Pa x s x sq. m) maximum when tested according to ASTM E 96/E 96M, Procedure A.

7. Antimicrobial Agent: Compound shall be tested for efficacy by an NRTL, and registered by the EPA for use in HVAC systems.

8. Noise-Reduction Coefficient: 0.65 minimum when tested according to ASTM C 423, Mounting A.

9. Required Markings: EI rating, UL label, and other markings required by UL 181 on each full sheet of duct board.

C. Closure Materials:

Retain one of three subparagraphs below, or retain all to permit Contractor's choice.

1. Pressure-Sensitive Tape: Comply with UL 181A; imprinted by the manufacturer with the coding "181A-P," the manufacturer's name, and a date code.

a. Tape: Aluminum foil-scrim tape imprinted with listing information.

b. Minimum Tape Width: 2-1/2 inches (64 mm); 3 inches (76 mm) for duct board thicker than 1 inch (25 mm).

c. Staples: 1/2-inch (13-mm) outward clinching, 2 inches (51 mm) o.c. in tabs, one tab per joint.

d. Water resistant.

e. Mold and mildew resistant.

2. Heat-Activated Tape: Comply with UL 181A; imprinted by the manufacturer with the coding "181A-H," the manufacturer's name, and a date code.

a. Tape: Aluminum foil-scrim tape imprinted with listing information.

b. Minimum Tape Width: 3 inches (76 mm).

c. Heat-Sensitive Imprint: Printed indicator on tape to show proper heating during application has been achieved.

d. Water resistant.

e. Mold and mildew resistant.

3. Two-Part Tape Sealing System: Comply with UL 181A; imprinted by the manufacturer with the coding "181A-M," the manufacturer's name, and a date code.

a. Tape: Woven glass fiber impregnated with mineral gypsum.

b. Minimum Tape Width: 3 inches (76 mm).

c. Sealant: Modified styrene acrylic.

d. Water resistant.

e. Mold and mildew resistant.

One or both subparagraphs below may be required to comply with Project requirements or authorities having jurisdiction. Retain first subparagraph below if required for LEED-NC, LEED-CI, or LEED-CS Credit IEQ 4.1.

f. For indoor applications, sealant shall have a VOC content of 250 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

Retain subparagraph below if required for LEED for Schools Credit IEQ 4.

g. Sealant shall comply with the testing and product requirements of the California Department of Health Services' "Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers."

D. Fabrication:

1. Select joints, seams, transitions, elbows, and branch connections and fabricate according to [SMACNA's "Fibrous Glass Duct Construction Standards," Chapter 2, "Specifications and Closure," and Chapter 4, "Fittings and Connections."] [NAIMA AH116, "Fibrous Glass Duct Construction Standards," Section II, "Fabrication of Straight Duct Modules," Section III, "Fabrication of Fittings from Modules or Flat Board," and Section IV, "Closure."]

2. Fabricate 90-degree mitered elbows to include turning vanes.

3. Reinforcements: Comply with requirements in [SMACNA's "Fibrous Glass Duct Construction Standards," Chapter 5, "Reinforcement"] [NAIMA AH116, "Fibrous Glass Duct Construction Standards," Section V, "Reinforcement"] for channel- and tie-rod reinforcement materials, spacing, and fabrication.

Retain subparagraph below for preformed round duct.

4. Preformed Round Duct: Comply with NAIMA AH116, "Fibrous Glass Duct Construction Standards," Section VII, "Preformed Round Duct."

2.2 PHENOLIC-FOAM DUCTS AND FITTINGS

Maximum performance parameters are static-pressure classes from minus 4- to plus 4-inch wg (minus 1000 to plus 1000 Pa), velocity up to 5000 fpm (25 m/s), and leakage class 6 cfm/100 sq. ft. at 1-inch wg (0.29 L/s per sq. m at 250 Pa) with all joints sealed.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain first paragraph and list of manufacturers below. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Knauf has an exclusive agreement with Pal International in Italy to market the KoolDuct System in the U.S.

1. Knauf Insulation.

2. <Insert manufacturer's name>.

B. Duct Panel: CFC-free phenolic-foam bonded on both sides with factory-applied 0.001-inch- (0.025-mm-) thick, aluminum foil reinforced with fiberglass scrim.

1. Maximum Temperature: 158 deg F (70 deg C) inside ducts or ambient temperature surrounding ducts.

2. Maximum Thermal Conductivity: [0.13 Btu x in./h x sq. ft. x deg F (0.019 W/m x K)] <Insert conductivity> at 75 deg F (24 deg C) mean temperature.

3. Permeability: 0.0002 perms (0.0115 ng/Pa x s x sq. m) maximum when tested according to ASTM E 96/E 96M, Procedure A.

4. Antimicrobial Agent: Compound shall be tested for efficacy by an NRTL, and registered by the EPA for use in HVAC systems.

5. Noise-Reduction Coefficient: 0.65 minimum when tested according to ASTM C 423, Mounting A.

6. Required Markings: UL label and other markings required by UL 181 on each full sheet of duct panel; UL ratings for closure materials.

C. Closure Materials:

1. V-Groove Adhesive: Silicone.

One or both subparagraphs below may be required to comply with Project requirements or authorities having jurisdiction. Retain first subparagraph below if required for LEED-NC, LEED-CI, or LEED-CS Credit IEQ 4.1.

a. For indoor applications, sealant shall have a VOC content of 250 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

Retain subparagraph below if required for LEED for Schools Credit IEQ 4.

b. Sealant shall comply with the testing and product requirements of the California Department of Health Services' "Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers."

Retain one of two subparagraphs below, or retain both to permit Contractor's choice.

2. Pressure-Sensitive Tape: Comply with UL 181A; imprinted by the manufacturer with the coding "181A-P," the manufacturer's name, and a date code.

a. Tape: Aluminum foil tape imprinted with listing information.

b. Minimum Tape Width: 3 inches (76 mm).

c. Water resistant.

d. Mold and mildew resistant.

3. Polymeric Sealing System:

a. Structural Membrane: Woven glass fiber.

b. Minimum Tape Width: 3 inches (76 mm).

c. Sealant: Water based.

d. Color: White.

e. Water resistant.

f. Mold and mildew resistant.

One or both subparagraphs below may be required to comply with Project requirements or authorities having jurisdiction. Retain first subparagraph below if required for LEED-NC, LEED-CI, or LEED-CS Credit IEQ 4.1.

g. For indoor applications, sealant shall have a VOC content of 250 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

Retain subparagraph below if required for LEED for Schools Credit IEQ 4.

h. Sealant shall comply with the testing and product requirements of the California Department of Health Services' "Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers."

D. Fabrication:

1. Fabricate joints, seams, transitions, reinforcement, elbows, branch connections, access doors and panels, and damage repairs according to Knauf Insulation's "Knauf KoolDuct System Design Guide," Section 4, "Duct Construction," and Section 5, "Ductwork System General."

2. Fabricate 90-degree mitered elbows to include turning vanes.

2.3 HANGERS AND SUPPORTS

Indicate extent of corrosive environment on Drawings.

A. Hanger Rods for Noncorrosive Environments: Cadmium-plated steel rods and nuts.

B. Hanger Rods for Corrosive Environments: Electrogalvanized, all-thread rods or galvanized rods with threads painted with zinc-chromate primer after installation.

C. Strap and Rod Sizes: Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Table 5-1 (Table 5-1M), "Rectangular Duct Hangers Minimum Size," and Table 5-2, "Minimum Hanger Sizes for Round Duct."

D. Steel Cables: [ASTM A 603, galvanized] [ASTM A 492, stainless] steel with end connections made of cadmium-plated steel assemblies with brackets, swivel, and bolts designed for duct hanger service; with an automatic-locking and clamping device.

E. Duct Attachments: Sheet metal screws, blind rivets, or self-tapping metal screws; compatible with duct materials.

F. Trapeze and Riser Supports: Steel shapes complying with ASTM A 36/A 36M.

PART 3 -  EXECUTION

3.1 DUCT INSTALLATION

A. Install ducts with fewest possible joints.

B. Unless otherwise indicated, install ducts vertically and horizontally, and parallel and perpendicular to building lines.

C. Install ducts close to walls, overhead construction, columns, and other structural and permanent enclosure elements of building.

D. Install ducts with a clearance of 1 inch (25 mm), plus allowance for insulation thickness.

E. Where ducts pass through non-fire-rated interior partitions and exterior walls and are exposed to view, cover the opening between the partition and duct or duct insulation with sheet metal flanges. Overlap openings on four sides by at least 1-1/2 inches (38 mm).

F. Where ducts pass through fire-rated interior partitions and exterior walls, install fire dampers. Comply with requirements in Section 233300 "Air Duct Accessories" for fire and smoke dampers.

G. Protect duct interiors from the moisture, construction debris and dust, and other foreign materials.[ Comply with SMACNA's "IAQ Guidelines for Occupied Buildings Under Construction," Appendix G, "Duct Cleanliness for New Construction Guidelines."]

H. Install fibrous-glass ducts and fittings to comply with [NAIMA AH116, "Fibrous Glass Duct Construction Standards] [SMACNA's "Fibrous Glass Duct Construction Standards]."

I. Install foam ducts and fittings to comply with Knauf Insulation's "Knauf KoolDuct System Design Guide."

3.2 HANGER AND SUPPORT INSTALLATION

A. Install hangers and supports for fibrous-glass ducts and fittings to comply with [SMACNA's "Fibrous Glass Duct Construction Standards," Chapter 6, "Hangers and Supports."] [NAIMA AH116, "Fibrous Glass Duct Construction Standards," Section VI, "Hangers and Supports."]

B. Install hangers and supports for phenolic-foam ducts and fittings to comply with Knauf Insulation's "Knauf KoolDuct System Design Guide," Section 5, "Ductwork System General."

Verify attachment selection in first paragraph below with structural engineer.

C. Building Attachments: Concrete inserts, powder-actuated fasteners, or structural-steel fasteners appropriate for construction materials to which hangers are being attached.

1. Install concrete inserts before placing concrete.

2. Install powder-actuated concrete fasteners after concrete is placed and completely cured.

3. Use powder-actuated concrete fasteners for standard-weight aggregate concretes or for slabs more than 4 inches (100 mm) thick.

4. Do not use powder-actuated concrete fasteners for lightweight-aggregate concretes or for slabs less than 4 inches (100 mm) thick.

D. Install upper attachments to structures. Select and size upper attachments with pull-out, tension, and shear capacities appropriate for supported loads and building materials where used.

3.3 DUCT CLEANING

Retain this article for applications where construction dust and debris in duct system must be removed before air-system operation or if applying for LEED certification.

LEED Prerequisite IEQ 1 requires compliance with ASHRAE 62.1, in which, Section 7.2.4 - "Ventilation System Start-up" requires that distribution systems be clean of dirt and debris.

A. Clean [new] [and] [existing] duct system(s) before testing, adjusting, and balancing.

B. Use service openings for entry and inspection.

1. Create new openings and install access panels appropriate for duct static-pressure class if required for cleaning access. Provide insulated panels for insulated or lined duct. Patch duct as recommended by duct manufacturer. Comply with Section 233300 "Air Duct Accessories" for access panels and doors.

2. Disconnect and reconnect flexible ducts as needed for cleaning and inspection.

3. Remove and reinstall ceiling to gain access during the cleaning process.

C. Particulate Collection and Odor Control:

1. When venting vacuuming system inside the building, use HEPA filtration with 99.97 percent collection efficiency for 0.3-micron-size (or larger) particles.

2. When venting vacuuming system to outdoors, use filter to collect debris removed from HVAC system, and locate exhaust downwind and away from air intakes and other points of entry into building.

D. Clean the following components by removing surface contaminants and deposits:

1. Air outlets and inlets (registers, grilles, and diffusers).

2. Supply, return, and exhaust fans including fan housings, plenums (except ceiling supply and return plenums), scrolls, blades or vanes, shafts, baffles, dampers, and drive assemblies.

3. Air-handling unit internal surfaces and components including mixing box, coil section, air wash systems, spray eliminators, condensate drain pans, humidifiers and dehumidifiers, filters and filter sections, and condensate collectors and drains.

4. Coils and related components.

5. Return-air ducts, dampers, actuators, and turning vanes except in ceiling plenums and mechanical equipment rooms.

6. Supply-air ducts, dampers, actuators, and turning vanes.

7. Dedicated exhaust and ventilation components and makeup air systems.

E. Mechanical Cleaning Methodology:

1. Use vacuum-collection devices that are operated continuously during cleaning. Connect vacuum device to downstream end of duct sections so areas being cleaned are under negative pressure.

2. Use mechanical agitation to dislodge debris adhered to interior duct surfaces without damaging integrity of ducts or duct accessories.

3. Clean fibrous-glass duct with HEPA vacuuming equipment; do not permit duct to get wet. Replace fibrous-glass duct that is damaged, deteriorated, or delaminated or that has friable material, mold, or fungus growth.

4. Clean coils and coil drain pans according to NADCA 1992. Keep drain pan operational. Rinse coils with clean water to remove latent residues and cleaning materials; comb and straighten fins.

5. Provide drainage and cleanup for wash-down procedures.

6. Antimicrobial Agents and Coatings: Apply EPA-registered antimicrobial agents if fungus is present. Apply antimicrobial agents according to manufacturer's written instructions after removal of surface deposits and debris.

3.4 START UP

LEED Prerequisite IEQ 1 requires compliance with ASHRAE 62.1;

A. Air Balance: Comply with requirements in Section 230593 "Testing, Adjusting, and Balancing for HVAC."

3.5 DUCT SCHEDULE

Retain and revise required duct applications in this article. Coordinate with materials specified in Part 2.

LEED Prerequisite EA 2 requires that duct insulation R-value comply with ASHRAE/IESNA 90.1 tables titled "Minimum Duct Insulation R-Value, Cooling and Heating Only Supply Ducts and Return Ducts" and "Minimum Duct Insulation R-Value, Combined Heating and Cooling Supply Ducts and Return Ducts." If using duct material alone to satisfy thermal requirements, verify that material is available in thickness needed to provide thermal performance without jeopardizing other requirements.

A. Indoor Ducts and Fittings:

Retain one or more of three subparagraphs below for materials of ducts to be installed indoors. Indicate materials on Drawings if more than one is required.

1. Fibrous-Glass Rectangular Ducts and Fittings:

Retain first subparagraph below to require minimum flexural rigidity of fibrous-glass ducts. Otherwise, Contractor will select EI rating as part of duct design based on size of ducts and static-pressure class. SMACNA's "Fibrous Glass Duct Construction Standards" does not recognize EI-1400.

a. Minimum Flexural Rigidity: EI-[475] [800] [1400].

Retain first subparagraph below for minimum thermal performance of fibrous-glass ducts. Otherwise, Contractor will select thickness based on structural requirements of ducts. 1-1/2- and 2-inch- (38- and 51-mm-) thick boards below are not available in EI-475.

b. Minimum Board Thickness: [1 inch (25 mm)] [1-1/2 inches (38 mm)] [2 inches (51 mm)].

2. Fibrous-Glass Round Ducts and Fittings:

a. Minimum Thickness: [1 inch (25 mm)] <Insert thickness>.

3. Phenolic-Foam Rectangular Ducts and Fittings:

Retain first subparagraph below for minimum thermal performance of phenolic-foam ducts. Otherwise, Contractor will select thickness based on structural requirements of ducts.

a. Minimum Panel Thickness: [7/8 inch (22 mm)] [1-3/32 inches (28 mm)].

Retain subparagraph below for factory-applied aluminum cladding for indoor installation of ducts exposed to view.

b. Aluminum Cladding: Minimum 0.025 inch (0.635 mm) thick.

B. Outdoor Duct and Fittings:

Retain subparagraph below for materials of ducts to be installed outdoors.

1. Phenolic-Foam Rectangular Ducts and Fittings:

Retain first subparagraph below for minimum thermal performance of phenolic-foam ducts. Otherwise, Contractor will select thickness based on structural requirements of ducts.

a. Minimum Panel Thickness: [7/8 inch (22 mm)] [1-3/32 inches (28 mm)].

Retain one of two subparagraphs below for ducts installed outdoors.

b. Aluminum Cladding: Minimum 0.032 inch (0.813 mm) thick.

c. Polymeric Sealing System: Coat ducts, including gang-nail couplings, grip flanges, and couplings.

END OF SECTION 233116

	NONMETAL DUCTS
	233116 - 1



