Copyright 2011 AIA
MasterSpec Professional
09/11

Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 233416 - CENTRIFUGAL HVAC FANS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes: For each product.

1. Backward-inclined centrifugal fans.

2. Forward-curved centrifugal fans.

1.2 ACTION SUBMITTALS

A. Product Data:

1. Include rated capacities, furnished specialties, and accessories for each fan.

2. Certified fan performance curves with system operating conditions indicated.

3. Certified fan sound-power ratings.

4. Motor ratings and electrical characteristics, plus motor and electrical accessories.

5. Material thickness and finishes, including color charts.

6. Dampers, including housings, linkages, and operators.

B. Shop Drawings:

1. Include plans, elevations, sections, and attachment details.

2. Include details of equipment assemblies. Indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

3. Include diagrams for power, signal, and control wiring.

4. Design Calculations: Calculate requirements for selecting vibration isolators and seismic restraints and for designing vibration isolation bases.

5. Vibration Isolation Base Details: Detail fabrication, including anchorages and attachments to structure and to supported equipment. Include auxiliary motor slides and rails, and base weights.

1.3 INFORMATIONAL SUBMITTALS

Retain "Coordination Drawings" Paragraph below for situations where limited space necessitates maximum utilization for efficient installation of different components or if coordination is required for installation of products and materials by separate installers. Coordinate paragraph with other Sections specifying products listed below. Preparation of coordination drawings requires the participation of each trade involved in installations within the limited space.

A. Coordination Drawings: Show fan room layout and relationships between components and adjacent structural and mechanical elements. Show support locations, type of support, and weight on each support. Indicate and certify field measurements.

Retain "Field quality-control reports" Paragraph below if Contractor is responsible for field quality-control testing and inspecting.

B. Field quality-control reports.

1.4 CLOSEOUT SUBMITTALS

A. Operation and Maintenance Data: For centrifugal fans to include in emergency, operation, and maintenance manuals.

1.5 MAINTENANCE MATERIAL SUBMITTALS

A. Belts: [One] <Insert number> set(s) for each belt-driven unit.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

2.1 PERFORMANCE REQUIREMENTS

AMCA compliance is an optional requirement and not necessarily available from all manufacturers.

A. AMCA Compliance: Comply with AMCA performance requirements and bear the AMCA-Certified Ratings Seal.

If Project has more than one type or configuration of centrifugal fan, delete "Capacities and Characteristics" Paragraph below and schedule fans on Drawings.

B. Capacities and Characteristics:

1. Total Airflow: <Insert cfm (L/s)>.

2. External Static Pressure: <Insert inches wg (Pa)>.

3. Class: [I] [II] [III].

4. Arrangement: <Insert discharge configuration>.

5. Housing Material: [Reinforced steel] [Aluminum] [Stainless steel].

6. Special Housing Coating: [Thermoplastic vinyl] [Epoxy] [Zinc] [Synthetic resin] [Phenolic] [Color-match enamel] [Polytetrafluoroethylene] [Vinyl ester] [Hot-dip galvanized] [Powder-baked enamel]; <Insert manufacturer's name and trade name>.

7. Wheel Size (Diameter): <Insert inches (mm)>.

8. Wheel Material: [Steel] [Aluminum] [Stainless steel].

9. Special Wheel Coating: [Thermoplastic vinyl] [Epoxy] [Zinc] [Synthetic resin] [Phenolic] [Color-match enamel] [Polytetrafluoroethylene] [Vinyl ester] [Hot-dip galvanized] [Powder-baked enamel]; <Insert manufacturer's name and trade name>.

10. Brake Horsepower: <Insert value>.

11. Drive Type: [Belt] [Direct].

12. Fan Rpm: <Insert value>.

13. Outlet Velocity: <Insert fpm (m/s)>.

14. Motor:

Retain "Electrical Characteristics" Subparagraph below if characteristics are not indicated on Drawings.

a. Electrical Characteristics:

1) Motor Size: <Insert horsepower>.

2) Motor Rpm: <Insert value>.

3) Volts: [120] [208] [230] [460] <Insert value>.

4) Phase: [Single] [Poly].

5) Hertz: 60.

6) Full-Load Amperes: <Insert value>.

7) Minimum Circuit Ampacity: <Insert value>.

8) Maximum Overcurrent Protection: <Insert amperage>.

15. Discharge Sound Power:

a. 1st Octave: <Insert dB>.

b. 2nd Octave: <Insert dB>.

c. 3rd Octave: <Insert dB>.

d. 4th Octave: <Insert dB>.

e. 5th Octave: <Insert dB>.

f. 6th Octave: <Insert dB>.

g. 7th Octave: <Insert dB>.

h. 8th Octave: <Insert dB>.

16. Inlet Sound Power:

a. 1st Octave: <Insert dB>.

b. 2nd Octave: <Insert dB>.

c. 3rd Octave: <Insert dB>.

d. 4th Octave: <Insert dB>.

e. 5th Octave: <Insert dB>.

f. 6th Octave: <Insert dB>.

g. 7th Octave: <Insert dB>.

h. 8th Octave: <Insert dB>.

17. Vibration Isolators: [Spring] [Restrained spring] isolators <Insert type> having a static deflection of [1 inch (25 mm)] <Insert deflection>.

18. Spark-Resistance Class: [A] [B] [C].

2.2 BACKWARD-INCLINED CENTRIFUGAL FANS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Review list below if AMCA-certified fans are required; not all manufacturers are AMCA members.

1. Acme Engineering & Mfg. Corp.

2. Aerovent; a Twin City Fan company.

3. Central Blower Company.

4. Chicago Blower Corporation.

5. Cincinnati Fan.

6. CML Northern Blower Inc.

7. Howden Buffalo Inc.

8. Loren Cook Company.

9. New York Blower Company (The).

10. <Insert manufacturer's name>.

C. Description:

1. Factory-fabricated, -assembled, -tested, and -finished, belt-driven centrifugal fans consisting of housing, wheel, fan shaft, bearings, motor, drive assembly, and support structure.

2. Deliver fans as factory-assembled units, to the extent allowable by shipping limitations.

3. Factory-installed and -wired disconnect switch.

D. Housings:

1. Formed panels to make curved-scroll housings with shaped cutoff.

2. Panel Bracing: Steel angle- or channel-iron member supports for mounting and supporting fan scroll, wheel, motor, and accessories.

Split housings in first subparagraph below are an optional configuration.

3. Horizontally split, bolted-flange housing.

4. Spun inlet cone with flange.

5. Outlet flange.

E. Backward-Inclined Wheels:

1. Single-width-single-inlet and double-width-double-inlet construction with curved inlet flange, backplate, backward-inclined blades, and fastened to shaft with set screws.

2. Welded or riveted to flange and backplate; cast-iron or cast-steel hub riveted to backplate.

F. Shafts:

1. Statically and dynamically balanced and selected for continuous operation at maximum rated fan speed and motor horsepower, with adjustable alignment and belt tensioning.

2. Turned, ground, and polished hot-rolled steel with keyway. Ship with protective coating of lubricating oil.

3. Designed to operate at no more than 70 percent of first critical speed at top of fan's speed range.

G. Grease-Lubricated Shaft Bearings:

1. Self-aligning, pillow-block-type, ball or roller bearings with adapter mount and two-piece, cast-iron housing.

H. Belt Drives:

1. Factory mounted, with adjustable alignment and belt tensioning.

2. Service Factor Based on Fan Motor Size: 1.5.

3. Fan Pulleys: Cast iron or cast steel with split, tapered bushing; dynamically balanced at factory.

4. Motor Pulleys: Adjustable pitch for use with motors through 5 hp; fixed pitch for use with larger motors. Select pulley so pitch adjustment is at the middle of adjustment range at fan design conditions.

5. Belts: Oil resistant, nonsparking, and nonstatic; matched sets for multiple belt drives.

6. Belt Guards: Fabricate to comply with OSHA and SMACNA requirements of diamond-mesh wire screen welded to steel angle frame or equivalent, prime coated. Secure to fan or fan supports without short circuiting vibration isolation. Include provisions for adjustment of belt tension, lubrication, and use of tachometer with guard in place.

7. Motor Mount: Adjustable for belt tensioning.

I. Accessories:

Retain "Access for Inspection, Cleaning, and Maintenance" Subparagraph below if applying for LEED certification. LEED Prerequisite EQ 1 requires compliance with ASHRAE 62.1, which includes requirements for equipment access for inspection, cleaning, and maintenance.

1. Access for Inspection, Cleaning, and Maintenance: Comply with requirements in ASHRAE 62.1.

2. Scroll Drain Connection: NPS 1 (DN 25) steel pipe coupling welded to low point of fan scroll.

3. Companion Flanges: Rolled flanges for duct connections of same material as housing.

4. Variable Inlet Vanes: With blades supported at both ends with two permanently lubricated bearings of same material as housing. Variable mechanism terminating in single control lever with control shaft for double-width fans.

5. Discharge Dampers: Assembly with [parallel] [opposed] blades constructed of two plates formed around and to shaft, channel frame, and sealed ball bearings; with blades linked outside of airstream to single control lever of same material as housing.

6. Inlet Screens: Grid screen of same material as housing.

7. Shaft Cooler: Metal disk between bearings and fan wheel, designed to dissipate heat from shaft.

8. Spark-Resistant Construction: AMCA 99.

9. Shaft Seals: Airtight seals installed around shaft on drive side of single-width fans.

10. Weather Cover: Enameled-steel sheet with ventilation slots, bolted to housing.

2.3 FORWARD-CURVED CENTRIFUGAL FANS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

Review list below if AMCA-certified fans are required; not all manufacturers are AMCA members.

1. Acme Engineering & Mfg. Corp.

2. Central Blower Company.

3. Howden Buffalo Inc.

4. Lau Industries.

5. New York Blower Company (The).

6. <Insert manufacturer's name>.

C. Description:

1. Factory-fabricated, -assembled, -tested, and -finished, belt-driven centrifugal fans consisting of housing, wheel, fan shaft, bearings, motor, drive assembly, and support structure.

2. Deliver fans as factory-assembled units, to the extent allowable by shipping limitations.

3. Factory-installed and -wired disconnect switch.

D. Housings:

1. Formed panels to make curved-scroll housings with shaped cutoff.

2. Panel Bracing: Steel angle- or channel-iron member supports for mounting and supporting fan scroll, wheel, motor, and accessories.

Split housings in first subparagraph below are an optional configuration.

3. Horizontally split, bolted-flange housing.

4. Spun inlet cone with flange.

5. Outlet flange.

E. Forward-Curved Wheels:

1. Black-enameled or galvanized-steel construction with inlet flange, backplate, shallow blades with inlet and tip curved forward in direction of airflow.

2. Mechanically secured to flange and backplate; cast-steel hub swaged to backplate and fastened to shaft with set screws.

F. Shafts:

1. Statically and dynamically balanced and selected for continuous operation at maximum rated fan speed and motor horsepower, with adjustable alignment and belt tensioning.

2. Turned, ground, and polished hot-rolled steel with keyway. Ship with protective coating of lubricating oil.

3. Designed to operate at no more than 70 percent of first critical speed at top of fan's speed range.

G. Grease-Lubricated Shaft Bearings:

1. Self-aligning, pillow-block-type, ball or roller bearings with adapter mount and two-piece, cast-iron housing.

H. Belt Drives:

1. Factory mounted, with adjustable alignment and belt tensioning.

2. Service Factor Based on Fan Motor Size: 1.5.

3. Fan Pulleys: Cast iron or cast steel with split, tapered bushing; dynamically balanced at factory.

4. Motor Pulleys: Adjustable pitch for use with motors through 5 hp; fixed pitch for use with larger motors. Select pulley so pitch adjustment is at the middle of adjustment range at fan design conditions.

5. Belts: Oil resistant, nonsparking, and nonstatic; matched sets for multiple belt drives.

6. Belt Guards: Fabricate to comply with OSHA and SMACNA requirements of diamond-mesh wire screen welded to steel angle frame or equivalent, prime coated. Secure to fan or fan supports without short circuiting vibration isolation. Include provisions for adjustment of belt tension, lubrication, and use of tachometer with guard in place.

7. Motor Mount: Adjustable for belt tensioning.

I. Accessories:

Retain "Access for Inspection, Cleaning, and Maintenance" Subparagraph below if applying for LEED certification. LEED Prerequisite EQ 1 requires compliance with ASHRAE 62.1, which includes requirements for equipment access for inspection, cleaning, and maintenance.

1. Access for Inspection, Cleaning, and Maintenance: Comply with requirements in ASHRAE 62.1.

2. Scroll Drain Connection: NPS 1 (DN 25) steel pipe coupling welded to low point of fan scroll.

3. Companion Flanges: Rolled flanges for duct connections of same material as housing.

4. Variable Inlet Vanes: With blades supported at both ends with two permanently lubricated bearings of same material as housing. Variable mechanism terminating in single control lever with control shaft for double-width fans.

5. Discharge Dampers: Assembly with [parallel] [opposed] blades constructed of two plates formed around and to shaft, channel frame, and sealed ball bearings; with blades linked outside of airstream to single control lever of same material as housing.

6. Inlet Screens: Grid screen of same material as housing.

7. Shaft Cooler: Metal disk between bearings and fan wheel, designed to dissipate heat from shaft.

8. Spark-Resistant Construction: AMCA 99.

9. Shaft Seals: Airtight seals installed around shaft on drive side of single-width fans.

10. Weather Cover: Enameled-steel sheet with ventilation slots, bolted to housing.

2.4 SOURCE QUALITY CONTROL

Sound-power rating information may only be available from manufacturers on request. See discussion on sound and vibration control in the Evaluations.

A. Sound-Power Level Ratings: Comply with AMCA 301, "Methods for Calculating Fan Sound Ratings from Laboratory Test Data." Factory test fans according to AMCA 300, "Reverberant Room Method for Sound Testing of Fans." Label fans with the AMCA-Certified Ratings Seal.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Install centrifugal fans level and plumb.

B. Disassemble and reassemble units, as required for moving to the final location, according to manufacturer's written instructions.

C. Lift and support units with manufacturer's designated lifting or supporting points.

D. Equipment Mounting:

Retain first subparagraph below to require equipment to be installed on cast-in-place concrete equipment bases.

1. Install centrifugal fans on cast-in-place concrete equipment base(s). Comply with requirements for equipment bases and foundations specified in [Section 033000 "Cast-in-Place Concrete."] [Section 033053 "Miscellaneous Cast-in-Place Concrete."]

Retain one of two subparagraphs below. Retain first for projects in seismic areas; retain second for projects not in seismic areas. Indicate vibration isolation and seismic-control device type and minimum deflection in supported equipment schedule on Drawings.

2. Comply with requirements for vibration isolation and seismic control devices specified in Section 230548 "Vibration and Seismic Controls for HVAC."

3. Comply with requirements for vibration isolation devices specified in Section 230548.13 "Vibration Controls for HVAC."

Retain "Curb Support" Paragraph below if curbs are furnished with centrifugal fans for rooftop installations; delete if units are installed on field-fabricated curbs or pilings.

E. Curb Support: Install roof curb on roof structure, level and secure, according to "The NRCA Roofing and Waterproofing Manual," Low-Slope Membrane Roofing Construction Details Section, Illustration "Raised Curb Detail for Rooftop Air Handling Units and Ducts." Install and secure centrifugal fans on curbs, and coordinate roof penetrations and flashing with roof construction.[ Secure units to curb support with anchor bolts.]

F. Unit Support: Install centrifugal fans level on structural [curbs] [pilings]. Coordinate wall penetrations and flashing with wall construction.[ Secure units to structural support with anchor bolts.]

Retain "Isolation Curb Support" Paragraph below for units mounted on isolation curbs.

G. Isolation Curb Support: Install centrifugal fans on isolation curbs, and install[ flexible duct connectors] and vibration isolation and seismic-control devices.

1. Comply with requirements in Section 233300 "Air Duct Accessories" for flexible duct connectors.

2. Comply with requirements in [Section 230548 "Vibration and Seismic Controls for HVAC"] [Section 230548.13 "Vibration Controls for HVAC"] for vibration isolation[ and seismic-control] devices.

H. Install units with clearances for service and maintenance.

I. Label fans according to requirements specified in Section 230553 "Identification for HVAC Piping and Equipment."

3.2 CONNECTIONS

Coordinate duct installations and specialty arrangements with Drawings and with requirements specified in duct systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Drawings indicate general arrangement of ducts and duct accessories. Make final duct connections with flexible connectors. Flexible connectors are specified in Section 233300 "Air Duct Accessories."

B. Install ducts adjacent to fans to allow service and maintenance.

Retain paragraph below if fans have scroll drains.

C. Install piping from scroll drain connection, with trap with seal equal to 1.5 times specified static pressure, to nearest floor drain with pipe sizes matching the drain connection.

3.3 FIELD QUALITY CONTROL

Retain "Perform the following tests and inspections" Paragraph below to require Contractor to perform tests and inspections.

A. Perform the following tests and inspections[ with the assistance of a factory-authorized service representative]:

1. Verify that shipping, blocking, and bracing are removed.

2. Verify that unit is secure on mountings and supporting devices and that connections to ducts and electrical components are complete. Verify that proper thermal-overload protection is installed in motors, starters, and disconnect switches.

3. Verify that cleaning and adjusting are complete.

4. Disconnect fan drive from motor, verify proper motor rotation direction, and verify fan wheel free rotation and smooth bearing operation. Reconnect fan drive system, align and adjust belts, and install belt guards.

5. Adjust belt tension.

6. Adjust damper linkages for proper damper operation.

7. Verify lubrication for bearings and other moving parts.

8. Verify that manual and automatic volume control and fire and smoke dampers in connected ductwork systems are in fully open position.

9. See Section 230593 "Testing, Adjusting, and Balancing For HVAC" for testing, adjusting, and balancing procedures.

10. Remove and replace malfunctioning units and retest as specified above.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

B. Test and adjust controls and safeties. Controls and equipment will be considered defective if they do not pass tests and inspections.

C. Prepare test and inspection reports.

END OF SECTION 233416

	CENTRIFUGAL HVAC FANS
	233416 - 1



