Copyright 2011 AIA
MasterSpec Professional
09/11

Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 233423 - HVAC POWER VENTILATORS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Centrifugal roof ventilators.

2. Centrifugal wall ventilators.

3. Ceiling-mounted ventilators.

4. In-line centrifugal fans.

5. Propeller fans.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product indicated.

B. Shop Drawings: Include plans, elevations, sections, details, and attachments to other work.

1. Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

2. Wiring Diagrams: For power, signal, and control wiring.

3. Vibration Isolation Base Details: Detail fabrication including anchorages and attachments to structure and to supported equipment. Include adjustable motor bases, rails, and frames for equipment mounting.

4. Design Calculations: Calculate requirements for selecting vibration isolators[ and seismic restraints] and for designing vibration isolation bases.

1.3 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

1.4 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

AMCA compliance in paragraph below is an optional requirement and not necessarily available from all manufacturers.

B. AMCA Compliance: Fans shall have AMCA-Certified performance ratings and shall bear the AMCA-Certified Ratings Seal.

PART 2 -  PRODUCTS

2.1 CENTRIFUGAL ROOF VENTILATORS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

If retaining first paragraph below, retain option if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

Review list below if AMCA-certified fans are required; not all manufacturers are AMCA members.

1. Acme Engineering & Manufacturing Corporation.

2. Aerovent; a division of Twin City Fan Companies, Ltd.

3. American Coolair Corporation.

4. Ammerman; Millennium Equipment.

5. Breidert Air Products.

6. Broan-NuTone LLC.

7. Broan-NuTone LLC; NuTone Inc.
8. Carnes Company.

9. Central Blower Company.

10. Delhi Industries Inc.

11. Greenheck Fan Corporation.

12. Hartzell Fan Incorporated.

13. JencoFan.

14. Loren Cook Company.

15. PennBarry.

16. Quietaire Inc.

17. W.W. Grainger, Inc.; Dayton Products.

18. <Insert manufacturer's name>.

Painted galvanized-steel and fiberglass housings are also available from some manufacturers.

C. Housing: Removable, [spun-aluminum, dome top and outlet baffle] [extruded-aluminum, rectangular top] [galvanized steel, mushroom-domed top]; square, one-piece, aluminum base with venturi inlet cone.

1. Upblast Units: Provide spun-aluminum discharge baffle to direct discharge air upward, with rain and snow drains[ and grease collector].

2. Hinged Subbase: Galvanized-steel hinged arrangement permitting service and maintenance.

D. Fan Wheels: Aluminum hub and wheel with backward-inclined blades.

Retain "Belt Drives" Paragraph below if belt-driven fans are required; delete if only direct-drive fans are required.

E. Belt Drives:

1. Resiliently mounted to housing.

2. Fan Shaft: Turned, ground, and polished steel; keyed to wheel hub.

3. Shaft Bearings: Permanently lubricated, permanently sealed, self-aligning ball bearings.

4. Pulleys: Cast-iron, adjustable-pitch motor pulley.

5. Fan and motor isolated from exhaust airstream.

F. Accessories:

Accessories listed in subparagraphs below are optional features.

1. Variable-Speed Controller: Solid-state control to reduce speed from 100 to less than 50 percent.

2. Disconnect Switch: Nonfusible type, with thermal-overload protection mounted [inside] [outside] fan housing, factory wired through an internal aluminum conduit.

3. Bird Screens: Removable, 1/2-inch (13-mm) mesh, aluminum or brass wire.

4. Dampers: Counterbalanced, parallel-blade, backdraft dampers mounted in curb base; factory set to close when fan stops.

5. Motorized Dampers: Parallel-blade dampers mounted in curb base with electric actuator; wired to close when fan stops.

Specify site-fabricated roof curbs in Section 077200 "Roof Accessories." Retain first paragraph below to require roof curbs to be provided by fan manufacturer.

G. Roof Curbs: Galvanized steel; mitered and welded corners; 1-1/2-inch- (40-mm-) thick, rigid, fiberglass insulation adhered to inside walls; and 1-1/2-inch (40-mm) wood nailer. Size as required to suit roof opening and fan base.

1. Configuration: [Self-flashing without a cant strip, with mounting flange] [Built-in cant and mounting flange] [Built-in raised cant and mounting flange].

Coordinate curb height with roof deck construction and insulation thickness; other heights are available. 16-inch (400-mm) height in first subparagraph below is for sound curb.

2. Overall Height: [8 inches (200 mm)] [9-1/2 inches (240 mm)] [12 inches (300 mm)] [16 inches (400 mm)] [18 inches (450 mm)].

Subparagraphs below are optional features.

3. Sound Curb: Curb with sound-absorbing insulation.

4. Pitch Mounting: Manufacture curb for roof slope.

5. Metal Liner: Galvanized steel.

6. Burglar Bars: [1/2-inch- (13-mm-)] [5/8-inch- (16-mm-)] [3/4-inch- (19-mm-)] thick steel bars welded in place to form 6-inch (150-mm) squares.

7. Mounting Pedestal: Galvanized steel with removable access panel.

8. Vented Curb: Unlined with louvered vents in vertical sides.

If Project has more than one type or configuration of centrifugal roof ventilator, delete paragraph below and schedule ventilators on Drawings.

H. Capacities and Characteristics:

1. Airflow: <Insert cfm (L/s)>.

2. External Static Pressure: <Insert inches wg (Pa)>.

3. Fan Diameter: <Insert inches (mm)>.

4. Drive Arrangement: [Direct] [Belt drive].

5. Fan rpm: <Insert value>.

6. Tip Speed: <Insert fpm (m/s)>.

7. Sound: <Insert sone>.

8. Curb Size: <Insert inches by inches (mm by mm)>.

9. Curb Height: <Insert inches (mm)>.

10. Damper: [Yes] [No].

11. Damper Size: <Insert inches by inches (mm by mm)>.

12. Brake Horsepower: <Insert value>.

13. Motor Size: <Insert value> hp.

14. Motor rpm: <Insert value>.

15. Electrical Characteristics:

a. Volts: <Insert value>.

b. Phase: <Insert value>.

c. Hertz: <Insert value>.

2.2 CENTRIFUGAL WALL VENTILATORS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

If retaining first paragraph below, retain option if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

Review list below if AMCA-certified fans are required; not all manufacturers are AMCA members.

1. Acme Engineering & Manufacturing Corporation.

2. Aerovent; a division of Twin City Fan Companies, Ltd.

3. American Coolair Corporation.

4. Ammerman; Millennium Equipment.

5. Breidert Air Products.

6. Broan-NuTone LLC.

7. Broan-NuTone LLC; NuTone Inc.

8. Carnes Company.

9. Greenheck Fan Corporation.

10. Hartzell Fan Incorporated.

11. JencoFan.

12. Loren Cook Company.

13. PennBarry.

14. W.W. Grainger, Inc.; Dayton Products.

15. <Insert manufacturer's name>.

Galvanized-steel and fiberglass housings are also available from some manufacturers.

C. Housing: Heavy-gage, removable, spun-aluminum, dome top and outlet baffle; venturi inlet cone.

D. Fan Wheel: Aluminum hub and wheel with backward-inclined blades.

Retain "Belt Drives" Paragraph below if belt-driven fans are required; delete if only direct-drive fans are required.

E. Belt Drives:

1. Resiliently mounted to housing.

2. Fan Shaft: Turned, ground, and polished steel; keyed to wheel hub.

3. Shaft Bearings: Permanently lubricated, permanently sealed, self-aligning ball bearings.

4. Pulleys: Cast-iron, adjustable-pitch motor pulley.

5. Fan and motor isolated from exhaust airstream.

F. Accessories:

Accessories listed in subparagraphs below are optional features.

1. Variable-Speed Controller: Solid-state control to reduce speed from 100 to less than 50 percent.

2. Disconnect Switch: Nonfusible type, with thermal-overload protection mounted inside fan housing, factory wired through internal aluminum conduit.

3. Bird Screens: Removable, 1/2-inch (13-mm) mesh, aluminum or brass wire.

4. Wall Grille: Ring type for flush mounting.

5. Dampers: Counterbalanced, parallel-blade, backdraft dampers mounted in wall sleeve; factory set to close when fan stops.

6. Motorized Dampers: Parallel-blade dampers mounted in curb base with electric actuator; wired to close when fan stops.

If Project has more than one type or configuration of centrifugal wall ventilator, delete paragraph below and schedule ventilators on Drawings.

G. Capacities and Characteristics:

1. Airflow: <Insert cfm (L/s)>.

2. External Static Pressure: <Insert inches wg (Pa)>.

3. Fan Diameter: <Insert inches (mm)>.

4. Drive Arrangement: [Direct] [Belt drive].

5. Fan rpm: <Insert value>.

6. Tip Speed: <Insert fpm (m/s)>.

7. Sound: <Insert sone>.

8. Damper: [Yes] [No].

9. Damper Size: <Insert inches by inches (mm by mm)>.

10. Brake Horsepower: <Insert value>.

11. Motor Size: <Insert value> hp.

12. Motor rpm: <Insert value>.

13. Electrical Characteristics:

a. Volts: <Insert value>.

b. Phase: <Insert value>.

c. Hertz: <Insert value>.

2.3 CEILING-MOUNTED VENTILATORS

These units are factory assembled with one or more centrifugal wheels up to 12 inches (300 mm) wide, directly connected to motor, enclosed in housing, with inlet grille and integral backdraft damper; AMCA rated.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

If retaining first paragraph below, retain option if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

Review list below if AMCA-certified fans are required; not all manufacturers are AMCA members.

1. American Coolair Corporation.

2. Ammerman; Millennium Equipment.

3. Breidert Air Products.

4. Broan-NuTone LLC.

5. Broan-NuTone LLC; NuTone Inc.

6. Carnes Company.

7. FloAire.

8. Greenheck Fan Corporation.

9. JencoFan.

10. Loren Cook Company.

11. PennBarry.

12. W.W. Grainger, Inc.; Dayton Products.

13. <Insert manufacturer's name>.

C. Housing: Steel, lined with acoustical insulation.

D. Fan Wheel: Centrifugal wheels directly mounted on motor shaft. Fan shrouds, motor, and fan wheel shall be removable for service.

Grille designs other than those specified in first paragraph below are available.

E. Grille: [Plastic] [Stainless steel] [Aluminum] [Painted aluminum], louvered grille with flange on intake and thumbscrew attachment to fan housing.

F. Electrical Requirements: Junction box for electrical connection on housing and receptacle for motor plug-in.

G. Accessories:

Accessories listed in subparagraphs below are optional features.

1. Variable-Speed Controller: Solid-state control to reduce speed from 100 to less than 50 percent.

2. Manual Starter Switch: Single-pole rocker switch assembly with cover and pilot light.

3. Time-Delay Switch: Assembly with single-pole rocker switch, timer, and cover plate.

4. Motion Sensor: Motion detector with adjustable shutoff timer.

5. Ceiling Radiation Damper: Fire-rated assembly with ceramic blanket, stainless-steel springs, and fusible link.

6. Filter: Washable aluminum to fit between fan and grille.

7. Isolation: Rubber-in-shear vibration isolators.

8. Manufacturer's standard roof jack or wall cap, and transition fittings.

If Project has more than one type or configuration of ceiling-mounted ventilator, delete paragraph below and schedule ventilators on Drawings.

H. Capacities and Characteristics:

1. Airflow: <Insert cfm (L/s)>.

2. External Static Pressure: <Insert inches wg (Pa)>.

3. Sound: <Insert sone>.

4. Motor Size: <Insert value> hp.

5. Motor rpm: <Insert value>.

6. Electrical Characteristics:

a. Volts: <Insert value>.

b. Phase: <Insert value>.

c. Hertz: <Insert value>.

2.4 IN-LINE CENTRIFUGAL FANS

These fans are both belt driven and direct drive, usually with spun-aluminum housings, and are used for small ventilation requirements.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

If retaining first paragraph below, retain option if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

Review list below if AMCA-certified fans are required; not all manufacturers are AMCA members.

1. Acme Engineering & Manufacturing Corporation.

2. American Coolair Corporation.

3. Ammerman; Millennium Equipment.

4. Breidert Air Products.

5. Carnes Company.

6. FloAire.

7. Greenheck Fan Corporation.

8. Hartzell Fan Incorporated.

9. JencoFan.

10. Loren Cook Company.

11. Madison Manufacturing.

12. PennBarry.

13. Quietaire Inc.

14. <Insert manufacturer's name>.

C. Housing: Split, spun aluminum with aluminum straightening vanes, inlet and outlet flanges, and support bracket adaptable to floor, side wall, or ceiling mounting.

D. Direct-Drive Units: Motor mounted in airstream, factory wired to disconnect switch located on outside of fan housing[; with wheel, inlet cone, and motor on swing-out service door].

E. Belt-Driven Units: Motor mounted on adjustable base, with adjustable sheaves, enclosure around belts within fan housing, and lubricating tubes from fan bearings extended to outside of fan housing.

F. Fan Wheels: Aluminum, airfoil blades welded to aluminum hub.

G. Accessories:

Accessories listed in subparagraphs below are optional features.

1. Variable-Speed Controller: Solid-state control to reduce speed from 100 to less than 50 percent.

2. Volume-Control Damper: Manually operated with quadrant lock, located in fan outlet.

3. Companion Flanges: For inlet and outlet duct connections.

4. Fan Guards: 1/2- by 1-inch (13- by 25-mm) mesh of galvanized steel in removable frame. Provide guard for inlet or outlet for units not connected to ductwork.

5. Motor and Drive Cover (Belt Guard): Epoxy-coated steel.

If Project has more than one type or configuration of in-line centrifugal fan, delete paragraph below and schedule fans on Drawings.

H. Capacities and Characteristics:

1. Airflow: <Insert cfm (L/s)>.

2. External Static Pressure: <Insert inches wg (Pa)>.

3. Fan Diameter: <Insert inches (mm)>.

4. Wheel Type: [Backward inclined] [Forward curved] [Airfoil].

5. Class: [I] [II] [III].

6. Drive Arrangement: <Insert AMCA number>.

7. Fan rpm: <Insert value>.

8. Outlet Velocity: <Insert fpm (m/s)>.

9. Brake Horsepower: <Insert value>.

10. Motor Size: <Insert value> hp.

11. Electrical Characteristics:

a. Volts: <Insert value>.

b. Phase: <Insert value>.

c. Hertz: <Insert value>.

12. Vibration Isolators:

a. Type: [Elastomeric hangers] <Insert type>.

b. Static Deflection: [1 inch (25 mm)] <Insert value>.

13. Spark Arrestance Class: [A] [B] [C].

2.5 PROPELLER FANS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

If retaining first paragraph below, retain option if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

Review list below if AMCA-certified fans are required; not all manufacturers are AMCA members.

1. Acme Engineering & Manufacturing Corporation.

2. Aerovent; a division of Twin City Fan Companies, Ltd.

3. Airmaster Fan Company.

4. American Coolair Corporation.

5. Ammerman; Millennium Equipment.

6. Breidert Air Products.

7. Broan-NuTone LLC; NuTone Inc.

8. Carnes Company.

9. Chicago Blower Corporation.

10. Cincinnati Fan.

11. Hartzell Fan Incorporated.

12. Howden Buffalo Inc.

13. JencoFan.

14. King Company; part of Mestek, Inc.

15. Loren Cook Company.

16. Madison Manufacturing.

17. Moffitt Corporation Inc.

18. New York Blower Company (The).

19. PennBarry.

20. Quietaire Inc.

21. Stanley Fans.

22. W.W. Grainger, Inc.; Dayton Products.

23. <Insert manufacturer's name>.

C. Housing: Galvanized-steel sheet with flanged edges and integral orifice ring with baked-enamel finish coat applied after assembly.

Retain one of first two paragraphs below. Aluminum blades are normally used in large sizes and in high-static-pressure applications.

D. Steel Fan Wheels: Formed-steel blades riveted to heavy-gage steel spider bolted to cast-iron hub.

E. Fan Wheel: Replaceable, [cast] [extruded]-aluminum, airfoil blades fastened to cast-aluminum hub; factory set pitch angle of blades.

Retain one of two "Fan Drive" paragraphs below.

F. Fan Drive: Motor mounted in airstream, factory wired to disconnect switch located on outside of fan housing.

G. Fan Drive:

1. Resiliently mounted to housing.

2. Statically and dynamically balanced.

3. Selected for continuous operation at maximum rated fan speed and motor horsepower, with final alignment and belt adjustment made after installation.

4. Extend grease fitting to accessible location outside of unit.

5. Service Factor Based on Fan Motor Size: 1.4.

6. Fan Shaft: Turned, ground, and polished steel; keyed to wheel hub.

7. Shaft Bearings: Permanently lubricated, permanently sealed, self-aligning ball bearings.

a. Ball-Bearing Rating Life: ABMA 9, [L10 of 100,000 hours] <Insert life>.

8. Pulleys: Cast iron with split, tapered bushing; dynamically balanced at factory.

9. Motor Pulleys: Adjustable pitch for use with motors through [5] <insert value> hp; fixed pitch for use with larger motors. Select pulley so pitch adjustment is at the middle of adjustment range at fan design conditions.

10. Belts: Oil resistant, nonsparking, and nonstatic; matched sets for multiple belt drives.

11. Belt Guards: Fabricate of steel for motors mounted on outside of fan cabinet.

H. Accessories:

Accessories listed in subparagraphs below are optional features.

1. Gravity Shutters: Aluminum blades in aluminum frame; interlocked blades with nylon bearings.

2. Motor-Side Back Guard: Galvanized steel, complying with OSHA specifications, removable for maintenance.

3. Wall Sleeve: Galvanized steel to match fan and accessory size.

4. Weathershield Hood: Galvanized steel to match fan and accessory size.

5. Weathershield Front Guard: Galvanized steel with expanded metal screen.

6. Variable-Speed Controller: Solid-state control to reduce speed from 100 to less than 50 percent.

7. Disconnect Switch: Nonfusible type, with thermal-overload protection mounted inside fan housing, factory wired through an internal aluminum conduit.

If Project has more than one type or configuration of propeller fan, delete paragraph below and schedule fans on Drawings.

I. Capacities and Characteristics:

1. Airflow: <Insert cfm (L/s)>.

2. Fan Diameter: <Insert inches (mm)>.

3. Fan rpm: <Insert value>.

4. Brake Horsepower: <Insert value>.

5. Motor Size: <Insert value> hp.

6. Electrical Characteristics:

a. Volts: <Insert value>.

b. Phase: <Insert value>.

c. Hertz: <Insert value>.

7. Vibration Isolators:

a. Type: [Elastomeric hangers] [Spring isolators] [Restrained spring isolators] <Insert type>.

b. Static Deflection: [1 inch (25 mm)] <Insert value>.

8. Spark Arrestance Class: [A] [B] [C].

2.6 MOTORS

Default motor characteristics are specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

A. Comply with NEMA designation, temperature rating, service factor, enclosure type, and efficiency requirements for motors specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

1. Motor Sizes: Minimum size as indicated. If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

Retain paragraph below if enclosure type is not open dripproof.

B. Enclosure Type: Totally enclosed, fan cooled.

2.7 SOURCE QUALITY CONTROL

Sound-power rating information may only be available from manufacturers on request. See discussion on sound and vibration control in the Evaluations.

A. Certify sound-power level ratings according to AMCA 301, "Methods for Calculating Fan Sound Ratings from Laboratory Test Data." Factory test fans according to AMCA 300, "Reverberant Room Method for Sound Testing of Fans." Label fans with the AMCA-Certified Ratings Seal.

B. Certify fan performance ratings, including flow rate, pressure, power, air density, speed of rotation, and efficiency by factory tests according to AMCA 210, "Laboratory Methods of Testing Fans for Aerodynamic Performance Rating." Label fans with the AMCA-Certified Ratings Seal.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Equipment Mounting:

Retain first subparagraph below to require equipment to be installed on cast-in-place concrete equipment bases.

1. Install power ventilators on cast-in-place concrete equipment base(s). Comply with requirements for equipment bases and foundations specified in [Section 033000 "Cast-in-Place Concrete."] [Section 033053 "Miscellaneous Cast-in-Place Concrete."]

Retain one of two subparagraphs below. Retain first for projects in seismic areas; retain second for projects not in seismic areas. Indicate vibration isolation and seismic-control device type and minimum deflection in supported equipment schedule on Drawings.

2. Comply with requirements for vibration isolation and seismic control devices specified in Section 230548 "Vibration and Seismic Controls for HVAC."

3. Comply with requirements for vibration isolation devices specified in Section 230548.13 "Vibration Controls for HVAC."

B. Secure roof-mounted fans to roof curbs with cadmium-plated hardware. See Section 077200 "Roof Accessories" for installation of roof curbs.

C. Ceiling Units: Suspend units from structure; use steel wire or metal straps.

Retain and revise first paragraph below for suspended units; delete if vibration and seismic controls are specified in "Capacities and Characteristics" paragraphs or are indicated on Drawings. If not scheduled, identify required vibration- and seismic-control device by using the titles of devices described in Section 230548 "Vibration and Seismic Controls for HVAC Piping and Equipment" and identify required static deflection.

D. Support suspended units from structure using threaded steel rods and [elastomeric hangers] [spring hangers] [spring hangers with vertical-limit stops] <Insert device> having a static deflection of [1 inch (25 mm)] <Insert deflection>. Vibration-control devices are specified in [Section 230548 "Vibration and Seismic Controls for HVAC."] [Section 230548.13 "Vibration Controls for HVAC."]

E. Install units with clearances for service and maintenance.

F. Label units according to requirements specified in Section 230553 "Identification for HVAC Piping and Equipment."

3.2 CONNECTIONS

Coordinate duct installation and specialty arrangements with schematics on Drawings and with requirements specified in duct systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Drawings indicate general arrangement of ducts and duct accessories. Make final duct connections with flexible connectors. Flexible connectors are specified in Section 233300 "Air Duct Accessories."

B. Install ducts adjacent to power ventilators to allow service and maintenance.

C. Ground equipment according to Section 260526 "Grounding and Bonding for Electrical Systems."

D. Connect wiring according to Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

3.3 FIELD QUALITY CONTROL

A. Perform tests and inspections.

Retain subparagraph below to require a factory-authorized service representative to assist Contractor with inspections, tests, and adjustments.

1. Manufacturer's Field Service: Engage a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

B. Tests and Inspections:

1. Verify that shipping, blocking, and bracing are removed.

2. Verify that unit is secure on mountings and supporting devices and that connections to ducts and electrical components are complete. Verify that proper thermal-overload protection is installed in motors, starters, and disconnect switches.

3. Verify that cleaning and adjusting are complete.

4. Disconnect fan drive from motor, verify proper motor rotation direction, and verify fan wheel free rotation and smooth bearing operation. Reconnect fan drive system, align and adjust belts, and install belt guards.

5. Adjust belt tension.

6. Adjust damper linkages for proper damper operation.

7. Verify lubrication for bearings and other moving parts.

8. Verify that manual and automatic volume control and fire and smoke dampers in connected ductwork systems are in fully open position.

9. Disable automatic temperature-control operators, energize motor and adjust fan to indicated rpm, and measure and record motor voltage and amperage.

10. Shut unit down and reconnect automatic temperature-control operators.

11. Remove and replace malfunctioning units and retest as specified above.

C. Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.

D. Prepare test and inspection reports.

3.4 ADJUSTING

A. Adjust damper linkages for proper damper operation.

B. Adjust belt tension.

C. Comply with requirements in Section 230593 "Testing, Adjusting, and Balancing for HVAC" for testing, adjusting, and balancing procedures.

D. Replace fan and motor pulleys as required to achieve design airflow.

E. Lubricate bearings.

END OF SECTION 233423

	HVAC POWER VENTILATORS
	233423 - 1



