Copyright 2010 AIA
MasterSpec Professional
12/10

Copyright 2010 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 233723 - HVAC GRAVITY VENTILATORS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Louvered-penthouse ventilators.

2. Roof hoods.

1.2 PERFORMANCE REQUIREMENTS

A. Structural Performance: Ventilators shall withstand the effects of gravity loads and the following loads and stresses within limits and under conditions indicated without permanent deformation of ventilator components, noise or metal fatigue caused by ventilator blade rattle or flutter, or permanent damage to fasteners and anchors. Wind pressures shall be considered to act normal to the face of the building.

Indicate pressures on appropriate elevation Drawings. Verify compliance with codes. See Evaluations.

1. Wind Loads: Determine loads based on pressures as indicated on Drawings.

Retain paragraph below with "Seismic Qualification Certificates" Paragraph in "Informational Submittals" Article for projects requiring seismic design. Model building codes and ASCE/SEI 7 establish criteria for buildings subject to earthquake motions. Verify requirements of authorities having jurisdiction.

B. Seismic Performance: Ventilators, including attachments to other construction, shall withstand the effects of earthquake motions determined according to [ASCE/SEI 7] <Insert requirement>.

Retain subparagraph below to define the term "withstand" as it applies to this Project. Definition varies with type of building and occupancy and is critical to valid certification. Option is used for essential facilities where equipment must operate immediately after an earthquake.

1. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified[ and the unit will be fully operational after the seismic event]."

1.3 ACTION SUBMITTALS

A. Product Data: For each type of product indicated.

B. LEED Submittals:

1. Product Data for Prerequisite IEQ 1: Documentation indicating that units comply with ASHRAE 62.1, Section 5 - "Systems and Equipment."

C. Shop Drawings: For gravity ventilators. Include plans, elevations, sections, details, ventilator attachments to curbs, and curb attachments to roof structure.

First paragraph below assumes manufacturer's standard-size Samples are acceptable. Revise to suit Project.

D. Samples: For each exposed product and for each color and texture specified.

Paragraph below is defined in Section 013300 "Submittal Procedures" as a "Delegated-Design Submittal." Retain if Work of this Section is required to withstand specific design loads and design responsibilities have been delegated to Contractor or if structural data are required as another way to verify compliance with performance requirements. Professional engineer qualifications are specified in Section 014000 "Quality Requirements."

E. Delegated-Design Submittal: For shop-fabricated ventilators indicated to comply with performance requirements and design criteria, including analysis data signed and sealed by the qualified professional engineer responsible for their preparation.

1. Detail fabrication and assembly of shop-fabricated ventilators.

1.4 INFORMATIONAL SUBMITTALS

Retain paragraph below if required by seismic criteria applicable to Project. Coordinate with Sections specifying mechanical vibration, supports, and seismic controls. See ASCE/SEI 7 for certification requirements for equipment and components.

A. Seismic Qualification Certificates: For ventilators, accessories, and components, from manufacturer.

1.5 COORDINATION

A. Coordinate sizes and locations of roof curbs, equipment supports, and roof penetrations with actual equipment provided.

PART 2 -  PRODUCTS

2.1 MATERIALS

Retain materials in this article that are required for gravity ventilators specified in succeeding articles.

A. Aluminum Extrusions: ASTM B 221 (ASTM B 221M), Alloy 6063-T5 or T-52.

B. Aluminum Sheet: ASTM B 209 (ASTM B 209M), Alloy 3003 or 5005 with temper as required for forming or as otherwise recommended by metal producer for required finish.

C. Galvanized-Steel Sheet: ASTM A 653/A 653M, G90 (Z275) zinc coating, mill phosphatized.

D. Fasteners: Same basic metal and alloy as fastened metal or 300 Series stainless steel unless otherwise indicated. Do not use metals that are incompatible with joined materials.

1. Use types and sizes to suit unit installation conditions.

2. Use [Phillips flat] [hex-head or Phillips pan]-head screws for exposed fasteners unless otherwise indicated.

E. Post-Installed Fasteners for Concrete and Masonry: Torque-controlled expansion anchors made from stainless-steel components, with capability to sustain without failure a load equal to 4 times the loads imposed for concrete, or 6 times the load imposed for masonry, as determined by testing per ASTM E 488, conducted by a qualified independent testing agency.

F. Bituminous Paint: Cold-applied asphalt emulsion complying with ASTM D 1187.

2.2 FABRICATION, GENERAL

A. Factory fabricate gravity ventilators to minimize field splicing and assembly. Disassemble units to the minimum extent as necessary for shipping and handling. Clearly mark units for reassembly and coordinated installation.

B. Fabricate frames, including integral bases, to fit in openings of sizes indicated, with allowances made for fabrication and installation tolerances, adjoining material tolerances, and perimeter sealant joints.

C. Fabricate units with closely fitted joints and exposed connections accurately located and secured.

D. Fabricate supports, anchorages, and accessories required for complete assembly.

2.3 LOUVERED-PENTHOUSE VENTILATORS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Acme Engineering & Mfg. Corporation.

2. Aerovent.

3. Carnes.

4. Greenheck Fan Corporation.

5. JencoFan.

6. Loren Cook Company.

7. PennBarry.

8. <Insert manufacturer's name>.

Retain roof material option in first paragraph below to match retained frame and blade materials.

C. Construction: All-welded assembly with [4-inch (100-mm)] [6-inch (150-mm)]-deep louvers, mitered corners, and [aluminum] [galvanized-steel] [stainless-steel] sheet roof[ with mineral-fiber insulation and vapor barrier].

D. Frame and Blade Material and Nominal Thickness: Extruded aluminum, of thickness required to comply with structural performance requirements, but not less than 0.080 inch (2.0 mm) for frames and [0.080 inch (2.0 mm)] [0.060 inch (1.5 mm)] for blades[ with condensate deflectors].

Verify availability of seal in first subparagraph below for ventilators indicated. See Editing Instruction No. 2 in the Evaluations for discussion on certified ratings. Coordinate with product data requirement in "Action Submittals" Article.

1. AMCA Seal: Mark units with the AMCA Certified Ratings Seal.

Retain subparagraph below for exterior mitered corners. If retaining, verify available corner construction with manufacturers.

2. Exterior Corners: Prefabricated corner units with [mitered and welded blades] [mitered blades with concealed close-fitting splices] and with [fully recessed] [semirecessed] mullions at corners.

E. Frame and Blade Material and Nominal Thickness: Galvanized-steel sheet, of thickness required to comply with structural performance requirements, but not less than 0.052 inch (1.3 mm) for frames and [0.040 inch (1.0 mm)] [0.052 inch (1.3 mm)] [0.064 inch (1.6 mm)] for blades[ with condensate deflectors].

Verify availability of seal in first subparagraph below for ventilators indicated. See Editing Instruction No. 2 in the Evaluations for discussion on certified ratings. Coordinate with product data requirement in "Action Submittals" Article.

1. AMCA Seal: Mark units with the AMCA Certified Ratings Seal.

Retain subparagraph below for exterior mitered corners. If retaining, verify available corner construction with manufacturers.

2. Exterior Corners: Prefabricated corner units with [mitered and welded blades] [mitered blades with concealed close-fitting splices] and with [fully recessed] [semirecessed] mullions at corners.

F. Frame and Blade Material and Nominal Thickness: Stainless-steel sheet, of thickness required to comply with structural performance requirements, but not less than [0.050 inch (1.27 mm)] [0.062 inch (1.57 mm)], with grain running [parallel] [perpendicular] to length of blades and frame members[ with condensate deflectors].

Retain two subparagraphs below with any of last three paragraphs above; revise to suit Project.

Verify availability of seal in first subparagraph below for louvers indicated. See Editing Instruction No. 2 in the Evaluations for discussion on certified ratings. Coordinate with product data requirement in "Action Submittals" Article.

1. AMCA Seal: Mark units with the AMCA Certified Ratings Seal.

Retain subparagraph below for exterior mitered corners. If retaining, verify available corner construction with manufacturers.

2. Exterior Corners: Prefabricated corner units with [mitered and welded blades] [mitered blades with concealed close-fitting splices] and with [fully recessed] [semirecessed] mullions at corners.

Retain first paragraph below for roof curbs furnished by louvered-penthouse ventilator manufacturer for field installation. Delete if roof curbs are specified in Section 077200 "Roof Accessories."

G. Roof Curbs: Galvanized-steel sheet; with mitered and welded corners; 1-1/2-inch- (40-mm-) thick, rigid fiberglass insulation adhered to inside walls; and 1-1/2-inch (40-mm) wood nailer. Size as required to fit roof opening and ventilator base.

1. Configuration: [Self-flashing without a cant strip, with] [Built-in cant and] [Built-in raised cant and] mounting flange.

Coordinate curb height in subparagraph below with roof deck construction; other heights are available.

2. Overall Height: [8 inches (200 mm)] [9-1/2 inches (240 mm)] [12 inches (300 mm)] [16 inches (400 mm)] [18 inches (450 mm)].

Retain one or both of first two paragraphs below. If both bird screening and insect screening are required, indicate location of each on Drawings.

Retain "Bird Screening" Paragraph below to require compliance with ASHRAE 62.1, in which Section 5.6.5 - "Bird Screens" requires that outdoor intakes be equipped with a screening device designed to limit penetration of a 1/2-inch (13-mm) probe. Also retain paragraph for LEED Prerequisite IEQ 1, which requires compliance with ASHRAE 62.1.

H. Bird Screening: [Galvanized-steel, 1/2-inch- (12.7-mm-) square mesh, 0.041-inch (1.04-mm) wire] [Aluminum, 1/2-inch- (12.7-mm-) square mesh, 0.063-inch (1.6-mm) wire] [Flattened, expanded aluminum, 3/4 by 0.050 inch (19 by 1.27 mm) thick] [Stainless-steel, 1/2-inch- (12.7-mm-) square mesh, 0.047-inch (1.19-mm) wire].

I. Insect Screening: [Aluminum, 18-by-16 (1.4-by-1.6-mm) mesh, 0.012-inch (0.30-mm)] [Stainless-steel, 18-by-18 (1.4-by-1.4-mm) mesh, 0.009-inch (0.23-mm)] wire.

J. Galvanized-Steel Sheet Finish:

1. Surface Preparation: Clean surfaces of dirt, grease, and other contaminants. Clean welds, mechanical connections, and abraded areas and repair galvanizing according to ASTM A 780. Apply a conversion coating suited to the organic coating to be applied over it.

Revise first subparagraph below if a specific type of primer or a baked-on application is required. Coordinate with Section 099113 "Exterior Painting."

2. Factory Priming for Field-Painted Finish: Where field painting after installation is indicated, apply an air-dried primer immediately after cleaning and pretreating.

Subparagraph below is an example only. Revise to suit Project or paint systems available from manufacturers.

3. Baked-Enamel Finish: Immediately after cleaning and pretreating, apply manufacturer's standard finish consisting of prime coat and thermosetting topcoat, with a minimum dry film thickness of 1 mil (0.025 mm) for topcoat and an overall minimum dry film thickness of 2 mils (0.05 mm).

a. Color and Gloss: [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from manufacturer's full range].

If Project has more than one type or configuration of ventilator, delete paragraph below and schedule ventilators on Drawings.

K. Capacities and Characteristics:

1. Height: <Insert inches (mm)>.

2. Width and Depth: <Insert inches (mm)> by <Insert inches (mm)>.

3. Free Area: Not less than [5.0 sq. ft. (0.46 sq. m)] [6.0 sq. ft. (0.56 sq. m)] [7.0 sq. ft. (0.65 sq. m)] <Insert free area> for 48-inch- (1220-mm-) wide by 48-inch- (1220-mm-) high louver.

4. Air Performance: Not more than [0.10-inch wg (25-Pa)] <Insert pressure> static pressure drop at [600-fpm (3.0-m/s)] [700-fpm (3.6-m/s)] [800-fpm (4.1-m/s)] <Insert velocity> free-area [exhaust] [intake] velocity.

5. Wind-Driven Rain Performance: Not less than [99] [95] [80] <Insert number> percent effectiveness when subjected to a rainfall rate of [3 inches (75 mm) per hour and a wind speed of 29 mph (13 m/s)] [8 inches (200 mm) per hour and a wind speed of 50 mph (22.4 m/s)] at a core-area intake velocity of [300 fpm (1.5 m/s)] [400 fpm (2.0 m/s)] [500 fpm (2.5 m/s)] <Insert velocity>.

2.4 ROOF HOODS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Acme Engineering & Mfg. Corporation.

2. Aerovent.

3. Carnes.

4. Greenheck Fan Corporation.

5. JencoFan.

6. Loren Cook Company.

7. PennBarry.

8. <Insert manufacturer's name>.

C. Factory fabricated according to SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Figures 6-6 and 6-7.

D. Materials: [Galvanized-steel sheet, minimum 0.064-inch- (1.62-mm-) thick base and 0.040-inch- (1.0-mm-) thick hood] [Aluminum sheet, minimum 0.063-inch- (1.6-mm-) thick base and 0.050-inch- (1.27-mm-) thick hood]; suitably reinforced.

Retain first paragraph below for roof curbs that are shop fabricated for field installation. Delete if roof curbs are specified in Section 077200 "Roof Accessories."

E. Roof Curbs: Galvanized-steel sheet; with mitered and welded corners; 1-1/2-inch- (40-mm-) thick, rigid fiberglass insulation adhered to inside walls; and 1-1/2-inch (40-mm) wood nailer. Size as required to fit roof opening and ventilator base.

1. Configuration: [Self-flashing without a cant strip, with] [Built-in cant and] [Built-in raised cant and] mounting flange.

Coordinate curb height in subparagraph below with roof deck construction; other heights are available.

2. Overall Height: [8 inches (200 mm)] [9-1/2 inches (240 mm)] [12 inches (300 mm)] [16 inches (400 mm)] [18 inches (450 mm)].

Retain one or both of first two paragraphs below. If both bird screening and insect screening are required, indicate location of each on Drawings.

Retain "Bird Screening" Paragraph below to require compliance with ASHRAE 62.1, in which Section 5.6.5 - "Bird Screens" requires that outdoor intakes be equipped with a screening device designed to limit penetration of a 1/2-inch (13-mm) probe. Also retain paragraph for LEED Prerequisite IEQ 1, which requires compliance with ASHRAE 62.1.

F. Bird Screening: [Galvanized-steel, 1/2-inch- (12.7-mm-) square mesh, 0.041-inch (1.04-mm) wire] [Aluminum, 1/2-inch- (12.7-mm-) square mesh, 0.063-inch (1.6-mm) wire] [Flattened, expanded aluminum, 3/4 by 0.050 inch (19 by 1.27 mm) thick] [Stainless-steel, 1/2-inch- (12.7-mm-) square mesh, 0.047-inch (1.19-mm) wire].

G. Insect Screening: [Aluminum, 18-by-16 (1.4-by-1.6-mm) mesh, 0.012-inch (0.30-mm)] [Stainless-steel, 18-by-18 (1.4-by-1.4-mm) mesh, 0.009-inch (0.23-mm)] wire.

H. Galvanized-Steel Sheet Finish:

1. Surface Preparation: Clean surfaces of dirt, grease, and other contaminants. Clean welds, mechanical connections, and abraded areas and repair galvanizing according to ASTM A 780. Apply a conversion coating suited to the organic coating to be applied over it.

Revise first subparagraph below if a specific type of primer or a baked-on application is required. Coordinate with Section 099113 "Exterior Painting."

2. Factory Priming for Field-Painted Finish: Where field painting after installation is indicated, apply an air-dried primer immediately after cleaning and pretreating.

Subparagraph below is an example only. Revise to suit Project or paint systems available from manufacturers.

3. Baked-Enamel Finish: Immediately after cleaning and pretreating, apply manufacturer's standard finish consisting of prime coat and thermosetting topcoat, with a minimum dry film thickness of 1 mil (0.025 mm) for topcoat and an overall minimum dry film thickness of 2 mils (0.05 mm).

a. Color and Gloss: [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from manufacturer's full range].

If Project has more than one type or configuration of roof hood, delete paragraph below and schedule roof hoods on Drawings.

I. Capacities and Characteristics:

1. Height: <Insert inches (mm)>.

2. Width and Depth: <Insert inches (mm)> by <Insert inches (mm)>.

3. Free Area: Not less than [5.0 sq. ft. (0.46 sq. m)] [6.0 sq. ft. (0.56 sq. m)] [7.0 sq. ft. (0.65 sq. m)] <Insert free area> for 48-inch- (1220-mm-) wide by 48-inch- (1220-mm-) high louver.

4. Air Performance: Not more than [0.10-inch wg (25-Pa)] <Insert pressure> static pressure drop at [600-fpm (3.0-m/s)] [700-fpm (3.6-m/s)] [800-fpm (4.1-m/s)] <Insert velocity> free-area [exhaust] [intake] velocity.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Install gravity ventilators level, plumb, and at indicated alignment with adjacent work.

B. Secure gravity ventilators to roof curbs with cadmium-plated hardware. Use concealed anchorages where possible. Refer to Section 077200 "Roof Accessories."

C. Install gravity ventilators with clearances for service and maintenance.

D. Install perimeter reveals and openings of uniform width for sealants and joint fillers, as indicated.

E. Install concealed gaskets, flashings, joint fillers, and insulation as installation progresses. Comply with Section 079200 "Joint Sealants" for sealants applied during installation.

F. Label gravity ventilators according to requirements specified in Section 230553 "Identification for HVAC Piping and Equipment."

G. Protect galvanized and nonferrous-metal surfaces from corrosion or galvanic action by applying a heavy coating of bituminous paint on surfaces that will be in contact with concrete, masonry, or dissimilar metals.

H. Repair finishes damaged by cutting, welding, soldering, and grinding. Restore finishes so no evidence remains of corrective work. Return items that cannot be refinished in the field to the factory, make required alterations, and refinish entire unit or provide new units.

END OF SECTION 233723

	HVAC GRAVITY VENTILATORS
	233723 - 1



