Copyright 2011 AIA
MasterSpec Professional
09/11

Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 233813 - COMMERCIAL-KITCHEN HOODS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. This Section includes [Type I] [Type II] [Type I and Type II] commercial kitchen hoods.

1.2 ACTION SUBMITTALS

A. Product Data: For the following:

1. Filters/baffles.

2. Fire-suppression systems.

3. Lighting fixtures.

Retain paragraph and subparagraphs below if products are required to withstand specific design loads and Architect either has delegated design responsibility to Contractor or wants to review engineering data as another way to verify product's compliance with performance requirements. Professional engineer qualifications are specified in Section 014000 "Quality Requirements."

B. Shop Drawings: Signed and sealed by a qualified professional engineer.

1. Show plan view, elevation view, sections, roughing-in dimensions, service requirements, duct connection sizes, and attachments to other work.

2. Show cooking equipment plan and elevation to confirm minimum code-required overhang.

3. Indicate performance, exhaust and makeup air airflow, and pressure loss at actual Project-site elevation.

4. Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

5. Design Calculations: Calculate requirements for selecting seismic restraints.

6. Wiring Diagrams: Power, signal, and control wiring.

7. Piping Diagrams: Detail fire-suppression piping and components and differentiate between manufacturer-installed and field-installed piping. Show cooking equipment plan and elevation to illustrate fire-suppression nozzle locations.

1.3 INFORMATIONAL SUBMITTALS

Retain paragraph below if procedures for welder certification are retained in "Quality Assurance" Article.

A. Welding certificates.

Retain first paragraph below if required by seismic criteria applicable to Project. Coordinate with Section 230548 "Vibration and Seismic Controls for HVAC." Verify ability of specified manufacturer to provide this certification.

B. Manufacturer Seismic Qualification Certification: Submit certification that commercial kitchen hoods, accessories, and components will withstand seismic forces defined in Section 230548 "Vibration and Seismic Controls for HVAC."

C. Field quality-control test reports.

1.4 QUALITY ASSURANCE

Retain first paragraph below if welding is required. Retain "Welding certificates" Paragraph in "Informational Submittals" Article if retaining below. AWS states that welding qualifications remain in effect indefinitely unless welding personnel have not welded for more than six months or there is a specific reason to question their ability.

A. Welding: Qualify procedures and personnel according to AWS D1.1/D 1.1M, "Structural Welding Code - Steel," for hangers and supports; and AWS D9.1/D9.1M, "Sheet Metal Welding Code," for joint and seam welding.

B. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

PART 2 -  PRODUCTS

2.1 HOOD MATERIALS

A. Stainless-Steel Sheet: ASTM A 666, Type 304.

Most manufacturers' literature still uses the term "gage" as a unit of measure. First option in first subparagraph below is for 20-gage stainless steel. Most hood manufacturers advertise use of 18-gage stainless steel that equates to second option.

1. Minimum Thickness: [0.037 inch (0.94 mm)] [0.050 inch (1.3 mm)] <Insert thickness>.

2. Finish: Comply with SSINA's "Finishes for Stainless Steel" for recommendations for applying and designating finishes.

a. Finish shall be free from tool and die marks and stretch lines and shall have uniform, directionally textured, polished finish indicated, free of cross scratches. Grain shall run with long dimension of each piece.

Sheet finish designations in subparagraph below are often used to specify finishes applied after fabrication.

3. Concealed Stainless-Steel Surfaces: ASTM A 480/A 480M, No. 2B finish (bright, cold-rolled, unpolished finish).

Retain one of first six subparagraphs below. Finish Nos. 3 and 4 are most common.

4. Exposed Surfaces: ASTM A 480/A 480M, No. 2B finish (bright, cold-rolled, unpolished).

5. Exposed Surfaces: ASTM A 480/A 480M, No. 3 finish (intermediate polished surface).

6. Exposed Surfaces: ASTM A 480/A 480M, No. 4 finish (directional satin).

7. Exposed Surfaces: ASTM A 480/A 480M, No. 6 finish (dull satin).

8. Exposed Surfaces: ASTM A 480/A 480M, No. 7 finish (reflective, directional polish).

9. Exposed Surfaces: ASTM A 480/A 480M, No. 8 finish (mirrorlike reflective, nondirectional polish).

10. When polishing is completed, passivate and rinse surfaces. Remove embedded foreign matter and leave surfaces chemically clean.

B. Zinc-Coated Steel Shapes: ASTM A 36/A 36M, zinc coated according to ASTM A 123/A 123M requirements.

C. Sealant: ASTM C 920; Type S, Grade NS, Class 25, Use NT. Elastomeric sealant shall be NSF certified for commercial kitchen hood application. Sealants, when cured and washed, shall comply with requirements in 21 CFR, Section 177.2600, for use in areas that come in contact with food.

1. Color: As selected by Architect from manufacturer's full range.

2. Backer Rod: Closed-cell polyethylene, in diameter larger than joint width.

D. Sound Dampening: NSF-certified, nonabsorbent, hard-drying, sound-deadening compound for permanent adhesion to metal in minimum 1/8-inch (3-mm) thickness that does not chip, flake, or blister.

E. Gaskets: NSF certified for end-use application indicated; of resilient rubber, neoprene, or PVC that is nontoxic, stable, odorless, nonabsorbent, and unaffected by exposure to foods and cleaning compounds, and that passes testing according to UL 710.

2.2 GENERAL HOOD FABRICATION REQUIREMENTS

A. Welding: Use welding rod of same composition as metal being welded. Use methods that minimize distortion and develop strength and corrosion resistance of base metal. Make ductile welds free of mechanical imperfections such as gas holes, pits, or cracks.

1. Welded Butt Joints: Full-penetration welds for full-joint length. Make joints flat, continuous, and homogenous with sheet metal without relying on straps under seams, filling in with solder, or spot welding.

2. Grind exposed welded joints flush with adjoining material and polish to match adjoining surfaces.

3. Where fasteners are welded to underside of equipment, finish reverse side of weld smooth and flush.

4. Coat concealed stainless-steel welded joints with metallic-based paint to prevent corrosion.

Indicate acceptable field-joint locations and connection methods on Drawings. Coordinate with NSF requirements. SMACNA's "Kitchen Ventilation Systems & Food Service Equipment Guidelines" includes typical butt joints. Revise first paragraph below to suit Project.

B. For metal butt joints, comply with SMACNA's "Kitchen Ventilation Systems & Food Service Equipment Guidelines."

C. Form metal with break bends that are not flaky, scaly, or cracked in appearance; where breaks mar uniform surface appearance of material, remove marks by grinding, polishing, and finishing.

D. Sheared Metal Edges: Finish free of burrs, fins, and irregular projections.

E. In food zones, as defined in NSF, fabricate surfaces free from exposed fasteners.

F. Cap exposed fastener threads, including those inside cabinets, with stainless-steel lock washers and stainless-steel cap (acorn) nuts.

G. Fabricate pipe slots on equipment with turned-up edges sized to accommodate service and utility lines and mechanical connections.

H. Fabricate enclosures, including panels, housings, and skirts, to conceal service lines, operating components, and mechanical and electrical devices including those inside cabinets, unless otherwise indicated.

Retain first paragraph below if Project requires seismic design.

I. Fabricate seismic restraints according to SMACNA's "Kitchen Ventilation Systems & Food Service Equipment Guidelines," Appendix A, "Seismic Restraint Details."

J. Fabricate equipment edges and backsplashes according to SMACNA's "Kitchen Ventilation Systems & Food Service Equipment Guidelines."

K. Fabricate enclosure panels to ceiling and wall as follows:

1. Fabricate panels on [one] [two] [three] [four] [all exposed] side(s) with same material as hood, and extend from ceiling to top of hood canopy and from canopy to wall.

Verify depth of wall offset spacer; most authorities having jurisdiction require between 3 and 6 inches (75 and 150 mm).

2. Wall Offset Spacer: Minimum of 3 inches (75 mm).

3. Wall Shelves and Overshelves: Fabricate according to SMACNA's "Kitchen Ventilation Systems & Food Service Equipment Guidelines," with minimum 0.0625-inch- (1.58-mm-) thick, stainless-steel shelf tops.

2.3 TYPE I EXHAUST HOOD FABRICATION

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. Retain one of first three paragraphs and list of manufacturers below for listed hoods. See Section 016000 "Product Requirements."

A. Available Manufacturers: Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product: Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Aerolator Systems, Inc.

2. AHR Metals, Inc.; Air Saver Systems.

3. Air Tech; Delfield Company (The).

4. AyrKing Corporation.

5. Captive-Aire Systems.

6. Carroll Manufacturing International.

7. Duke Manufacturing Company.

8. Gaylord Industries, Inc.

9. Giles Enterprises, Inc.

10. Grease Master; a division of Custom Industries, Inc.

11. Greenheck.

12. Halton Company.

13. LCSystems, Inc.

14. Sturdi-Bilt Restaurant Equipment.

15. Vent Master; Div. of Garland Commercial Ranges, Ltd.

16. <Insert manufacturer's name.>

D. Weld all joints exposed to grease with continuous welds, and make filters/baffles or grease extractors and makeup air diffusers easily accessible for cleaning.

1. Fabricate hoods according to NSF 2, "Food Equipment."

2. Hoods shall be listed and labeled, according to UL 710, by a testing agency acceptable to authorities having jurisdiction.

3. Hoods shall be designed, fabricated, and installed according to NFPA 96.

Retain subparagraph below if fire dampers are required.

4. Include access panels as required for access to fire dampers and fusible links.

Retain subparagraph below for duct collars without fire dampers.

5. Duct Collars Without Fire Dampers: Minimum 0.0598-inch- (1.5-mm-) thick steel at least 3 inches (75 mm) long, continuously welded to top of hood and at corners.[ Fabricate a collar with a 0.5-inch- (13-mm-) wide duct flange.]

Retain subparagraph and associated subparagraphs below for duct collars with fire dampers.

6. Duct-Collar With Fire Dampers: Collar and damper shall comply with UL 710 testing and listing required for the entire hood.

a. Collar: Minimum 0.0598-inch- (1.5-mm-) thick stainless steel, at least 3 inches (75 mm) long, continuously welded to top of hood and at corners.[ Fabricate a collar with a minimum 0.5-inch- (13-mm-) wide duct flange.]

b. Blades: Minimum 0.1046-inch- (2.7-mm-) thick stainless steel, counterbalanced to remain closed after actuation.

c. Blade Pivot and Spring: Stainless steel.

d. Fusible Link: Replaceable, 212 deg F (100 deg C) rated.

Retain subparagraph and associated subparagraphs below for makeup air fire dampers. Specifically ask authorities having jurisdiction if fire dampers are required for makeup air and exhaust-air connections.

7. Makeup Air Fire Dampers: Labeled, according to UL 555, by a testing agency acceptable to authorities having jurisdiction.

a. Fire Rating: 1-1/2 hours.

b. Frame: SMACNA [Type A] [Type B], with blades in airstream; fabricated with roll-formed, [galvanized] [stainless] steel; with mitered and interlocking corners.

c. Blades: Roll-formed, interlocking or folded, minimum 0.034-inch- (0.86-mm-) thick, galvanized-steel sheet.

d. Horizontal Dampers: Include a blade lock and stainless-steel closure spring.

e. Fusible Link: Replaceable, [165 deg F (74 deg C)] [212 deg F (100 deg C)] rated.

E. Hood Configuration: Exhaust [only] [and makeup air].

Retain one or more of three subparagraphs below for makeup air configuration. If more than one hood configuration is required, makeup air arrangement must be indicated in a schedule. First subparagraph describes an induction or "short-circuit" hood that is not acceptable to all authorities having jurisdiction. Consult authorities having jurisdiction before specifying this hood.

1. Makeup air shall be introduced by [induction] [combination of induction and diffusion] inside canopy. If makeup air is not heated, insulate interior of makeup air plenum with high-density insulation having maximum flame-spread and smoke-developed indexes of 25 and 50, respectively.

2. Makeup air shall be introduced through [front] [front and bottom] [bottom] of canopy through [perforated diffusers] [supply-air registers with adjustable guide vanes].

3. Makeup air shall be introduced through laminar-flow-type, perforated metal panels on front of hood canopy.

F. Hood Style: [Wall-mounted canopy] [Single-island canopy] [Double-island canopy] [Back shelf] [Eyebrow] [Pass over].

Retain paragraph below for hoods equipped with removable filters/baffles. Spring-loaded fasteners are required for filters/baffles in some jurisdictions.

G. Filters/Baffles: Removable, [stainless-steel] [aluminum] [, with spring-loaded fastening]. Fabricate stainless steel for filter frame and removable collection cup and pitched trough. Exposed surfaces shall be pitched to drain to collection cup. Filters/baffles shall be tested according to UL 1046, "Grease Filters for Exhaust Ducts," by an NRTL acceptable to authorities having jurisdiction.

Retain paragraph and subparagraphs below for hoods containing lighting fixtures.

H. Lighting Fixtures: [Recessed] [Surface-mounted], [fluorescent] [incandescent] fixtures and lamps with lenses sealed vaportight. Wiring shall be installed in conduit on hood exterior. Number and location of fixtures shall provide a minimum of 70 fc (753 lx) at 30 inches (762 mm) above finished floor.

1. Light switches shall be mounted [on front panel of hood canopy] [on wall adjacent to hood] [in hood control panel].

2. Lighting Fixtures: [Fluorescent] [Incandescent] complying with UL 1598.

Retain one of two paragraphs below. Retain second paragraph and subparagraphs for controls provided with commercial kitchen hoods.

I. Comply with requirements in Section 230900 "Instrumentation and Control for HVAC" and Section 230993 "Sequence of Operations for HVAC Controls" for hood controls.

J. Hood Controls: [Hood] [Wall]-mounting control cabinet, [factory wired to control groups of adjacent hoods, and ]fabricated of stainless steel.

Retain option in subparagraph below for makeup air or replacement-air unit.

1. Exhaust Fan: On-off switches shall start and stop the exhaust fan. [Interlock exhaust fan with makeup air supply fan to operate simultaneously. ]Interlock exhaust fan with fire-suppression system to operate fan(s) during fire-suppression-agent release and to remain in operation until manually stopped. Include red pilot light to indicate fan operation. Motor starters shall comply with Section 262913 "Enclosed Controllers."

Retain subparagraph below to interlock adjacent hoods to operate together. Hoods involved in this interlock must be indicated on Drawings.

2. Exhaust Fan Interlock: Factory wire the exhaust fan starters in a single control cabinet for adjacent hoods to operate together.

Retain subparagraph below to save cost of cleanup from release of fire-suppression agent.

3. High-Temperature Control: Alarm shall sound and cooking equipment shall shut down before hood discharge temperature rises to actuation temperature of fire-suppression system.

If Project has more than one commercial kitchen hood configuration, delete paragraph and subparagraphs below and schedule commercial kitchen hoods on Drawings. If retaining below, retain "Basis-of-Design Product" Paragraph at the beginning of this Article and insert manufacturer's name and model number there.

K. Capacities and Characteristics:

1. Nominal Hood Length: <Insert inches (mm).>

2. Nominal Hood Width: <Insert inches (mm).>

3. Canopy Height: <Insert inches (mm).>

4. Exhaust Airflow: <Insert cfm (L/s).>

5. Exhaust-Air Pressure Loss: <Insert inches wg (kPa).>

6. Makeup Air Airflow: <Insert cfm (L/s).>

7. Makeup Air Pressure Loss: <Insert inches wg (kPa).>

2.4 TYPE II EXHAUST HOOD FABRICATION

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. Retain one of first three paragraphs and list of manufacturers below for listed hoods. See Section 016000 "Product Requirements."

A. Available Manufacturers: Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product: Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Aerolator Systems, Inc.

2. AHR Metals, Inc.; Air Saver Systems.

3. Air Tech; Delfield Company (The).

4. AyrKing Corporation.

5. Captive-Aire Systems.

6. Carroll Manufacturing International.

7. Duke Manufacturing Company.

8. Gaylord Industries, Inc.

9. Giles Enterprises, Inc.

10. Grease Master; a division of Custom Industries, Inc.

11. Greenheck.

12. Halton Company.

13. LCSystems, Inc.

14. Sturdi-Bilt Restaurant Equipment.

15. Vent Master; Div. of Garland Commercial Ranges, Ltd.

16. <Insert manufacturer's name.>

D. Fabricate hoods according to NSF 2, "Food Equipment."

Retain first paragraph below for field-fabricated hoods.

E. Fabricate hoods to comply with SMACNA's "HVAC Duct Construction Standards: Metal and Flexible."

F. Hood Configuration: Exhaust [only] [and makeup air].

Retain one of three subparagraphs below for makeup air configuration. Consider using Type I hoods if makeup air for hoods is required.

1. Makeup air shall be introduced by [induction] [combination of induction and diffusion] inside canopy. If makeup air is not heated, insulate interior of makeup air plenum with high-density insulation having maximum flame-spread and smoke-developed indexes of 25 and 50, respectively.

2. Makeup air shall be introduced through [front] [front and bottom] [bottom] of canopy through supply-air registers.

3. Makeup air shall be introduced through laminar-flow-type, perforated metal panels on front of hood canopy.

G. Hood Type: [Heat and vapor] [Condensate] removal.

H. Hood Style: [Wall-mounted canopy] [Single-island canopy] [Double-island canopy] [Back shelf] [Eyebrow] [Pass over].

I. Condensate Hood Baffles: Removable, stainless-steel baffles to drain into a hood drain trough, and stainless-steel drain piping.

Retain paragraph and subparagraphs below for hoods containing lighting fixtures.

J. Lighting Fixtures: [Recessed] [Surface-mounted], [fluorescent] [incandescent] fixtures and lamps with lenses sealed vaportight. Wiring shall be installed in stainless-steel conduit on hood exterior. Number and location of fixtures shall provide a minimum of 70 fc (753 lx) at 30 inches (762 mm) above finished floor.

1. Light switches shall be mounted [on front panel of hood canopy] [on wall adjacent to hood] [in hood control panel].

2. Lighting Fixtures: [Fluorescent] [Incandescent] complying with UL 1598.

If Project has more than one commercial kitchen hood configuration, delete paragraph and subparagraphs below and schedule commercial kitchen hoods on Drawings. If retaining below, retain "Basis-of-Design Product" Paragraph at the beginning of this Article and insert manufacturer's name and model number there.

K. Capacities and Characteristics:

1. Nominal Hood Length: <Insert inches (mm).>

2. Nominal Hood Width: <Insert inches (mm).>

3. Canopy Height: <Insert inches (mm).>

4. Exhaust Airflow: <Insert cfm (L/s).>

5. Exhaust-Air Pressure Loss: <Insert inches wg (kPa).>

6. Makeup Air Airflow: <Insert cfm (L/s).>

7. Makeup Air Pressure Loss: <Insert inches wg (kPa).>

2.5 WET-CHEMICAL FIRE-SUPPRESSION SYSTEM

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. Retain one of first three paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Available Manufacturers: Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product: Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Ansul Incorporated; a Tyco International Ltd. Company.

2. Badger Fire Protection.

3. Kidde Fire Systems.

4. Pyro Chem.

5. <Insert manufacturer's name.>

D. Description: Engineered distribution piping designed for automatic detection and release or manual release of fire-suppression agent by hood operator. Fire-suppression system shall be listed and labeled for complying with NFPA 17A, "Wet Chemical Extinguishing Systems," by a qualified testing agency acceptable to authorities having jurisdiction.

1. Steel Pipe, NPS 2 (DN 50) and Smaller: ASTM A 53/A 53M, Type S, Grade A, Schedule 40, plain ends.

2. Malleable-Iron Threaded Fittings: ASME B16.3, Classes 150 and 300.

3. Piping, fusible links and release mechanism, tank containing the suppression agent, and controls shall be factory installed. Controls shall be in stainless-steel control cabinet mounted on [hood] [or] [wall]. Furnish manual pull station for wall mounting. Exposed piping shall be covered with chrome-plated aluminum tubing. Exposed fittings shall be chrome plated.

4. Liquid Extinguishing Agent: Noncorrosive, low-pH liquid.

Retain one of first two subparagraphs below.

5. Furnish electric-operated gas shutoff valve; refer to [Section 231123 "Facility Natural-Gas Piping."] [Section 231126 "Facility Liquefied-Petroleum Gas Piping."]

6. Furnish electric-operated gas shutoff valve with clearly marked open and closed indicator for field installation.

7. Fire-suppression system controls shall be integrated with controls for fans, lights, and fuel supply and located in a single cabinet for each group of hoods immediately adjacent.

8. Wiring shall have color-coded, numbered terminal blocks and grounding bar. Spare terminals for fire alarm, optional wiring to start fan with fire alarm, red pilot light to indicate fan operation, and control switches shall all be factory wired in control cabinet with relays or starters. Include spare terminals for fire alarm, and wiring to start fan with fire alarm.

PART 3 -  EXECUTION

3.1 INSTALLATION

Indicate field joints and methods of connection on Drawings. Coordinate with NSF requirements.

A. Complete field assembly of hoods where required.

1. Make closed butt and contact joints that do not require filler.

2. Grind field welds on stainless-steel equipment smooth, and polish to match adjacent finish. Comply with welding requirements in Part 2 "General Hood Fabrication Requirements" Article.

Verify maintenance clearance requirements of authorities having jurisdiction. Indicate minimum clearances on Drawings and revise paragraph below to suit Project.

B. Install hoods and associated services with clearances and access for maintaining, cleaning, and servicing hoods, filters/baffles, grease extractor, and fire-suppression systems according to manufacturer's written instructions and requirements of authorities having jurisdiction.

Retain first paragraph below if Type I hoods and associated services require on-site modification.

C. Make cutouts in hoods where required to run service lines and to make final connections, and seal openings according to UL 1978.

D. Securely anchor and attach items and accessories to walls, floors, or bases with stainless-steel fasteners, unless otherwise indicated.

E. Install hoods to operate free from vibration.

Retain first paragraph below and verify requirements of authorities having jurisdiction if Project requires seismic design.

F. Install seismic restraints according to SMACNA's "Kitchen Ventilation Systems & Food Service Equipment Guidelines," Appendix A, "Seismic Restraint Details."

G. Install trim strips and similar items requiring fasteners in a bed of sealant. Fasten with stainless-steel fasteners at 48 inches (1200 mm) o.c. maximum.

H. Install sealant in joints between equipment and abutting surfaces with continuous joint backing, unless otherwise indicated. Provide airtight, watertight, vermin-proof, sanitary joints.

I. Install lamps, with maximum recommended wattage, in equipment with integral lighting.

J. Set initial temperatures, and calibrate sensors.

K. Set field-adjustable switches.

L. Connect ducts according to requirements in Section 233300 "Air Duct Accessories." Install flexible connectors on makeup air supply duct. Weld exhaust-duct connections with continuous liquidtight joint.

M. Install fire-suppression piping for remote-mounted suppression systems according to NFPA 17A, "Wet Chemical Extinguishing Systems."

3.2 FIELD QUALITY CONTROL

Retain one of first two paragraphs below that identify who shall perform tests and inspections.

Retain paragraph below to require a factory-authorized service representative to perform inspections, tests, and adjustments.

A. Manufacturer's Field Service: Engage a factory-authorized service representative to inspect, test, and adjust components, assemblies, and equipment installations, including connections. Report results in writing.

Retain first paragraph below to require Contractor to perform tests and inspections.

B. Perform tests and inspections.

Retain subparagraph below to require a factory-authorized service representative to assist Contractor with inspections, tests, and adjustments.

1. Manufacturer's Field Service: Engage a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

C. Tests and Inspections:

1. Test each equipment item for proper operation. Repair or replace equipment that is defective, including units that operate below required capacity or that operate with excessive noise or vibration.

2. Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.

3. Perform hood performance tests required by authorities having jurisdiction.

4. Perform fire-suppression system performance tests required by authorities having jurisdiction.

D. Prepare test and inspection reports.

END OF SECTION 233813

	COMMERCIAL-KITCHEN HOODS
	233813 - 1



