Copyright 2010 AIA
MasterSpec Professional
03/10

Copyright 2010 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 234300 - ELECTRONIC AIR CLEANERS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Electronic air cleaners.

2. Side-service housings.

3. Front- and rear-access filter frames.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product indicated.

B. LEED Submittals:

See "LEED Rating System" Article in the Evaluations for discussion on LEED prerequisites and credits.

1. Product Data for Prerequisite IEQ 1: Documentation indicating that units comply with ASHRAE 62.1, Section 5 - "Systems and Equipment."

C. Shop Drawings: For each electronic air cleaner. Include plans, elevations, sections, details, and attachments to other work.

1. Show filter assembly, dimensions, materials, and methods of assembly of components.

2. Include setting drawings, templates, and requirements for installing anchor bolts and anchorages.

3. Wiring Diagrams: For power, signal, and control wiring.

1.3 INFORMATIONAL SUBMITTALS

A. Field quality-control reports.

1.4 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

1.5 MAINTENANCE MATERIAL SUBMITTALS

A. Furnish extra materials that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

1. Provide [one] <Insert number> complete set(s) of prefilters for each filter bank.

2. Provide detergent for [one] [two] <Insert number> refill(s).

3. Provide [one] <Insert number> container(s) of red oil for inclined manometer filter gage.

1.6 QUALITY ASSURANCE

A. ASHRAE Compliance:

Retain first subparagraph below to require compliance with ASHRAE 62.1. LEED Prerequisite IEQ 1 requires compliance with requirements in ASHRAE 62.1. Besides establishing minimum ventilation rates, ASHRAE 62.1 includes requirements for surfaces in contact with the airstream, particulate and gaseous filtration, and equipment access. See "LEED Rating System" Article in the Evaluations for discussion on this prerequisite. Verify, with manufacturers, availability of units with components and features that comply with these requirements.

1. Comply with applicable requirements in ASHRAE 62.1, Section 4, "Outdoor Air Quality"; Section 5, "Systems and Equipment"; and Section 7 - "Construction and Startup."

2. Comply with ASHRAE 52.1 for arrestance and with ASHRAE 52.2 for MERV for methods of testing and rating air-filter units.

B. Comply with NFPA 90A and NFPA 90B.

C. Comply with ARI 850.

D. Comply with UL 867.

PART 2 -  PRODUCTS

2.1 ELECTRONIC AIR CLEANERS

A. Description: Factory-fabricated electronic air cleaner operating by electrostatic precipitation principles.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in subparagraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Air Quality Engineering, Inc.

b. CRS Industries, Inc.; CosaTron Div.

c. Flanders-Precisionaire.

d. Trion, Inc.

e. <Insert manufacturer's name>.

Prefilters are optional features.

If Project has more than one type or configuration of prefilter, retain each type and schedule prefilters on Drawings.

B. Prefilter: Comply with requirements in Section 234100 "Particulate Air Filtration" for [flat] [pleated] [ring] panel. Size and airflow capacity shall match those of electronic air cleaners.

1. Depth: [1 inch (25 mm)] [2 inches (50 mm)] [4 inches (100 mm)] <Insert dimension>.

2. Filter Unit Class: UL 900, [Class 1] [Class 2].

3. Arrestance: [85] <Insert number> percent when tested according to ASHRAE 52.1.

4. MERV: [8] <Insert value> when tested according to ASHRAE 52.2.

C. Collection Cells: Aluminum, independently supported and nested.

1. Ionizing Section: Alternately spaced grounded struts and charged ionizing wires.

2. Collecting Section: Alternately grounded and charged plates, with insulators located out of airstream.

In first paragraph below, coordinate electrical characteristics with those included in "Capacities and Characteristics" Article or in schedule on Drawings.

D. Power Pack: Self-contained, prewired rectifying unit to convert [120] [208/240] [480]-V ac, single-phase, 60-Hz power to approximately 12,000-V dc for ionizer and 6000-V dc for collector; include overload protection, on-off switch, pilot light showing operating status, and access door interlock.

E. Safety Accessories: Manual-reset safety switches and warning lights for filter plenum access doors, signal lights and safety switching upstream and downstream from unit within duct, and enameled high-voltage warning signs.

F. Collection Section Cleaning System:

1. Detergent Reservoir Tank: [30 gal. (110 L)] [55 gal. (200 L)] with pump, motor, solenoid valve, level sensor, backflow preventer, wye-strainer, and ball valve.

2. Detergent.

3. Dispensing System: Motor-driven oscillating copper manifolds with brass spray nozzles on each side of the collector.

G. Mist Eliminators: [Upstream][ and downstream] [Downstream].

H. Controls: Programmable logic controller in remotely mounted NEMA 250, Type 12 enclosure; with integral time clock and manual override.

1. Contacts for enable-disable control by building automation system.

"Finish of Interior Surfaces" Paragraph below may be required to comply with Project requirements or authorities having jurisdiction. Retain paragraph for LEED Prerequisite IEQ 1, which requires compliance with ASHRAE 62.1. See "LEED Rating System" Article in the Evaluations.

I. Finish of Interior Surfaces: Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1.

2.2 CABINET

A. Description: 16-gage galvanized steel with epoxy powder finish for suspended, wall, frame, or duct mounting.

2.3 SIDE-SERVICE HOUSINGS

This article is an example of filter-holding frames for side loading. Retain first option in first paragraph below if specifying cleaning system.

A. Description: Factory-assembled, side-service housings, [with bottom drain, ]constructed of [galvanized steel] [aluminum] and configured for stacking, with flanges to connect to duct or casing system.

B. Access Doors: [Hinged with continuous] [Continuous] gaskets on perimeter and positive-locking devices.

C. Sealing: Incorporate positive-sealing gasket material on channels to seal top and bottom of filter cartridge frames to prevent bypass of unfiltered air.

"Finish of Interior Surfaces" Paragraph below may be required to comply with Project requirements or authorities having jurisdiction. Retain paragraph for LEED Prerequisite IEQ 1, which requires compliance with ASHRAE 62.1. See "LEED Rating System" Article in the Evaluations.

D. Finish of Interior Surfaces: Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1.

2.4 FRONT- AND REAR-ACCESS FILTER FRAMES

This article is an example of filter-holding frames for front and rear loading.

A. Framing System: [Galvanized-steel] [Aluminum] framing members with access for either upstream (front) or downstream (rear) filter servicing, cut to size and prepunched for assembly into modules[ with bottom drain], and configured for stacking. Vertically support filters to prevent deflection of horizontal members without interfering with either filter installation or operation.

B. Prefilters: Incorporate a separate track[ with spring clips], removable from front[ or back].

C. Sealing: Factory-installed, positive-sealing device for each row of filters to ensure seal between gasketed filter elements to prevent bypass of unfiltered air.

Retain paragraph below to comply with LEED Prerequisite IEQ 1. See "LEED Rating System" Article in the Evaluations.

D. Finish of Interior Surfaces: Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1.

2.5 CAPACITIES AND CHARACTERISTICS

If Project has more than one type or configuration of filter, delete this article and schedule filters on Drawings.

Retain one of first two paragraphs below.

A. Unit Face Dimensions: [72 by 72 inches (1828 by 1828 mm)] <Insert dimensions> nominal.

B. Number of Cleaner Units: <Insert number>.

C. Unit Depth: [33 inches (825 mm)] [45 inches (1125 mm)] <Insert dimension> nominal.

D. Holding Frame Size: <Insert inches (mm)>.

E. Frame Access Location: [Front] [back] [or] [side].

F. System Airflow: <Insert cfm (L/s)>.

G. Maximum or Rated Face Velocity: [500 fpm (2.5 m/s)] <Insert value>.

H. Power Pack:

1. Volts: [120] [208] [230] [460] <Insert value> V.

2. Phase: [Single] [Three].

3. Hertz: 60.

4. Full-Load Amperes: <Insert value>.

5. Minimum Circuit Ampacity: <Insert value>.

6. Maximum Overcurrent Protection Device: <Insert amperage>.

I. Efficiency: 90 percent on particles 20 micrometers and larger at 500 fpm (2.5 m/s).

J. Initial Resistance: [0.25-inch wg (63 Pa)] <Insert value>.

K. Prefilter Type: Integral tracks to accommodate 2-inch- (50-mm-) thick disposable[ or washable] filters.

L. Cleaning System: [Manual] [or] [automatic].

M. Reservoir Tank: [30 gal. (114 L)] [50 gal. (190 L)].

N. Connections:

1. Water Supply: <Insert NPS (DN)>.

2. Drain: <Insert NPS (DN)>.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Position each filter unit with clearance for normal service and maintenance. Anchor filter holding frames to substrate.

B. Install filters in position to prevent passage of unfiltered air.

LEED-NC, LEED-CI, and LEED for Schools Credit IEQ 3.1 and LEED CS Credit IEQ 3 require filters with a minimum MERV 13 rating for air delivered to an occupied space. Air-handling units should not be used for temporary heating and ventilating unless expressly approved by Owner. If filters are used during construction, see SMACNA's "IAQ Guidelines for Occupied Buildings under Construction" for procedures to protect HVAC system.

LEED-NC, LEED-CI, and LEED for Schools Credit IEQ 3.1 and LEED-CS Credit IEQ 3 require that if permanently installed air handlers and air distribution system are used during construction, filtration media with a MERV 8, as determined by ASHRAE 52.2, shall be installed at each return-air grille. Filters in air handlers used during construction shall have a minimum MERV 13 rating for systems that deliver air to occupied spaces.

C. Do not operate fan system until filters (temporary or permanent) are in place. Replace temporary filters used during construction and testing with new, clean filters.

D. Operate electronic air cleaners for 24 hours as part of startup before filters are put into operation.

E. Install and connect water-supply and drainage piping.

F. Coordinate filter installations with duct and air-handling-unit installations.

3.2 FIELD QUALITY CONTROL

Retain first paragraph below to describe tests and inspections to be performed.

A. Tests and Inspections: Test for leakage of unfiltered air while system is operating.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

B. Air filter will be considered defective if it does not pass tests and inspections.

C. Prepare test and inspection reports.

3.3 CLEANING

A. After completing system installation and testing, adjusting, and balancing air-handling and air-distribution systems, clean filter housings and install new prefilter media.

END OF SECTION 234300

	ELECTRONIC AIR CLEANERS
	234300 - 1



