Copyright 2010 AIA
MasterSpec Professional
03/10

Copyright 2010 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 235113 - DRAFT CONTROL DEVICES
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. This Section includes the following:

Adjust list below to suit Project.

1. Barometric dampers.

2. Vent dampers.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product indicated.

B. Wiring Diagrams: Power, signal, and control wiring.

1.3 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

1.4 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

PART 2 -  PRODUCTS

2.1 BAROMETRIC DAMPERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. Retain one of first three paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Available Manufacturers: Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product: Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Babco Inc.

2. Bramec Corporation.

3. Effikal International Inc.

4. EXHAUSTO, Inc.

5. FAMCO.

6. Field Controls L.L.C.; Venting Solutions Company (The).

7. Quickdraft; a Litzler Company.

8. Snappy Air Distribution Products.

9. Tec-Air Inc.

10. Tjernlund Products, Inc.

11. Tutco, Inc.; Subsidiary of Smiths Industries.

12. Wing Draft Inducers; Subsidiary of Smiths Industries.

13. <Insert manufacturer's name.>

D. Damper Construction: High-temperature-enamel-painted steel damper and housing with galvanized-steel breeching connection. Adjustable counterweight with lock. Include knife-edge bearings that do not require lubrication.

2.2 VENT DAMPERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. Retain one of first three paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Available Manufacturers: Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product: Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Effikal International Inc.

2. Field Controls L.L.C.; Venting Solutions Company (The).

3. Johnson Controls, Inc.; Controls Group.

4. <Insert manufacturer's name.>

D. Damper Construction: Stainless-steel damper blade, shaft, and vent pipe with metal, prelubricated bearings.

1. Electric motor sized to power damper open and closed in approximately 15 seconds in each direction. Power is off when damper is at rest.

2. Comply with ANSI Z21.66.

E. Controls:

1. Control transformer.

2. Keyed wiring harness.

3. Damper end-switch to prove damper is open.

4. Interlock with boiler to permit burner operation when damper is open.

5. Hold-open switch for troubleshooting boiler controls.

2.3 MOTORS

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Section 230513 "Common Motor Requirements for HVAC Equipment." If characteristics other than these are required, add paragraphs to this Article to suit Project.

A. Comply with requirements in Section 230513 "Common Motor Requirements for HVAC Equipment."

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Install listed components in a manner complying with the listing.

B. Secure barometric dampers to breechings with hardware compatible with connected materials.

C. Locate barometric and motorized vent dampers as close to draft hood collar as possible.

D. Secure barometric and motorized vent dampers to appliances, breechings, or chimneys with hardware compatible with connected materials.

END OF SECTION 235113

	DRAFT CONTROL DEVICES
	235113 - 1



