Copyright 2011 AIA
MasterSpec Professional
09/11

Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 235216 - CONDENSING BOILERS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section includes packaged, factory-fabricated and -assembled, gas-fired, [pulse-combustion] [fire-tube] [water-tube] [water-jacketed] condensing boilers, trim, and accessories for generating hot water.

1.2 ACTION SUBMITTALS

A. Product Data: Include performance data, operating characteristics, furnished specialties, and accessories.

B. Shop Drawings: For boilers, boiler trim, and accessories. Include plans, elevations, sections, details, and attachments to other work.

Retain subparagraph and associated subparagraphs below if boilers are required to withstand specific design loads and Architect either has delegated design responsibility to Contractor or wants to review structural data as another way to verify equipment's compliance with performance requirements. Professional engineer qualifications are specified in Section 014000 "Quality Requirements."

1. Design calculations and vibration isolation base details, signed and sealed by a qualified professional engineer.

a. Design Calculations: Calculate requirements for selecting vibration isolators and seismic restraints and for designing vibration isolation bases.

b. Vibration Isolation Base Details: Detail fabrication including anchorages and attachments to structure and to supported equipment. Include auxiliary motor slides and rails and equipment mounting frames.

Retain subparagraph below if equipment includes wiring.

2. Include diagrams for power, signal, and control wiring.

1.3 INFORMATIONAL SUBMITTALS

Retain first paragraph below if required by seismic criteria applicable to Project. Coordinate with Section 230548 "Vibration and Seismic Controls for HVAC."

A. Manufacturer Seismic Qualification Certification: Submit certification that boiler, accessories, and components will withstand seismic forces defined in Section 230548 "Vibration and Seismic Controls for HVAC."

B. Source quality-control reports.

Retain "Field quality-control reports" Paragraph below if Contractor is responsible for field quality-control testing and inspecting.

C. Field quality-control reports.

D. Warranty: Special warranty specified in this Section.

1.4 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

1.5 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

B. ASME Compliance: Fabricate and label boilers to comply with ASME Boiler and Pressure Vessel Code.

"ASHRAE/IESNA 90.1 Compliance" Paragraph may be required to comply with Project requirements or authorities having jurisdiction. Also, LEED Prerequisite EA 2 requires compliance with ASHRAE/IESNA 90.1.

C. ASHRAE/IESNA 90.1 Compliance: Boilers shall have minimum efficiency according to "Gas and Oil Fired Boilers - Minimum Efficiency Requirements."

Delete first paragraph below if boiler rating exceeds 300,000 Btu/h (87.9 kW).

D. DOE Compliance: Minimum efficiency shall comply with 10 CFR 430, Subpart B, Appendix N, "Uniform Test Method for Measuring the Energy Consumption of Furnaces and Boilers."

E. UL Compliance: Test boilers for compliance with UL 795, "Commercial-Industrial Gas Heating Equipment." Boilers shall be listed and labeled by a testing agency acceptable to authorities having jurisdiction.

1.6 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this Article are not less than remedies available to Owner under prevailing local laws. Coordinate with Section 016000 "Product Requirements." See discussion about warranties in "Common Boiler Characteristics" Article in the Evaluations in Section 235200 "Heating Boilers."

A. Special Warranty: Manufacturer's standard form in which manufacturer agrees to repair or replace components of boilers that fail in materials or workmanship within specified warranty period.

Verify available warranties for units and components and insert number below.

1. Warranty Period for Pulse-Combustion Boilers:

a. Heat Exchanger Damaged by Thermal Shock: [10] <Insert number> years from date of Substantial Completion.

b. Heat-Exchanger Corrosion: [Prorated] [Nonprorated] for [five] <Insert number> years from date of Substantial Completion.

2. Warranty Period for Fire-Tube Condensing Boilers:

a. Leakage and Materials: [10] <Insert number> years from date of Substantial Completion.

b. Heat Exchanger Damaged by Thermal Stress and Corrosion: [Prorated] [Nonprorated] for [five] <Insert number> years from date of Substantial Completion.

3. Warranty Period for Water-Tube Condensing Boilers: [20] <Insert number> years from date of Substantial Completion.

4. Warranty Period for Water-Jacketed Condensing Boilers:

a. Leakage and Materials: [Eight] <Insert number> years from date of Substantial Completion.

b. Heat Exchanger Damaged by Thermal Stress and Corrosion: [Prorated] [Nonprorated] for [five] <Insert number> years from date of Substantial Completion.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations in Section 235200 "Heating Boilers" for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

2.1 PULSE-COMBUSTION CONDENSING BOILERS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Fulton Boiler Works, Inc.

2. Gasmaster Industries Incorporated.

3. Hydrotherm, Inc.

4. <Insert manufacturer's name>.

C. Description: Factory-fabricated, -assembled, and -tested, pulse-combustion condensing boiler with heat exchanger sealed pressure tight, built on a steel base; including insulated jacket; flue-gas vent; combustion-air intake connections; water supply, return, and condensate drain connections; and controls.

Retain first option in first paragraph below if boiler operates at less than 140-degree return-water temperature.

D. Heat Exchanger: [Type 316L, stainless-steel] [Carbon-steel] primary and secondary combustion chamber.

E. Pressure Vessel: Carbon steel with welded heads and tube connections.

F. Exhaust Decoupler: Fiberglass composite material in a corrosion-resistant steel box.

G. Burner: [Natural] [Propane] gas, self-aspirating and self-venting after initial start.

H. Blower: Centrifugal fan to operate only during start of each burner sequence.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Section 230513 "Common Motor Requirements for HVAC Equipment." If different characteristics are required, add subparagraphs below to suit Project.

1. Motors: Comply with requirements specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

a. Motor Sizes: Minimum size as indicated. If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

I. Gas Train: Combination gas valve with manual shutoff and pressure regulator.

J. Ignition: Spark ignition with 100 percent main-valve shutoff with electronic flame supervision.

K. Casing:

1. Jacket: Sheet metal, with snap-in or interlocking closures.

2. Control Compartment Enclosure: NEMA 250, Type 1A.

3. Finish: [Baked-enamel] [Powder-coated] protective finish.

4. Insulation: Minimum 2-inch- (50-mm-) thick, mineral-fiber insulation surrounding the heat exchanger.

5. Draft Hood: [Integral] [External].

6. Combustion-Air Connection: Inlet duct collar and sheet metal closure over burner compartment.

7. Mounting base to secure boiler to concrete base.

Retain subparagraph below for projects in seismic areas. If retaining, also retain "Manufacturer Seismic Qualification Certification" Paragraph in Part 1 "Informational Submittals" Article.

a. Seismic Fabrication Requirements: Fabricate mounting base and attachment to boiler pressure vessel, accessories, and components with reinforcement strong enough to withstand seismic forces defined in Section 230548 "Vibration and Seismic Controls for HVAC" when mounting base is anchored to building structure.

L. Mufflers: Carbon-steel intake muffler and stainless-steel exhaust.

M. Condensate Trap: Cast-iron body with stainless-steel internal parts.

If Project has more than one type or configuration of boiler, delete paragraph and subparagraphs below and schedule boilers on Drawings.

N. Characteristics and Capacities:

1. Heating Medium: Hot water.

2. Design Water Pressure Rating: [15 psig (104 kPa)] [150 psig (1035 kPa)] <Insert pressure rating>.

3. Safety Relief Valve Setting: <Insert psig (kPa).>

4. Entering-Water Temperature: <Insert deg F (deg C).>

5. Leaving-Water Temperature: <Insert deg F (deg C).>

6. Design Water Flow Rate: <Insert gpm (L/s).>

7. Minimum Water Flow Rate: <Insert gpm (L/s).>

8. Design Pressure Drop: <Insert psig (kPa).>

Retain one of three subparagraphs below. Specify standing or intermittent pilot with minimum AFUE. LEED Prerequisite EA 1 requires compliance with ASHRAE/IESNA 90.1. LEED Credit EA 1 requires efficiency in excess of minimum efficiency required by ASHRAE/IESNA 90.1.

9. Minimum Efficiency AFUE: <Insert number> percent.

10. Minimum Thermal Efficiency: <Insert number> percent.

11. Minimum Combustion Efficiency: <Insert number> percent.

Retain one of first two subparagraphs below.

12. AGA Input: <Insert MBh (kW).>

Consider actual Btu content of fuel source if retaining subparagraph below. Contact fuel supplier and boiler manufacturers to determine impact. Add text indicating Btu content of fuel if applicable.

13. Gas Input: <Insert cfh (mL/s).>

Retain one of three subparagraphs below for rating methods.

14. AGA Output Capacity: <Insert MBh (kW).>

15. DOE Output Capacity: <Insert MBh (kW).>

16. Equivalent Direct Radiation: <Insert EDR (W).>

Consider impact of site altitude on fan and motor.

17. Blower:

a. Motor Horsepower: <Insert value.>

b. RPM: <Insert value.>

18. Electrical Characteristics:

a. Volts: [115] [208] [230] [460] <Insert value> V.

b. Phase: [Single] [Three].

c. Hertz: [50] [60].

d. Full-Load Amperes: <Insert value.>

e. Minimum Circuit Ampacity: <Insert value.>

f. Maximum Overcurrent Protection: <Insert amperage.>

2.2 FIRE-TUBE CONDENSING BOILERS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. AERCO International.

2. Bosch Thermotechnology Corp.

3. Heat Transfer Products, Inc.

4. <Insert manufacturer's name>.

C. Description: Factory-fabricated, -assembled, and -tested, fire-tube condensing boiler with heat exchanger sealed pressure tight, built on a steel base; including insulated jacket; flue-gas vent; combustion-air intake connections; water supply, return, and condensate drain connections; and controls. Water heating service only.

D. Heat Exchanger: Nonferrous, corrosion-resistant combustion chamber.

E. Pressure Vessel: Carbon steel with welded heads and tube connections.

F. Burner: [Natural] [Propane] gas, forced draft.

G. Blower: Centrifugal fan to operate during each burner firing sequence and to prepurge and postpurge the combustion chamber.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Section 230513 "Common Motor Requirements for HVAC Equipment." If different characteristics are required, add subparagraphs below to suit Project.

1. Motors: Comply with requirements specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

a. Motor Sizes: Minimum size as indicated. If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

H. Gas Train: Combination gas valve with manual shutoff and pressure regulator.

I. Ignition: Spark ignition with 100 percent main-valve shutoff with electronic flame supervision.

J. Casing:

1. Jacket: [Sheet metal] [Plastic], with snap-in or interlocking closures.

2. Control Compartment Enclosures: NEMA 250, Type 1A.

If retaining second option in "Jacket" Subparagraph above, delete first subparagraph below.

3. Finish: [Baked-enamel] [Powder-coated] protective finish.

4. Insulation: Minimum 2-inch- (50-mm-) thick, [mineral-fiber] [polyurethane-foam] insulation surrounding the heat exchanger.

5. Combustion-Air Connections: Inlet and vent duct collars.

6. Mounting base to secure boiler.

Retain subparagraph below for projects in seismic areas. If retaining, also retain "Manufacturer Seismic Qualification Certification" Paragraph in Part 1 "Informational Submittals" Article.

a. Seismic Fabrication Requirements: Fabricate mounting base and attachment to boiler pressure vessel, accessories, and components with reinforcement strong enough to withstand seismic forces defined in Section 230548 "Vibration and Seismic Controls for HVAC" when mounting base is anchored to building structure.

If Project has more than one type or configuration of boiler, delete paragraph and subparagraphs below and schedule boilers on Drawings.

K. Characteristics and Capacities:

1. Heating Medium: Hot water.

2. Design Water Pressure Rating: [160 psig (1100 kPa)] <Insert value>.

3. Safety Relief Valve Setting: <Insert psig (kPa).>

4. Entering-Water Temperature: <Insert deg F (deg C).>

5. Leaving-Water Temperature: <Insert deg F (deg C).>

6. Design Water Flow Rate: <Insert gpm (L/s).>

7. Minimum Water Flow Rate: <Insert gpm (L/s).>

8. Design Pressure Drop: <Insert psig (kPa).>

Retain one of three subparagraphs below. Specify standing or intermittent pilot with minimum AFUE. LEED Prerequisite EA 1 requires compliance with ASHRAE/IESNA 90.1. LEED Credit EA 1 requires efficiency in excess of minimum efficiency required by ASHRAE/IESNA 90.1.

9. Minimum Efficiency AFUE: <Insert number> percent.

10. Minimum Thermal Efficiency: <Insert number> percent.

11. Minimum Combustion Efficiency: <Insert number> percent.

Retain one of first two subparagraphs below.

12. AGA Input: <Insert MBh (kW).>

Consider actual Btu content of fuel source if retaining subparagraph below. Contact fuel supplier and boiler manufacturers to determine impact. Add text indicating Btu content of fuel if applicable.

13. Gas Input: <Insert cfh (mL/s).>

Retain one of three subparagraphs below for rating methods.

14. AGA Output Capacity: <Insert MBh (kW).>

15. DOE Output Capacity: <Insert MBh (kW).>

16. Equivalent Direct Radiation: <Insert EDR (W).>

Consider impact of site altitude on fan and motor.

17. Blower:

a. Motor Horsepower: <Insert value.>

b. RPM: <Insert value.>

18. Electrical Characteristics:

a. Volts: [115] [208] [230] [460] <Insert value> V.

b. Phase: [Single] [Three].

c. Hertz: [50] [60].

d. Full-Load Amperes: <Insert value.>

e. Minimum Circuit Ampacity: <Insert value.>

f. Maximum Overcurrent Protection: <Insert amperage.>

2.3 WATER-TUBE CONDENSING BOILERS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Laars Heating Systems Company.

2. Lochinvar Corporation.

3. <Insert manufacturer's name>.

C. Description: Factory-fabricated, -assembled, and -tested, water-tube condensing boiler with heat exchanger sealed pressure tight, built on a steel base; including insulated jacket; flue-gas vent; combustion-air intake connections; water supply, return, and condensate drain connections; and controls. Water heating service only.

D. Heat Exchanger: Finned-copper primary and stainless-steel secondary heat exchangers.

E. Combustion Chamber: Stainless steel, sealed.

F. Burner: [Natural] [Propane] gas, forced draft drawing from gas premixing valve.

G. Blower: Centrifugal fan to operate during each burner firing sequence and to prepurge and postpurge the combustion chamber.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Section 230513 "Common Motor Requirements for HVAC Equipment." If different characteristics are required, add subparagraphs below to suit Project.

1. Motors: Comply with requirements specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

a. Motor Sizes: Minimum size as indicated. If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

H. Gas Train: Combination gas valve with manual shutoff and pressure regulator.

I. Ignition: Silicone carbide hot-surface ignition that includes flame safety supervision and 100 percent main-valve shutoff.

J. Integral Circulator: Cast-iron body and stainless-steel impeller sized for minimum flow required in heat exchanger.

K. Casing:

1. Jacket: Sheet metal, with snap-in or interlocking closures.

2. Control Compartment Enclosures: NEMA 250, Type 1A.

3. Finish: Textured epoxy.

4. Insulation: Minimum [1-inch- (25-mm-)] [2-inch- (50-mm-)] thick, mineral-fiber insulation surrounding the heat exchanger.

5. Combustion-Air Connections: Inlet and vent duct collars.

6. Mounting base to secure boiler.

Retain subparagraph below for projects in seismic areas. If retaining, also retain "Manufacturer Seismic Qualification Certification" Paragraph in Part 1 "Informational Submittals" Article.

a. Seismic Fabrication Requirements: Fabricate mounting base and attachment to boiler pressure vessel, accessories, and components with reinforcement strong enough to withstand seismic forces defined in Section 230548 "Vibration and Seismic Controls for HVAC" when mounting base is anchored to building structure.

If Project has more than one type or configuration of boiler, delete paragraph and subparagraphs below and schedule boilers on Drawings.

L. Characteristics and Capacities:

1. Heating Medium: Hot water.

2. Design Water Pressure Rating: [160 psig (1100 kPa)] <Insert value>.

3. Safety Relief Valve Setting: <Insert psig (kPa).>

4. Entering-Water Temperature: <Insert deg F (deg C).>

5. Leaving-Water Temperature: <Insert deg F (deg C).>

6. Design Water Flow Rate: <Insert gpm (L/s).>

7. Minimum Water Flow Rate: <Insert gpm (L/s).>

8. Design Pressure Drop: <Insert psig (kPa).>

Retain one of three subparagraphs below. Specify standing or intermittent pilot with minimum AFUE. LEED Prerequisite EA 1 requires compliance with ASHRAE/IESNA 90.1. LEED Credit EA 1 requires efficiency in excess of minimum efficiency required by ASHRAE/IESNA 90.1.

9. Minimum Efficiency AFUE: <Insert number> percent.

10. Minimum Thermal Efficiency: <Insert number> percent.

11. Minimum Combustion Efficiency: <Insert number> percent.

Retain one of first two subparagraphs below.

12. AGA Input: <Insert MBh (kW).>

Consider actual Btu content of fuel source if retaining subparagraph below. Contact fuel supplier and boiler manufacturers to determine impact. Add text indicating Btu content of fuel if applicable.

13. Gas Input: <Insert cfh (mL/s).>

Retain one of two subparagraphs below for rating methods.

14. AGA Output Capacity: <Insert MBh (kW).>

15. DOE Output Capacity: <Insert MBh (kW).>

Consider impact of site altitude on fan and motor.

16. Blower:

a. Motor Horsepower: <Insert value.>

b. RPM: <Insert value.>

17. Electrical Characteristics:

a. Volts: [115] [208] [230] [460] <Insert value> V.

b. Phase: [Single] [Three].

c. Hertz: [50] [60].

d. Full-Load Amperes: <Insert value.>

e. Minimum Circuit Ampacity: <Insert value.>

f. Maximum Overcurrent Protection: <Insert amperage.>

2.4 WATER-JACKETED CONDENSING BOILERS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Viessmann Manufacturing Company Inc.

2. <Insert manufacturer's name>.

C. Description: Factory-fabricated, -assembled, and -tested, water-jacketed condensing boiler with heat exchanger sealed pressure tight, built on a steel base; including insulated jacket; flue-gas vent; water supply, return, and condensate drain connections; and controls. Water heating service only.

D. Heat Exchanger: Stainless-steel primary and secondary combustion chamber.

E. Pressure Vessel: Carbon steel with welded heads and tube connections where not in contact with combustion or flue gases.

F. Burner: [Natural] [Propane] gas, forced draft; swing-open front and burner observation port.

G. Blower: Centrifugal fan, forced draft. Include prepurge and postpurge of the combustion chamber.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Section 230513 "Common Motor Requirements for HVAC Equipment." If characteristics other than those in "Motors" Section are required, add subparagraphs below to suit Project.

1. Motors: Comply with requirements specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

a. Motor Sizes: Minimum size as indicated. If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

H. Gas Train: Combination gas valve with manual shutoff and pressure regulator. Include 100 percent safety shutoff with electronic flame supervision.

I. Ignition: Electric-spark ignition with 100 percent main-valve shutoff with electronic flame supervision.

J. Casing:

1. Jacket: Sheet metal, with snap-in or interlocking closures.

2. Control Compartment Enclosures: NEMA 250, Type 1A.

3. Finish: Powder-coated protective finish.

4. Insulation: Minimum 4-inch- (100-mm-) thick, mineral-fiber insulation surrounding the heat exchanger.

5. Combustion-Air Connections: Inlet and vent duct collars.

6. Mounting base to secure boiler.

Retain subparagraph below for projects in seismic areas. If retaining, also retain "Manufacturer Seismic Qualification Certification" Paragraph in Part 1 "Informational Submittals" Article.

a. Seismic Fabrication Requirements: Fabricate mounting base and attachment to boiler pressure vessel, accessories, and components with reinforcement strong enough to withstand seismic forces defined in Section 230548 "Vibration and Seismic Controls for HVAC" when mounting base is anchored to building structure.

If Project has more than one type or configuration of boiler, delete paragraph and subparagraphs below and schedule boilers on Drawings.

K. Characteristics and Capacities:

1. Heating Medium: Hot water.

2. Design Water Pressure Rating: [30 psig (207 kPa)] <Insert value>.

3. Safety Relief Valve Setting: <Insert psig (kPa).>

4. Maximum Design Temperature: 210 deg F (99 deg C).

5. Entering-Water Temperature: <Insert deg F (deg C).>

6. Leaving-Water Temperature: <Insert deg F (deg C).>

7. Design Water Flow Rate: <Insert gpm (L/s).>

8. Design Pressure Drop: <Insert psig (kPa).>

Retain one of three subparagraphs below. Specify standing or intermittent pilot with minimum AFUE. LEED Prerequisite EA 1 requires compliance with ASHRAE/IESNA 90.1. LEED Credit EA 1 requires efficiency in excess of minimum efficiency required by ASHRAE/IESNA 90.1.

9. Minimum Efficiency AFUE: <Insert number> percent.

10. Minimum Thermal Efficiency: <Insert number> percent.

11. Minimum Combustion Efficiency: <Insert number> percent.

Retain one of first two subparagraphs below.

12. AGA Input: <Insert MBh (kW).>

Consider actual Btu content of fuel source if retaining subparagraph below. Contact fuel supplier and boiler manufacturers to determine impact. Add text indicating Btu content of fuel if applicable.

13. Gas Input: <Insert cfh (mL/s).>

Retain one of three subparagraphs below for rating methods.

14. AGA Output Capacity: <Insert MBh (kW).>

15. DOE Output Capacity: <Insert MBh (kW).>

16. Equivalent Direct Radiation: <Insert EDR (W).>

Consider impact of site altitude on fan and motor.

17. Blower:

a. Motor Horsepower: <Insert value.>

b. RPM: <Insert value.>

18. Electrical Characteristics:

a. Volts: [115] [208] [230] [460] <Insert value> V.

b. Phase: [Single] [Three].

c. Hertz: [50] [60].

d. Full-Load Amperes: <Insert value.>

e. Minimum Circuit Ampacity: <Insert value.>

f. Maximum Overcurrent Protection: <Insert amperage.>

2.5 TRIM

In paragraph below, retain first option if boiler operating pressure exceeds 160 psig (1100 kPa) or boiler temperature exceeds 250 deg F (121 deg C).

A. Include devices sized to comply with [ANSI B31.1, "Power Piping] [ANSI B31.9, "Building Services Piping]."

Retain option in first paragraph below if using modulating or low-high-low firing sequence.

B. Aquastat Controllers: Operating[, firing rate,] and high limit.

C. Safety Relief Valve: ASME rated.

D. Pressure and Temperature Gage: Minimum 3-1/2-inch- (89-mm-) diameter, combination water-pressure and -temperature gage. Gages shall have operating-pressure and -temperature ranges so normal operating range is about 50 percent of full range.

E. Boiler Air Vent: [Automatic] [Manual].

F. Drain Valve: Minimum NPS 3/4 (DN 20) hose-end gate valve.

Retain paragraph below if pump is a component of boiler. Coordinate with Section 232123 "Hydronic Pumps."

G. Circulation Pump: Non-overloading, in-line pump with split-capacitor motor having thermal-overload protection and lubricated bearings; designed to operate at specified boiler pressures and temperatures.

2.6 CONTROLS

Retain paragraph below if controls are specified in Section 230900 "Instrumentation and Control for HVAC."

A. Refer to Section 230900 "Instrumentation and Control for HVAC."

Delete paragraph above and retain first two paragraphs and associated subparagraphs below if controls are components of boilers. Coordinate with Section 230900 "Instrumentation and Control for HVAC."

B. Boiler operating controls shall include the following devices and features:

1. Control transformer.

2. Set-Point Adjust: Set points shall be adjustable.

Retain one of two subparagraphs below for operating control sequences.

3. Sequence of Operation: Electric, factory-fabricated and field-installed panel to control burner firing rate to maintain space temperature in response to thermostat with heat anticipator located in heated space.

4. Sequence of Operation: Electric, factory-fabricated and field-installed panel to control burner firing rate to reset supply-water temperature inversely with outside-air temperature. At [0 deg F (minus 17 deg C)] <Insert temperature> outside-air temperature, set supply-water temperature at [200 deg F (93 deg C)] <Insert temperature>; at [60 deg F (15 deg C)] <Insert temperature> outside-air temperature, set supply-water temperature at [140 deg F (60 deg C)] <Insert temperature>.

Retain subparagraph below with either "Sequence of Operation" Subparagraph above.

a. Include automatic, alternating-firing sequence for multiple boilers to ensure maximum system efficiency throughout the load range and to provide equal runtime for boilers.

C. Burner Operating Controls: To maintain safe operating conditions, burner safety controls limit burner operation.

1. High Cutoff: [Manual] [Automatic] reset stops burner if operating conditions rise above maximum boiler design temperature.

2. Low-Water Cutoff Switch: Electronic probe shall prevent burner operation on low water. Cutoff switch shall be [manual] [automatic]-reset type.

3. Blocked Inlet Safety Switch: Manual-reset pressure switch field mounted on boiler combustion-air inlet.

4. Audible Alarm: Factory mounted on control panel with silence switch; shall sound alarm for above conditions.

Retain paragraph and subparagraphs below if boiler controls interface with building automation system.

D. Building Automation System Interface: Factory install hardware and software to enable building automation system to monitor, control, and display boiler status and alarms.

Retain subparagraph and associated subparagraphs below if interface with building automation system is through hardwired points and minimal interface is required. If extensive interface is required, delete below and retain second subparagraph below.

1. Hardwired Points:

a. Monitoring: On/off status, [common trouble alarm] [low water level alarm] <Insert monitoring>.

b. Control: On/off operation[, hot water supply temperature set-point adjustment].

Retain subparagraph below if extensive interface with building automation system is required and is beyond that than can be provided by hardwired points. Requirement may exclude some manufacturers listed.

2. A communication interface with building automation system shall enable building automation system operator to remotely control and monitor the boiler from an operator workstation. Control features available, and monitoring points displayed, locally at boiler control panel shall be available through building automation system.

2.7 ELECTRICAL POWER

Retain one of two paragraphs and associated subparagraphs in this article. Retain first if single-point field power connection is not applicable; retain second if single-point field power connection is applicable.

A. Controllers, Electrical Devices, and Wiring: Electrical devices and connections are specified in electrical Sections.

B. Single-Point Field Power Connection: Factory-installed and -wired switches, motor controllers, transformers, and other electrical devices necessary shall provide a single-point field power connection to boiler.

1. House in NEMA 250, Type [1] <Insert type> enclosure.

2. Wiring shall be numbered and color-coded to match wiring diagram.

3. Install factory wiring outside of an enclosure in a [metal ]raceway.

4. Field power interface shall be to [wire lugs] [fused disconnect switch] [nonfused disconnect switch] [circuit breaker].

5. Provide branch power circuit to each motor and to controls[ with a disconnect switch or circuit breaker].

6. Provide each motor with overcurrent protection.

2.8 VENTING KITS

Some boiler manufacturers offer venting kits that can be included with boiler. Retain this article if venting kit is included with boiler; otherwise, specify kit in Section 235100 "Breechings, Chimneys, and Stacks."

A. Kit: Complete system, ASTM A 959, Type 29-4C stainless steel, pipe, vent terminal, thimble, indoor plate, vent adapter, condensate trap and dilution tank, and sealant.

B. Combustion-Air Intake: Complete system, stainless steel, pipe, vent terminal with screen, inlet air coupling, and sealant.

2.9 SOURCE QUALITY CONTROL

A. Burner and Hydrostatic Test: Factory adjust burner to eliminate excess oxygen, carbon dioxide, oxides of nitrogen emissions, and carbon monoxide in flue gas and to achieve combustion efficiency; perform hydrostatic test.

B. Test and inspect factory-assembled boilers, before shipping, according to ASME Boiler and Pressure Vessel Code.

PART 3 -  EXECUTION

3.1 BOILER INSTALLATION

A. Equipment Mounting:

Retain first subparagraph below to require equipment to be installed on cast-in-place concrete equipment bases.

1. Install boilers on cast-in-place concrete equipment base(s). Comply with requirements for equipment bases and foundations specified in [Section 033000 "Cast-in-Place Concrete."] [Section 033053 "Miscellaneous Cast-in-Place Concrete."]

Retain one of two subparagraphs below. Retain first for projects in seismic areas; retain second for projects not in seismic areas. Indicate vibration isolation and seismic-control device type and minimum deflection in supported equipment schedule on Drawings.

2. Comply with requirements for vibration isolation and seismic control devices specified in Section 230548 "Vibration and Seismic Controls for HVAC."

3. Comply with requirements for vibration isolation devices specified in Section 230548.13 "Vibration Controls for HVAC."

B. Install gas-fired boilers according to NFPA 54.

C. Assemble and install boiler trim.

D. Install electrical devices furnished with boiler but not specified to be factory mounted.

E. Install control wiring to field-mounted electrical devices.

3.2 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Piping installation requirements are specified in other Sections. Drawings indicate general arrangement of piping, fittings, and specialties.

B. Install piping adjacent to boiler to allow service and maintenance.

C. Install piping from equipment drain connection to nearest floor drain. Piping shall be at least full size of connection. Provide an isolation valve if required.

D. Connect piping to boilers, except safety relief valve connections, with flexible connectors of materials suitable for service. Flexible connectors and their installation are specified in Section 232116 "Hydronic Piping Specialties."Section 15179 "Hydronic Piping Specialties."

E. Connect gas piping to boiler gas-train inlet with union. Piping shall be at least full size of gas train connection. Provide a reducer if required.

F. Connect hot-water piping to supply- and return-boiler tappings with shutoff valve and union or flange at each connection.

G. Install piping from safety relief valves to nearest floor drain.

H. Boiler Venting:

1. Install flue venting kit and combustion-air intake.

Delete option in subparagraph below if vent kit is specified in this Section.

2. Connect full size to boiler connections.[ Comply with requirements in Section 235100 "Breechings, Chimneys, and Stacks."]

I. Ground equipment according to Section 260526 "Grounding and Bonding for Electrical Systems."

J. Connect wiring according to Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

3.3 FIELD QUALITY CONTROL

Retain "Testing Agency," "Manufacturer's Field Service," and "Perform the following tests and inspections" paragraphs below to identify who shall perform tests and inspections. If retaining second option in "Testing Agency" Paragraph or if retaining "Manufacturer's Field Service" or "Perform the following tests and inspections" Paragraph, retain "Field quality-control reports" Paragraph in "Informational Submittals" Article.

A. Testing Agency: [Owner will engage] [Engage] a qualified testing agency to perform tests and inspections.

Retain "Manufacturer's Field Service" Paragraph below to require a factory-authorized service representative to perform tests and inspections.

B. Manufacturer's Field Service: Engage a factory-authorized service representative to test and inspect components, assemblies, and equipment installations, including connections.

Retain "Perform the following tests and inspections" Paragraph below to require Contractor to perform tests and inspections.

C. Perform the following tests and inspections[ with the assistance of a factory-authorized service representative]:

1. Perform installation and startup checks according to manufacturer's written instructions.

2. Leak Test: Hydrostatic test. Repair leaks and retest until no leaks exist.

3. Operational Test: Start units to confirm proper motor rotation and unit operation. Adjust air-fuel ratio and combustion.

4. Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.

a. Check and adjust initial operating set points and high- and low-limit safety set points of fuel supply, water level, and water temperature.

b. Set field-adjustable switches and circuit-breaker trip ranges as indicated.

D. Remove and replace malfunctioning units and retest as specified above.

E. Prepare test and inspection reports.

F. Occupancy Adjustments: When requested within [12 months of date of Substantial Completion] <Insert time period>, provide on-site assistance in adjusting system to suit actual occupied conditions. Provide up to [two] <Insert number> visits to Project during other than normal occupancy hours for this purpose.

3.4 DEMONSTRATION

A. [Engage a factory-authorized service representative to train] [Train] Owner's maintenance personnel to adjust, operate, and maintain boilers.[ Video training sessions.] Refer to Section 017900 "Demonstration and Training."

END OF SECTION 235216

	CONDENSING BOILERS
	235216 - 1



