Copyright 2012 AIA
MasterSpec Professional
03/12

Copyright 2012 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 235223 - CAST-IRON BOILERS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. This Section includes packaged, factory-fabricated and -assembled, gas-fired, cast-iron boilers, trim, and accessories for generating hot water.

1.2 ACTION SUBMITTALS

A. Product Data: Include performance data, operating characteristics, furnished specialties, and accessories.

B. Shop Drawings: For boilers, boiler trim, and accessories. Include plans, elevations, sections, details, and attachments to other work.

Retain first subparagraph and associated subparagraphs below if boilers are required to withstand specific design loads and Architect either has delegated design responsibility to Contractor or wants to review structural data as another way to verify boiler's compliance with performance requirements. Professional engineer qualifications are specified in Section 014000 "Quality Requirements."

1. Design calculations and vibration isolation base details, signed and sealed by a qualified professional engineer.

a. Design Calculations: Calculate requirements for selecting vibration isolators and seismic restraints and for designing vibration isolation bases.

b. Vibration Isolation Base Details: Detail fabrication including anchorages and attachments to structure and to supported equipment. Include auxiliary motor slides and rails and equipment mounting frames.

2. Wiring Diagrams: Power, signal, and control wiring.

1.3 INFORMATIONAL SUBMITTALS

Retain first paragraph below if required by seismic criteria applicable to Project. Coordinate with Section 230548 "Vibration and Seismic Controls for HVAC."

A. Manufacturer Seismic Qualification Certification: Submit certification that boiler, accessories, and components will withstand seismic forces defined in Section 230548 "Vibration and Seismic Controls for HVAC."

B. Source quality-control test reports.

C. Field quality-control test reports.

D. Warranty: Special warranty specified in this Section.

1.4 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

1.5 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

B. ASME Compliance: Fabricate and label boilers to comply with ASME Boiler and Pressure Vessel Code.

"ASHRAE/IESNA 90.1 Compliance" Paragraph may be required to comply with Project requirements or authorities having jurisdiction. Also, LEED Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1. LEED Credit EA 1 requires efficiency in excess of minimum efficiency required by ASHRAE/IESNA 90.1.

C. ASHRAE/IESNA 90.1 Compliance: Boilers shall have minimum efficiency according to "Gas and Oil Fired Boilers - Minimum Efficiency Requirements."

Delete first paragraph below if boiler rating exceeds 300,000 Btu/h (87.9 kW).

D. DOE Compliance: Minimum efficiency shall comply with 10 CFR 430, Subpart B, Appendix N, "Uniform Test Method for Measuring the Energy Consumption of Furnaces and Boilers."

E. I=B=R Compliance: Boilers shall be tested and rated according to HI's "Rating Procedure for Heating Boilers" and "Testing Standard for Commercial Boilers," with I=B=R emblem on a nameplate affixed to boiler.

F. UL Compliance: Test boilers for compliance with UL 795, "Commercial-Industrial Gas Heating Equipment." Boilers shall be listed and labeled by a testing agency acceptable to authorities having jurisdiction.

1.6 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this Article are not less than remedies available to Owner under prevailing local laws. Coordinate with Section 016000 "Product Requirements." See discussion about warranties in "Common Boiler Characteristics" Article in the Evaluations in Section 235200 "Heating Boilers."

A. Special Warranty: Manufacturer's standard form in which manufacturer agrees to repair or replace controls and heat exchangers of boilers that fail in materials or workmanship within specified warranty period.

Verify available warranties for units and components and insert number below.

1. Warranty Period for Controls: [Two] <Insert number> years from date of Substantial Completion.

2. Warranty Period for Heat Exchangers: [Five] [10] [20] <Insert number> years from date of Substantial Completion.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations in Section 235200 "Heating Boilers" for cautions about naming manufacturers and products. Retain one of three paragraphs and list of manufacturers in this Article. See Section 016000 "Product Requirements."

A. Available Manufacturers: Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product: Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Burnham Hydronics.

2. Crown Boiler Co.

3. Hydrotherm, Inc./Mestek, Inc.

4. Lennox Industries Inc.

5. Peerless Boilers.

6. Slant/Fin Corp.

7. Smith Cast Iron Boilers.

8. Viessmann Manufacturing Co. (US) Inc.

9. Weil-McLain.

10. <Insert manufacturer's name.>

2.2 MANUFACTURED UNITS

A. Description: Factory fabricated.

1. Cast-iron sections shall be sealed pressure tight and held together with tie rods[ set on an insulated steel base]; including insulated jacket and flue-gas vent connection.

B. Cast-Iron Section Design:

1. Configuration: Wet [base] [back] [leg].

2. Number of Passes: [Single] [Multiple].

3. Sectional Joints: High-temperature sealant to seal flue-gas passages not in contact with heating medium, [tapered cast-iron push nipples,] [O-ring gaskets,] [fiber roping,] and held together with tie rods.

4. Drain and blowdown tappings.

5. Return injection tube to equalize water flow to all sections.

6. Crown inspection tappings with brass plugs.

Separator in subparagraph below is available only in small residential-size boilers. Verify availability with manufacturer.

7. Built-in air separator.

C. Combustion Chamber: Equipped with [ceramic-fiber target wall] [refractory] [insulation] [and] flame observation ports, front and back.

D. Casing:

1. Jacket: [Galvanized sheet] [Sheet] metal, with snap-in or interlocking closures and [baked-enamel] [powder-coated] protective finish.

2. Insulation: Minimum [1-inch- (25-mm-)] [2-inch- (50-mm-)] thick, mineral-fiber insulation surrounding the heat exchanger.

Feature in first subparagraph below is unique for some boiler manufacturers.

3. Combustion Chamber Access: Refractory lined, hinged, front.

4. Access: For cleaning between cast-iron sections.

5. Draft Hood: Flue canopy and [top] [rear] flue connection shall be constructed of [aluminized] [stainless] steel containing adjustable outlet damper assembly.

Delete first subparagraph below if boiler design permits.

6. Insulated base constructed of aluminized steel to permit boiler to be installed on combustible floor.

7. Mounting Frame: Steel rails to mount assembled boiler package on concrete base.

Retain subparagraph below for projects in seismic areas. If retaining, also retain "Manufacturer Seismic Qualification Certification" Paragraph in Part 1 "Informational Submittals" Article.

a. Seismic Fabrication Requirements: Fabricate mounting base and attachment to boiler, accessories, and components with reinforcement strong enough to withstand seismic forces defined in Section 230548 "Vibration and Seismic Controls for HVAC" when mounting base is anchored to building structure.

Cabinet in subparagraph below is available only in residential natural-draft boilers.

8. Control Cabinet: Sheet metal casing shall cover all controls, gas train, and burner.

2.3 BURNER

A. Burner Tubes and Orifices: [Stainless steel] [Cast iron], for [natural] [propane] gas.

Retain one of two "Gas Train" paragraphs below. First applies to commercial boilers; second applies to residential boilers. Retain any of three control sequences with any of four safety requirements.

B. Gas Train: Control devices and [full-modulation] [on-off] [low-high-low] control sequence shall comply with requirements in [ASME CSD-1] [FMG] [IRI] [UL].

C. Gas Train: Combination gas valve with manual shutoff, pressure regulator, and pilot adjustment.

D. Pilot: [Standing] [Intermittent-electric-spark] pilot ignition with 100 percent main-valve and pilot-safety shutoff with electronic supervision of burner flame.

2.4 TRIM

A. Include devices sized to comply with ANSI B31.9, "Building Services Piping."

Retain option in first paragraph below if using modulating or low-high-low firing sequence.

B. Aquastat Controllers: Operating[, firing rate,] and high limit.

C. Safety Relief Valve: ASME rated.

D. Pressure and Temperature Gage: Minimum 3-1/2-inch- (89-mm-) diameter, combination water-pressure and -temperature gage. Gages shall have operating-pressure and -temperature ranges so normal operating range is about 50 percent of full range.

E. Boiler Air Vent: [Automatic] [Manual].

F. Drain Valve: Minimum NPS 3/4 (DN 20) hose-end gate valve.

2.5 CONTROLS

Retain paragraph below if controls are specified in Section 230900 "Instrumentation and Control for HVAC."

A. Refer to Section 230900 "Instrumentation and Control for HVAC."

Delete paragraph above and retain first two paragraphs and associated subparagraphs below if controls are components of boilers. Coordinate with Section 230900 "Instrumentation and Control for HVAC."

B. Boiler operating controls shall include the following devices and features:

1. Control transformer.

2. Set-Point Adjust: Set points shall be adjustable.

Retain one of two subparagraphs below for operating control sequences.

3. Sequence of Operation: Electric, factory-fabricated and field-installed panel to control burner firing rate to maintain space temperature in response to thermostat with heat anticipator located in heated space.

4. Sequence of Operation: Electric, factory-fabricated and field-installed panel to control burner firing rate to reset supply-water temperature inversely with outside-air temperature. At [0 deg F (minus 17 deg C)] <Insert temperature> outside-air temperature, set supply-water temperature at [200 deg F (93 deg C)] <Insert temperature>; at [60 deg F (15 deg C)] <Insert temperature> outside-air temperature, set supply-water temperature at [140 deg F (60 deg C)] <Insert temperature>.

Retain subparagraph below with either "Sequence of Operation" Subparagraph above.

a. Include automatic, alternating-firing sequence for multiple boilers.

C. Burner Operating Controls: To maintain safe operating conditions, burner safety controls limit burner operation.

1. High Cutoff: [Manual] [Automatic] reset stops burner if operating conditions rise above maximum boiler design temperature.

2. Low-Water Cutoff Switch: Electronic probe shall prevent burner operation on low water. Cutoff switch shall be [manual] [automatic]-reset type.

Some boilers may be equipped with only one of two switches below. Verify availability with boiler manufacturer.

3. Blocked Vent Safety Switch: Manual-reset switch factory mounted on draft diverter.

4. Rollout Safety Switch: Factory mounted on boiler combustion chamber.

5. Audible Alarm: Factory mounted on control panel with silence switch; shall sound alarm for above conditions.

Retain paragraph and subparagraphs below if boiler controls interface with building management system.

D. Building Management System Interface: Factory install hardware and software to enable building management system to monitor, control, and display boiler status and alarms.

Retain subparagraph and associated subparagraphs below if interface with building management system is through hardwired points and minimal interface is required. If extensive interface is required, delete below and retain second subparagraph below.

1. Hardwired Points:

a. Monitoring: On/off status, [common trouble alarm] [low water level alarm] <Insert monitoring>.

b. Control: On/off operation[, hot water supply temperature set-point adjustment].

Retain subparagraph below if extensive interface with building management system is required and is beyond that than can be provided by hardwired points. Requirement may exclude some manufacturers listed.

2. A communication interface with building management system shall enable building management system operator to remotely control and monitor the boiler from an operator workstation. Control features available, and monitoring points displayed, locally at boiler control panel shall be available through building management system.

2.6 ELECTRICAL POWER

Retain one of two paragraphs and associated subparagraphs in this Article. Retain first if single-point field power connection is not applicable; retain second if single-point field power connection is applicable.

A. Controllers, Electrical Devices, and Wiring: Electrical devices and connections are specified in electrical Sections.

B. Single-Point Field Power Connection: Factory-installed and -wired switches, motor controllers, transformers, and other electrical devices necessary shall provide a single-point field power connection to boiler.

1. House in NEMA 250, Type [1] <Insert type> enclosure.

2. Wiring shall be numbered and color-coded to match wiring diagram.

3. Install factory wiring outside of an enclosure in a [metal ]raceway.

4. Field power interface shall be to [wire lugs] [fused disconnect switch] [nonfused disconnect switch] [circuit breaker].

5. Provide branch power circuit to each motor and to controls[ with disconnect switch or circuit breaker].

6. Provide each motor with overcurrent protection.

2.7 CAPACITIES AND CHARACTERISTICS

If Project has more than one type or configuration of boiler, delete this Article and schedule boilers on Drawings.

A. Heating Medium: Hot water.

B. Design Water Pressure Rating: [30 psig (207 kPa)] [50 psig (345 kPa)] [80 psig (550 kPa)] <Insert pressure rating>.

C. Safety Relief Valve Setting: <Insert psig (kPa).>

D. Entering-Water Temperature: <Insert deg F (deg C).>

E. Leaving-Water Temperature: <Insert deg F (deg C).>

F. Design Water Flow Rate: <Insert gpm (L/s).>

G. Design Pressure Drop: <Insert psig (kPa).>

Retain one of first three paragraphs below. Specify standing or intermittent pilot with minimum AFUE. LEED Prerequisite EA 1 requires compliance with ASHRAE/IESNA 90.1. LEED Credit EA 1 requires efficiency in excess of minimum efficiency required by ASHRAE/IESNA 90.1.

H. Minimum Efficiency AFUE: <Insert number> percent.

I. Minimum Thermal Efficiency: <Insert number> percent.

J. Minimum Combustion Efficiency: <Insert number> percent.

K. Number of Passes: [One] [Two] <Insert number>.

Retain one of first three paragraphs below.

L. AGA Input: <Insert MBh (kW).>

M. I=B=R Input: <Insert MBh (kW).>

Consider actual Btu content of fuel source if retaining paragraph below. Contact fuel supplier and boiler manufacturers to determine impact. Add text indicating Btu content of fuel if applicable.

N. Gas Input: <Insert cfh (mL/s).>

Retain one of first five paragraphs below for rating methods.

O. AGA Output Capacity: <Insert MBh (kW).>

P. DOE Output Capacity: <Insert MBh (kW).>

Q. Net I=B=R Output Capacity: <Insert MBh (kW).>

R. Gross I=B=R Output Capacity: <Insert MBh (kW).>

S. Equivalent Direct Radiation: <Insert EDR (W).>

T. Electrical Characteristics:

1. Volts: [115] <Insert value> V.

2. Phase: Single.

3. Hertz: [50] [60].

4. Full-Load Amperes: <Insert value.>

5. Minimum Circuit Ampacity: <Insert value.>

6. Maximum Overcurrent Protection: <Insert amperage.>

2.8 SOURCE QUALITY CONTROL

Factory tests are an additional cost item.

A. Test and inspect factory-assembled boilers, before shipping, according to ASME Boiler and Pressure Vessel Code.

B. Burner and Hydrostatic Test: Factory adjust burner to eliminate excess oxygen, carbon dioxide, oxides of nitrogen emissions, and carbon monoxide in flue gas and to achieve combustion efficiency; perform hydrostatic test.

PART 3 -  EXECUTION

3.1 BOILER INSTALLATION

A. Equipment Mounting:

Retain first subparagraph below to require equipment to be installed on cast-in-place concrete equipment bases.

1. Install boilers on cast-in-place concrete equipment base(s). Comply with requirements for equipment bases and foundations specified in [Section 033000 "Cast-in-Place Concrete."] [Section 033053 "Miscellaneous Cast-in-Place Concrete."]

Retain one of two subparagraphs below. Retain first for projects in seismic areas; retain second for projects not in seismic areas. Indicate vibration isolation and seismic-control device type and minimum deflection in supported equipment schedule on Drawings.

2. Comply with requirements for vibration isolation and seismic control devices specified in Section 230548 "Vibration and Seismic Controls for HVAC."

3. Comply with requirements for vibration isolation devices specified in Section 230548.13 "Vibration Controls for HVAC."

B. Install gas-fired boilers according to NFPA 54.

C. Assemble and install boiler trim.

D. Install electrical devices furnished with boiler but not specified to be factory mounted.

E. Install control wiring to field-mounted electrical devices.

3.2 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Piping installation requirements are specified in other Sections. Drawings indicate general arrangement of piping, fittings, and specialties.

B. Install piping adjacent to boiler to allow service and maintenance.

C. Connect gas piping to boiler gas-train inlet with union. Piping shall be at least full size of gas train connection. Provide a reducer if required.

D. Connect hot-water piping to supply- and return-boiler tappings with shutoff valve and union or flange at each connection.

E. Install piping from safety relief valves to nearest floor drain.

F. Install piping from equipment drain connection to nearest floor drain. Piping shall be at least full size of connection. Provide an isolation valve if required.

G. Connect breeching full size to boiler outlet. Comply with requirements in Section 235100 "Breechings, Chimneys, and Stacks" for venting materials.

H. Install flue-gas recirculation duct from vent to burner. Comply with requirements in Section 235100 "Breechings, Chimneys, and Stacks" for recirculation duct materials.

I. Ground equipment according to Section 260526 "Grounding and Bonding for Electrical Systems."

J. Connect wiring according to Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

3.3 FIELD QUALITY CONTROL

A. Perform tests and inspections and prepare test reports.

Retain subparagraph below to require a factory-authorized service representative to assist Contractor with inspections, tests, and adjustments.

1. Manufacturer's Field Service: Engage a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

B. Tests and Inspections:

1. Perform installation and startup checks according to manufacturer's written instructions.

2. Leak Test: Hydrostatic test. Repair leaks and retest until no leaks exist.

3. Operational Test: Start units to confirm proper motor rotation and unit operation. Adjust air-fuel ratio and combustion.

4. Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.

a. Check and adjust initial operating set points and high- and low-limit safety set points of fuel supply, water level, and water temperature.

b. Set field-adjustable switches and circuit-breaker trip ranges as indicated.

C. Remove and replace malfunctioning units and retest as specified above.

D. Occupancy Adjustments: When requested within [12 months of date of Substantial Completion] <Insert time period>, provide on-site assistance in adjusting system to suit actual occupied conditions. Provide up to [two] <Insert number> visits to Project during other than normal occupancy hours for this purpose.

3.4 DEMONSTRATION

A. [Engage a factory-authorized service representative to train] [Train] Owner's maintenance personnel to adjust, operate, and maintain boilers.[ Video training sessions.] Refer to Section 017900 "Demonstration and Training."

END OF SECTION 235223

	CAST-IRON BOILERS
	235223 - 1



