Copyright 2012 AIA
MasterSpec Professional
03/12

Copyright 2012 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 235233 - WATER-TUBE BOILERS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

Retain one of two paragraphs below. See Evaluations for a comparison of finned water-tube, steel water-tube, and flexible water-tube boilers.

A. This Section includes packaged, factory-fabricated and -assembled, gas-fired, finned water-tube boilers, trim, and accessories for generating hot water.

B. This Section includes packaged, factory-fabricated and -assembled, [atmospheric-gas] [forced-draft gas]-fired, water-tube boilers, trim, and accessories for generating hot water.

1.2 ACTION SUBMITTALS

A. Product Data: Include performance data, operating characteristics, furnished specialties, and accessories.

B. Shop Drawings: For boilers, boiler trim, and accessories. Include plans, elevations, sections, details, and attachments to other work.

Retain subparagraph and associated subparagraphs below if boilers are required to withstand specific design loads and Architect either has delegated design responsibility to Contractor or wants to review structural data as another way to verify boiler's compliance with performance requirements. Professional engineer qualifications are specified in Section 014000 "Quality Requirements."

1. Design calculations and vibration isolation base details, signed and sealed by a qualified professional engineer.

a. Design Calculations: Calculate requirements for selecting vibration isolators and seismic restraints and for designing vibration isolation bases.

b. Vibration Isolation Base Details: Detail fabrication including anchorages and attachments to structure and to supported equipment. Include auxiliary motor slides and rails and equipment mounting frames.

2. Wiring Diagrams: Power, signal, and control wiring.

1.3 INFORMATIONAL SUBMITTALS

Retain first paragraph below if required by seismic criteria applicable to Project. Coordinate with Section 230548 "Vibration and Seismic Controls for HVAC."

A. Manufacturer Seismic Qualification Certification: Submit certification that boiler, accessories, and components will withstand seismic forces defined in Section 230548 "Vibration and Seismic Controls for HVAC."

B. Source quality-control test reports.

C. Field quality-control test reports.

D. Warranty: Special warranty specified in this Section.

1.4 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

1.5 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

B. ASME Compliance: Fabricate and label boilers to comply with ASME Boiler and Pressure Vessel Code.

"ASHRAE/IESNA 90.1 Compliance" Paragraph may be required to comply with Project requirements or authorities having jurisdiction. Also, LEED Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1.

C. ASHRAE/IESNA 90.1 Compliance: Boilers shall have minimum efficiency according to "Gas and Oil Fired Boilers - Minimum Efficiency Requirements."

Retain first two paragraphs below for finned water-tube boilers. Delete first paragraph if boiler rating exceeds 300,000 Btu/h (87.9 kW).

D. DOE Compliance: Minimum efficiency shall comply with 10 CFR 430, Subpart B, Appendix N, "Uniform Test Method for Measuring the Energy Consumption of Furnaces and Boilers."

E. I=B=R Compliance: Boilers shall be tested and rated according to HI's "Rating Procedure for Heating Boilers" and "Testing Standard for Commercial Boilers," with I=B=R emblem on a nameplate affixed to boiler.

F. UL Compliance: Test boilers for compliance with UL 795, "Commercial-Industrial Gas Heating Equipment." Boilers shall be listed and labeled by a testing agency acceptable to authorities having jurisdiction.

1.6 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this Article are not less than remedies available to Owner under prevailing local laws. Coordinate with Section 016000 "Product Requirements." See discussion about warranties in "Common Boiler Characteristics" Article in the Evaluations in Section 235200 "Heating Boilers."

Retain one of two paragraphs below. Retain first for finned water-tube boilers.

A. Special Warranty: Manufacturer's standard form in which manufacturer agrees to repair or replace heat exchangers damaged by thermal shock and vent dampers of boilers that fail in materials or workmanship within specified warranty period.

Verify available warranties for units and components and insert number below.

1. Warranty Period for Heat Exchangers: [20] <Insert number> years from date of Substantial Completion.

2. Warranty Period for Vent Dampers: [Five] <Insert number> years from date of Substantial Completion.

B. Special Warranty: Manufacturer's standard form in which manufacturer agrees to repair or replace drums, tubes, headers, cabinets, atmospheric gas burners, and pressure vessels of boilers that fail in materials or workmanship within specified warranty period.

Verify available warranties for units and components and insert number below.

1. Warranty Period for Drums, Tubes, Headers, Cabinets, and Atmospheric Gas Burner: [Five] <Insert number> years from date of Substantial Completion, pro rata.

2. Warranty Period for Pressure Vessel: [20] <Insert number> years from date of Substantial Completion, for thermal shock.

PART 2 -  PRODUCTS

2.1 FINNED WATER-TUBE BOILERS

See Editing Instruction No. 1 in the Evaluations in Section 235200 "Heating Boilers" for cautions about naming manufacturers and products. Retain one of first three paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Available Manufacturers: Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product: Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. A. O. Smith Corporation.

2. Ajax Boiler Inc.

3. Allied Engineering Co.

4. Laars Heating Systems.

5. Lochinvar Corporation.

6. Patterson-Kelley.

7. PRECISION Boilers, LLC.

8. Raypak.

9. RBI Water Heaters.

10. RECO USA.

11. Weben-Jarco, Inc.

12. <Insert manufacturer's name.>

D. Description: Factory-fabricated, -assembled, and -tested boiler with tubes sealed into headers pressure tight, and set on a steel base; including insulated jacket, flue-gas vent, combustion-air intake connections, water supply and return connections, and controls.

E. Heat Exchanger:

1. Finned [copper] [steel] [copper-nickel] tubing with stainless-steel baffles.

2. [Bronze] [Cast-iron] [Steel] headers.

3. [Single] [Two]-pass, [horizontal] [vertical] [coil] configuration.

4. Tubes shall be sealed in header [with silicone O-ring gaskets] [by welding] [by mechanically rolling tubes in header].

F. Combustion Chamber Internal Insulation: Interlocking panels of refractory insulation, high-temperature cements, mineral fiber, and ceramic refractory tile for service temperatures to 2000 deg F (1100 deg C).

G. Casing:

1. Jacket: [Sheet metal] [Stainless steel], with snap-in or interlocking closures.

2. Control Compartment Enclosure: NEMA 250, Type 1A.

Stainless-steel enclosures are typically not painted. If selecting stainless steel above, delete first subparagraph below.

3. Finish: [Baked enamel over primer] [Baked enamel over galvanizing] [Powder coated].

4. Insulation: Minimum [1-inch- (25-mm-)] [2-inch- (50-mm-)] thick, mineral-fiber insulation surrounding the heat exchanger.

Delete first subparagraph below if a direct vent burner is specified.

5. Draft Hood: [Integral] [External].

6. Combustion-Air Connection: Inlet duct collar and sheet metal closure over burner compartment.

7. Mounting base to secure boiler[ with accessory for mounting on combustible surface].

Retain subparagraph below for projects in seismic areas. If retaining, also retain "Manufacturer Seismic Qualification Certification" Paragraph in Part 1 "Informational Submittals" Article.

a. Seismic Fabrication Requirements: Fabricate mounting base and attachment to boiler pressure vessel, accessories, and components with reinforcement strong enough to withstand seismic forces defined in Section 230548 "Vibration and Seismic Controls for HVAC" when mounting base is anchored to building structure.

H. Burner:

1. Burner Tubes and Orifices: Stainless steel, for [natural] [propane] gas.[ Mount burner tubes in a slide-out burner drawer for ease of inspection.]

Retain applicable subparagraph(s) below for specified boiler. First is typically found on sealed combustion boilers. Second is typical with boilers vented through sidewalls. If conventional venting is specified, delete both.

a. Sealed Combustion: Factory-mounted centrifugal fan to draw outside air into boiler and discharge into burner compartment.

b. Direct Vent: Factory-mounted centrifugal fan to draw flue gas out of boiler and discharge into boiler vent.

2. Vertical Burner:

a. [High-temperature stainless steel] [Ceramic] to fire in a 360-degree pattern.

Filter option in first subparagraph below is required only for ceramic burner element.

b. Burner shall have a viewing port for observation of burner operation and a factory-mounted centrifugal fan to supply [room] [outside] air[ through a replaceable 99 percent efficient (1-micrometer particles) filter] to boiler burner.

c. Fan shall be controlled to prepurge and postpurge the combustion chamber before firing.

Retain one of two "Gas Train" subparagraphs below. First applies to commercial boilers; retain any of four control sequences with any of five safety requirements. Second paragraph applies to residential boilers.

3. Gas Train: Control devices and [full-modulation] [on-off] [low-high-low] [proportional] control sequence shall comply with requirements in [AGA] [ASME CSD-1] [FMG] [IRI] [UL]. In addition to these requirements, include shutoff cock, pressure regulator, and control valve.

4. Gas Train: Combination gas valve with manual shutoff, pressure regulator, and pilot adjustment.

5. Pilot: [Standing] [Intermittent-electric-spark] [Hot-surface] pilot ignition with 100 percent main-valve and pilot-safety shutoff with electronic supervision of burner flame.

6. Flue-Gas Recirculation Fans: Centrifugal fans on burner assembly to recirculate flue gas to decrease oxides of nitrogen emissions to less than [30] <Insert value> ppm.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Section 230513 "Common Motor Requirements for HVAC Equipment." If different characteristics are required, add subparagraphs below to suit Project.

a. Motors: Comply with requirements specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

I. Trim:

Retain option in first subparagraph below if using modulating or low-high-low firing sequence.

1. Aquastat Controllers: Operating[, firing rate,] and high limit.

2. Safety Relief Valve: ASME rated.

3. Pressure and Temperature Gage: Minimum 3-1/2-inch- (89-mm-) diameter, combination water-pressure and -temperature gage. Gages shall have operating-pressure and -temperature ranges so normal operating range is about 50 percent of full range.

4. Boiler Air Vent: [Automatic] [Manual].

5. Drain Valve: Minimum NPS 3/4 (DN 20) hose-end gate valve.

Retain subparagraph below if pump is a component of boiler. Coordinate with Section 232123 "Hydronic Pumps."

6. Circulation Pump: Non-overloading, in-line pump with split-capacitor motor having thermal-overload protection and lubricated bearings; designed to operate at specified boiler pressures and temperatures.

J. Controls:

Retain subparagraph below if controls are specified in Section 230900 "Instrumentation and Control for HVAC."

1. Refer to Section 230900 "Instrumentation and Control for HVAC."

Delete subparagraph above and retain first two subparagraphs and associated subparagraphs below if controls are components of boilers. Coordinate with Section 230900 "Instrumentation and Control for HVAC."

2. Boiler operating controls shall include the following devices and features:

a. Control transformer.

Motorized vent dampers in first subparagraph below are provided only on residential boilers.

b. Motorized Vent Damper: Interlocked with burner to open before burner starts. If damper fails to open, stop burner operation.

c. Set-Point Adjust: Set points shall be adjustable.

Retain one of first two subparagraphs below for operating control sequences.

d. Sequence of Operation: Electric, factory-fabricated and field-installed panel to control burner firing rate to maintain space temperature in response to thermostat with heat anticipator located in heated space.

e. Sequence of Operation: Electric, factory-fabricated and field-installed panel to control burner firing rate to reset supply-water temperature inversely with outside-air temperature. At [0 deg F (minus 17 deg C)] <Insert temperature> outside-air temperature, set supply-water temperature at [200 deg F (93 deg C)] <Insert temperature>; at [60 deg F (15 deg C)] <Insert temperature> outside-air temperature, set supply-water temperature at [140 deg F (60 deg C)] <Insert temperature>.

f. Include automatic, alternating-firing sequence for multiple boilers to ensure maximum system efficiency throughout the load range and to provide equal runtime for boilers.

3. Burner Operating Controls: To maintain safe operating conditions, burner safety controls limit burner operation.

a. High Cutoff: [Manual] [Automatic] reset stops burner if operating conditions rise above maximum boiler design temperature.

b. Water Flow Switch: Automatic-reset paddle-switch shall prevent burner operation on low water flow.

First two subparagraphs below apply to atmospheric burners. Some boilers may be equipped with only one of two switches below. Verify availability with boiler manufacturer.

c. Blocked Vent Safety Switch: Manual-reset switch factory mounted on draft diverter.

d. Rollout Safety Switch: Factory mounted on boiler combustion chamber.

e. Audible Alarm: Factory mounted on control panel with silence switch; shall sound alarm for above conditions.

Retain subparagraph below if boiler controls interface with building automation system.

4. Building Automation System Interface: Factory install hardware and software to enable building automation system to monitor, control, and display boiler status and alarms.

Retain two subparagraphs below if interface with building automation system is through hardwired points and minimal interface is required.

a. Monitoring: On/off status, [common trouble alarm] [low water level alarm] <Insert monitoring>.

b. Control: On/off operation[, hot water supply temperature set-point adjustment].

Delete last two subparagraphs above and retain subparagraph below if extensive interface with building automation system is required and is beyond what can be provided by hardwired points. Requirement may exclude some manufacturers listed.

c. A communication interface with building automation system shall enable building automation system operator to remotely control and monitor the boiler from an operator workstation. Control features available, and monitoring points displayed, locally at boiler control panel shall be available through building automation system.

2.2 [STEEL] [FLEXIBLE] WATER-TUBE BOILERS

See Editing Instruction No. 1 in the Evaluations in Section 235200 "Heating Boilers" for cautions about naming manufacturers and products. Retain one of first three paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Available Manufacturers: Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product: Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. AESYS Technologies, LLC.

2. Ajax Boiler Inc.

3. Bryan Steam LLC.

4. Cleaver-Brooks.

5. Parker Boiler Co.

6. Rite Engineering & Mfg. Corp.

7. <Insert manufacturer's name.>

D. Description: Factory-fabricated and -assembled, water-tube boiler with heat exchanger sealed pressure tight, built on a steel base; including insulated jacket, flue-gas vent, supply and return connections, and controls.

Retain one of first two paragraphs and subparagraphs below for heat-exchanger design. Retain first for straight-tube design; second, for bent-tube design.

E. Heat-Exchanger Design: Straight steel tubes rolled into steel headers.

1. Accessible head plates at both ends.

2. Handholes[ or couplings] in headers for water-side inspections.

3. Accessible drain and blowdown tappings, both high and low, for surface and mud removal.

4. Lifting lugs on top of boiler.

5. Built-in air separator.

F. Heat-Exchanger Design: Bent steel tubes [swaged] [welded] into steel headers[ with membrane waterwall design].

Retain first subparagraph below to limit tube configurations; otherwise, delete.

1. Limit tube configurations to [two] [four] <Insert number>.

2. Accessible drain and blowdown tappings, both high and low, for surface and mud removal.

3. Accessible inspection ports in drum, mud legs, and tube manifolds.

4. Lifting lugs on top of boiler.

5. Built-in air separator.

The need for refractory insulation around the combustion chamber is reduced by a membrane waterwall (tube-wall) construction design offered by some manufacturers.

G. Combustion Chamber: Equipped with minimum [2-1/2-inch (64-mm)] [3-inch (75-mm)] [4-inch (100-mm)], 2700 deg F (1482 deg C) poured refractory on floor and minimum [2-inch (50-mm)] [3-1/2-inch (89-mm)] lap-jointed cast refractory with fiber-blanket joint seals on side walls. Combustion chamber shall have flame observation ports in front [and] [or] back.

H. Casing:

1. Insulation: Minimum[ 2-inch (50-mm) thick, lightweight refractory; 1-inch (25-mm) thick insulating board; galvanized-steel membrane, and] 2-inch (50-mm) thick, mineral-fiber insulation surrounding the heat exchanger and combustion chamber.

2. Top Flue Connection: Constructed of [aluminized] [stainless] steel.

Retain one of first two subparagraphs below.

3. Jacket: Mirror-finish stainless steel, with screw-fastened closures.

4. Jacket: [Galvanized ]sheet metal, with screw-fastened closures and [baked-enamel] [powder-coated] protective finish.

5. Mounting base to secure boiler to concrete base.

Retain first subparagraph below for projects in seismic areas. If retaining, also retain "Manufacturer Seismic Qualification Certification" Paragraph in Part 1 "Informational Submittals" Article.

a. Seismic Fabrication Requirements: Fabricate mounting base and attachment to boiler, accessories, and components with reinforcement strong enough to withstand seismic forces defined in Section 230548 "Vibration and Seismic Controls for HVAC" when mounting base is anchored to building structure.

6. Control Compartment Enclosure: NEMA 250, Type 1A.

Retain second option in paragraph below if boiler is forced-draft type. Retain first option for atmospheric burner.

I. [Draft Diverter] [Barometric Damper]: Galvanized-steel assembly with flue-gas thermometer.

Retain one of two "Burner" paragraphs below. Retain first for atmospheric gas burners.

J. Burner:

1. Burner and Orifices: [Stainless steel] [Cast iron], for [natural] [propane] gas.

Retain one of two "Gas Train" subparagraphs below. First applies to commercial boilers; retain any of three control sequences with any of five safety requirements. Second paragraph applies to residential boilers. Availability of three control sequences listed depends on boiler capacity. Consult boiler manufacturer.

2. Gas Train: Control devices and [full-modulation] [on-off] [low-high-low] control sequence shall comply with requirements in [AGA] [ASME CSD-1] [FMG] [IRI] [UL].

3. Gas Train: Combination gas valve with manual shutoff, pressure regulator, and pilot adjustment.

4. Pilot: [Standing] [Intermittent-electric-spark] pilot ignition with 100 percent main-valve and pilot-safety shutoff with electronic supervision of burner flame.

Retain first paragraph below for forced-draft gas burners.

K. Burner:

1. Burner: Welded construction with multivane, stainless-steel, flame-retention diffuser for [natural] [propane] gas.[ Mount burner on hinged access door to permit access to combustion chamber.]

2. Blower: Forward-curved, centrifugal fan integral to burner, directly driven by motor; with adjustable, dual-blade damper assembly and locking quadrant to set air-fuel ratio.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Section 230513 "Common Motor Requirements for HVAC Equipment." If different characteristics are required, add subparagraphs below to suit Project.

a. Motors: Comply with requirements specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

In first subparagraph below, retain any of three control sequences with any of five safety requirements. Availability of three control sequences listed depends on boiler capacity. Consult boiler manufacturer.

3. Gas Train: Control devices and [modulating] [on-off] [low-high-low] control sequence shall comply with requirements in [AGA] [ASME CSD-1] [FMG] [IRI] [UL].

4. Pilot: [Intermittent] [Interrupted]-electric-spark pilot ignition with 100 percent main-valve and pilot-safety shutoff with electronic supervision of burner flame.

Retain subparagraph and associated subparagraph below to decrease oxides of nitrogen emissions. Not all manufacturers can comply with options listed below. Edit to suit Project.

5. Flue-Gas Recirculation: Burner connections shall be equipped for recirculating flue gas.

a. Maximum Oxides of Nitrogen Emissions: [30] <Insert value> ppm.

L. Trim:

In subparagraph below, retain first option if boiler operating pressure exceeds 160 psig (1100 kPa) or boiler temperature exceeds 250 deg F (120 deg C).

1. Include devices sized to comply with [ANSI B31.1, "Power Piping] [ANSI B31.9, "Building Services Piping]."

Retain option in first subparagraph below if using modulating or low-high-low firing sequence.

2. Aquastat Controllers: Operating[, firing rate,] and high limit.

3. Safety Relief Valve: ASME rated.

4. Pressure and Temperature Gage: Minimum 3-1/2-inch- (89-mm-) diameter, combination water-pressure and -temperature gage. Gages shall have operating-pressure and -temperature ranges so normal operating range is about 50 percent of full range.

5. Boiler Air Vent: [Automatic] [Manual].

6. Drain Valve: Minimum NPS 3/4 (DN 20) hose-end gate valve.

M. Controls:

Retain subparagraph below if controls are specified in Section 230900 "Instrumentation and Control for HVAC."

1. Refer to Section 230900 "Instrumentation and Control for HVAC."

Delete subparagraph above and retain first two subparagraphs and associated subparagraphs below if controls are components of boilers. Coordinate with Section 230900 "Instrumentation and Control for HVAC."

2. Boiler operating controls shall include the following devices and features:

a. Control transformer.

b. Set-Point Adjust: Set points shall be adjustable.

Retain one of two subparagraphs below for operating control sequences.

c. Sequence of Operation: Electric, factory-fabricated and field-installed panel to control burner firing rate to maintain space temperature in response to thermostat with heat anticipator located in heated space.

d. Sequence of Operation: Electric, factory-fabricated and field-installed panel to control burner firing rate to reset supply-water temperature inversely with outside-air temperature. At [0 deg F (minus 17 deg C)] <Insert temperature> outside-air temperature, set supply-water temperature at [200 deg F (93 deg C)] <Insert temperature>; at [60 deg F (15 deg C)] <Insert temperature> outside-air temperature, set supply-water temperature at [140 deg F (60 deg C)] <Insert temperature>.

Retain subparagraph below with either "Sequence of Operation" Subparagraph above.

e. Include automatic, alternating-firing sequence for multiple boilers to ensure maximum system efficiency throughout the load range and to provide equal runtime for boilers.

3. Burner Operating Controls: To maintain safe operating conditions, burner safety controls limit burner operation.

a. High Cutoff: [Manual] [Automatic] reset stops burner if operating conditions rise above maximum boiler design temperature.

b. Low-Water Cutoff Switch: Electronic probe shall prevent burner operation on low water. Cutoff switch shall be [manual] [automatic]-reset type.

First two subparagraphs below apply to atmospheric burners. Some boilers may be equipped with only one of two switches below. Verify availability with boiler manufacturer.

c. Blocked Vent Safety Switch: Manual-reset switch factory mounted on draft diverter.

d. Rollout Safety Switch: Factory mounted on boiler combustion chamber.

e. Audible Alarm: Factory mounted on control panel with silence switch; shall sound alarm for above conditions.

Retain subparagraph below if boiler controls interface with building automation system.

4. Building Automation System Interface: Factory install hardware and software to enable building automation system to monitor, control, and display boiler status and alarms.

Retain two subparagraphs below if interface with building automation system is through hardwired points and minimal interface is required.

a. Monitoring: On/off status, [common trouble alarm] [low water level alarm] <Insert monitoring>.

b. Control: On/off operation[, hot water supply temperature set-point adjustment].

Delete last two subparagraphs above and retain subparagraph below if extensive interface with building automation system is required and is beyond what can be provided by hardwired points. Requirement may exclude some manufacturers listed.

c. A communication interface with building automation system shall enable building automation system operator to remotely control and monitor the boiler from an operator workstation. Control features available, and monitoring points displayed, locally at boiler control panel shall be available through building automation system.

2.3 ELECTRICAL POWER

Retain one of two paragraphs and associated subparagraphs in this Article. Retain first if single-point field power connection is not applicable; retain second if single-point field power connection is applicable.

A. Controllers, Electrical Devices, and Wiring: Electrical devices and connections are specified in electrical Sections.

B. Single-Point Field Power Connection: Factory-installed and -wired switches, motor controllers, transformers, and other electrical devices necessary shall provide a single-point field power connection to boiler.

1. House in NEMA 250, Type [1] <Insert type> enclosure.

2. Wiring shall be numbered and color-coded to match wiring diagram.

3. Install factory wiring outside of an enclosure in a [metal ]raceway.

4. Field power interface shall be to [wire lugs] [fused disconnect switch] [nonfused disconnect switch] [circuit breaker].

5. Provide branch power circuit to each motor and to controls[ with disconnect switch or circuit breaker].

6. Provide each motor with overcurrent protection.

2.4 VENTING KITS

Retain this Article if venting kit is a component of boiler. Coordinate with Section 235100 "Breechings, Chimneys, and Stacks."

A. Vent Damper: Motorized, UL listed for use on atmospheric burner boiler equipped with draft hood; motor to open and close damper; stainless-steel vent coupling and damper blade; keyed wiring harness connector plug; and dual-position switches to permit burner operation.

Accessories in two paragraphs below can be included with boiler or specified in Section 235100 "Breechings, Chimneys, and Stacks." Retain option in first paragraph if boiler efficiency exceeds 83 percent.

B. Kit: Complete system, [ASTM A 959, Type 29-4C ]stainless steel, pipe, vent terminal, thimble, indoor plate, vent adapter, condensate trap, and sealant.

C. Combustion-Air Intake: Stainless steel, pipe, vent terminal with screen, inlet air coupling, and sealant.

2.5 CAPACITIES AND CHARACTERISTICS

If Project has more than one type or configuration of boiler, delete this Article and schedule boilers on Drawings.

A. Heating Medium: Hot water.

B. Design Pressure Rating: [60 psig (420 kPa)] [100 psig (690 kPa)] [140 psig (966 kPa)] [160 psig (1100 kPa)] <Insert value>.

C. Safety Relief Valve Setting: <Insert psig (kPa).>

D. Entering-Water Temperature: <Insert deg F (deg C).>

E. Leaving-Water Temperature: <Insert deg F (deg C).>

F. Design Water Flow Rate: <Insert gpm (L/s).>

G. Design Pressure Drop: <Insert psig (kPa).>

Retain one of first three paragraphs below. Specify standing or intermittent pilot with minimum AFUE. LEED Prerequisite EA 1 requires compliance with ASHRAE/IESNA 90.1. LEED Credit EA 1 requires efficiency in excess of minimum efficiency required by ASHRAE/IESNA 90.1.

H. Minimum Efficiency AFUE: <Insert number> percent.

I. Minimum Thermal Efficiency: <Insert number> percent.

J. Minimum Combustion Efficiency: <Insert number> percent.

K. Number of Passes: [One] [Two] <Insert number>.

Retain one of first three paragraphs below.

L. AGA Input: <Insert MBh (kW).>

M. I=B=R Input: <Insert MBh (kW).>

Consider actual Btu content of fuel source if retaining paragraph below. Contact fuel supplier and boiler manufacturers to determine impact. Add text indicating Btu content of fuel if applicable.

N. Gas Input: <Insert cfh (mL/s).>

Retain one of five paragraphs below for output rating methods. First paragraph applies to finned water-tube boilers.

O. DOE Output Capacity: <Insert MBh (kW).>

P. AGA Output Capacity: <Insert MBh (kW).>

Q. Net I=B=R Output Capacity: <Insert MBh (kW).>

R. Gross I=B=R Output Capacity: <Insert MBh (kW).>

S. Equivalent Direct Radiation: <Insert EDR (W).>

Consider impact of site altitude on fan and motor.

T. Burner Blower:

1. Motor Horsepower: <Insert value.>

2. RPM: <Insert value.>

U. Electrical Characteristics:

1. Volts: [115] [208] [230] [460] <Insert value> V.

2. Phase: [Single] [Three].

3. Hertz: [50] [60].

4. Full-Load Amperes: <Insert value.>

5. Minimum Circuit Ampacity: <Insert value.>

6. Maximum Overcurrent Protection: <Insert amperage.>

2.6 SOURCE QUALITY CONTROL

Factory tests are an additional cost item.

A. Test and inspect factory-assembled boilers, before shipping, according to ASME Boiler and Pressure Vessel Code.

B. Burner and Hydrostatic Test: Factory adjust burner to eliminate excess oxygen, carbon dioxide, oxides of nitrogen emissions, and carbon monoxide in flue gas and to achieve combustion efficiency; perform hydrostatic test.

PART 3 -  EXECUTION

3.1 BOILER INSTALLATION

A. Equipment Mounting:

Retain first subparagraph below to require equipment to be installed on cast-in-place concrete equipment bases.

1. Install boilers on cast-in-place concrete equipment base(s). Comply with requirements for equipment bases and foundations specified in [Section 033000 "Cast-in-Place Concrete."] [Section 033053 "Miscellaneous Cast-in-Place Concrete."]

Retain one of two subparagraphs below. Retain first for projects in seismic areas; retain second for projects not in seismic areas. Indicate vibration isolation and seismic-control device type and minimum deflection in supported equipment schedule on Drawings.

2. Comply with requirements for vibration isolation and seismic control devices specified in Section 230548 "Vibration and Seismic Controls for HVAC."

3. Comply with requirements for vibration isolation devices specified in Section 230548.13 "Vibration Controls for HVAC."

B. Install gas-fired boilers according to NFPA 54.

C. Assemble and install boiler trim.

D. Install electrical devices furnished with boiler but not specified to be factory mounted.

E. Install control wiring to field-mounted electrical devices.

3.2 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Piping installation requirements are specified in other Sections. Drawings indicate general arrangement of piping, fittings, and specialties.

B. Install piping adjacent to boiler to allow service and maintenance.

C. Connect gas piping to boiler gas-train inlet with union. Piping shall be at least full size of gas train connection. Provide a reducer if required.

D. Connect hot-water piping to supply- and return-boiler tappings with shutoff valve and union or flange at each connection.

E. Install piping from safety relief valves to nearest floor drain.

F. Install piping from equipment drain connection to nearest floor drain. Piping shall be at least full size of connection. Provide an isolation valve if required.

Retain first paragraph below for finned water-tube boilers provided with venting kits.

G. Boiler Flue Venting:

1. Install venting kit and combustion-air intake.

Edit subparagraph below to suit Project. Delete option if vent is specified in this Section.

2. Connect full size to boiler connections.[ Comply with requirements in Section 235100 "Breechings, Chimneys, and Stacks."]

H. Connect breeching to full size of boiler outlet. Comply with requirements in Section 235100 "Breechings, Chimneys, and Stacks" for venting materials.

I. Install flue-gas recirculation duct from vent to burner. Comply with requirements in Section 235100 "Breechings, Chimneys, and Stacks" for recirculation duct materials.

J. Ground equipment according to Section 260526 "Grounding and Bonding for Electrical Systems."

K. Connect wiring according to Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

3.3 FIELD QUALITY CONTROL

A. Perform tests and inspections and prepare test reports.

Retain subparagraph below to require a factory-authorized service representative to assist Contractor with inspections, tests, and adjustments.

1. Manufacturer's Field Service: Engage a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

B. Tests and Inspections:

1. Perform installation and startup checks according to manufacturer's written instructions.

2. Leak Test: Hydrostatic test. Repair leaks and retest until no leaks exist.

3. Operational Test: Start units to confirm proper motor rotation and unit operation. Adjust air-fuel ratio and combustion.

4. Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.

a. Check and adjust initial operating set points and high- and low-limit safety set points of fuel supply, water level, and water temperature.

b. Set field-adjustable switches and circuit-breaker trip ranges as indicated.

C. Remove and replace malfunctioning units and retest as specified above.

D. Occupancy Adjustments: When requested within [12 months of date of Substantial Completion] <Insert time period>, provide on-site assistance in adjusting system to suit actual occupied conditions. Provide up to [two] <Insert number> visits to Project during other than normal occupancy hours for this purpose.

3.4 DEMONSTRATION

A. [Engage a factory-authorized service representative to train] [Train] Owner's maintenance personnel to adjust, operate, and maintain boilers.[ Video training sessions.] Refer to Section 017900 "Demonstration and Training."

END OF SECTION 235233

	WATER-TUBE BOILERS
	235233 - 1



