Copyright 2012 AIA
MasterSpec Professional
03/12

Copyright 2012 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 235239 - FIRE-TUBE BOILERS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section includes packaged, factory-fabricated and -assembled, gas-fired, [horizontal] [fire-box], fire-tube boilers, trim, and accessories for generating [hot water] [steam].

1.2 ACTION SUBMITTALS

A. Product Data: Include performance data, operating characteristics, furnished specialties, and accessories.

B. Shop Drawings: For boilers, boiler trim, and accessories. Include plans, elevations, sections, details, and attachments to other work.

Retain subparagraph and associated subparagraphs below if boilers are required to withstand specific design loads and Architect either has delegated design responsibility to Contractor or wants to review structural data as another way to verify boiler's compliance with performance requirements. Professional engineer qualifications are specified in Section 014000 "Quality Requirements."

1. Design calculations and vibration isolation base details, signed and sealed by a qualified professional engineer.

a. Design Calculations: Calculate requirements for selecting vibration isolators and seismic restraints and for designing vibration isolation bases.

b. Vibration Isolation Base Details: Detail fabrication including anchorages and attachments to structure and to supported equipment. Include auxiliary motor slides and rails and equipment mounting frames.

Retain subparagraph below if equipment includes wiring.

2. Include diagrams for power, signal, and control wiring.

1.3 INFORMATIONAL SUBMITTALS

Retain first paragraph below if required by seismic criteria applicable to Project. Coordinate with Section 230548 "Vibration and Seismic Controls for HVAC."

A. Manufacturer Seismic Qualification Certification: Submit certification that boiler, accessories, and components will withstand seismic forces defined in Section 230548 "Vibration and Seismic Controls for HVAC."

B. Source quality-control reports.

Retain "Field quality-control reports" Paragraph below if Contractor is responsible for field quality-control testing and inspecting.

C. Field quality-control reports.

D. Warranty: Special warranty specified in this Section.

1.4 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

1.5 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

B. ASME Compliance: Fabricate and label boilers to comply with ASME Boiler and Pressure Vessel Code.

"ASHRAE/IESNA 90.1 Compliance" Paragraph may be required to comply with Project requirements or authorities having jurisdiction. Also, LEED Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1.

C. ASHRAE/IESNA 90.1 Compliance: Boilers shall have minimum efficiency according to "Gas and Oil Fired Boilers - Minimum Efficiency Requirements."

D. UL Compliance: Test Boilers for compliance with UL 795, "Commercial-Industrial Gas Heating Equipment." Boilers shall be listed and labeled by a testing agency acceptable to authorities having jurisdiction.

1.6 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this Article are not less than remedies available to Owner under prevailing local laws. Coordinate with Section 016000 "Product Requirements." See discussion about warranties in "Common Boiler Characteristics" Article in the Evaluations in Section 235200 "Heating Boilers."

A. Special Warranty: Manufacturer's standard form in which manufacturer agrees to repair or replace front- and rear-door refractories and heat exchangers of boilers that fail in materials or workmanship within specified warranty period.

Retain subparagraph below for horizontal, fire-tube and fire-box boilers only. The need for a refractory warranty depends on boiler design and is intended more for dryback boilers. Although front- and rear-door refractory warranties are available, a refractory warranty could penalize dryback boilers if both a dryback and a wetback boiler are allowed. Warranty should be reviewed with Owner and specified only when requested by Owner. Consult manufacturer to determine necessity for and availability of this warranty.

1. Horizontal, Fire-Tube and Fire-Box Boilers: Refractory in front and rear doors, [10] <Insert number> years from date of startup by factory-authorized personnel.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations in Section 235200 "Heating Boilers" for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

2.1 HORIZONTAL, FIRE-TUBE BOILERS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. AESYS Technologies, LLC.

2. Burnham Hydronics.

3. Cleaver-Brooks; div. of Aqua-Chem, Inc.

4. Hurst Boiler & Welding Company, Inc.

5. Iron Fireman Combustion Products.

6. Lattner Boiler Manufacturing.

7. L.E.S., Inc.

8. Sellers Engineering Co.

9. Superior Boiler Works, Inc.

10. <Insert manufacturer's name>.

C. Description: Factory-fabricated, -assembled, and -tested, horizontal, fire-tube boilers with heat exchanger sealed pressure tight, built on a steel base; including insulated jacket, flue-gas vent, water supply and return connections, and controls.

D. Pressure Vessel Design: Straight, steel tubes [rolled] [welded] into steel headers. [Three] [Four] passes with [dry] [wet]-back design. Minimum heat-exchanger surface of 5 sq. ft./bhp (2.1 sq. m/10 kW). Include the following accessories:

1. Handholes for water-side inspections.

2. Lifting lugs on top of boiler.

3. Minimum NPS 1 (DN 25) hose-end drain valves at shell low point.

Retain two subparagraphs below for hot-water boilers only.

4. Tappings or flanges for supply- and return-water piping.

5. Built-in air separator.

Retain two subparagraphs below for steam boilers only.

6. Accessible drain and blowdown tappings, both high and low, for surface and mud removal.

7. Tappings for steam supply, makeup, level controls, and chemical treatment.

Some boiler designs do not use refractory to insulate the doors. Verify door insulation with manufacturer.

E. Front and Rear Doors:

1. [Bolted] [Hinged] [Davited], sealed with heat-resistant gaskets and fastened with lugs and cap screws.

2. Designed so tube sheets and flues are fully accessible for inspection or cleaning when doors are open.

3. Include observation ports in doors at both ends of boiler for inspection of flame conditions.

4. Door [refractory] [insulation] shall be accessible for inspection and maintenance.

F. Casing:

1. Insulation: Minimum 2-inch- (50-mm-) thick, mineral-fiber insulation surrounding the boiler shell.

2. Flue Connection: Flange at top of boiler.

3. Jacket: [Galvanized sheet] [Sheet] metal, with screw-fastened closures and [baked-enamel] [powder-coated] protective finish.

4. Mounting base to secure boiler to concrete base.

Retain subparagraph below for projects in seismic areas. If retaining, also retain "Manufacturer Seismic Qualification Certification" Paragraph in Part 1 "Informational Submittals" Article.

a. Seismic Fabrication Requirements: Fabricate mounting base and attachment to boiler, accessories, and components with reinforcement strong enough to withstand seismic forces defined in Section 230548 "Vibration and Seismic Controls for HVAC" when mounting base is anchored to building structure.

Select one of four options in subparagraph below. Type 1 is the most common, and Type 12 is second. Type 4X is used primarily in corrosive environments.

5. Control Compartment Enclosure: NEMA 250, Type [1] [4] [4X] [12] <Insert type>.

Retain paragraph below if required by stack draft design conditions.

G. Barometric Damper: Galvanized-steel assembly with flue-gas thermometer having a minimum 3-1/2-inch- (89-mm-) diameter dial.

2.2 FIRE-BOX BOILERS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Hurst Boiler & Welding Company, Inc.

2. L.E.S., Inc.

3. <Insert manufacturer's name>.

C. Description: Factory-fabricated, -assembled, and -tested, fire-box boilers with heat exchanger sealed pressure tight, built on a steel base; including insulated jacket, flue-gas vent, water supply and return connections, and controls.

D. Pressure Vessel Design: Straight, steel tubes [rolled] [welded] into steel headers. Three passes with wet-back design. Minimum heat-exchanger surface of 5 sq. ft./bhp (2.1 sq. m/10 kW). Include the following features and accessories:

1. Tube Size and Thickness: [Minimum NPS 2 (DN 50), minimum 0.105 inch (2.667 mm) thick] <Insert size and thickness>.

2. Brass washout plugs.

3. Steel turbulators.

4. Lifting lugs on top of boiler.

5. Minimum NPS 1 (DN 25) hose-end drain valves at shell low point.

Retain two subparagraphs below for hot-water boilers only.

6. Tappings or flanges for supply- and return-water piping.

7. Built-in air separator.

Retain two subparagraphs below for steam boilers only.

8. Accessible drain and blowdown tappings, both high and low, for surface and mud removal.

9. Tappings for steam supply, makeup, level controls, and chemical treatment.

E. Combustion Chamber: Welded steel, [waterwall and -floor design] [water-leg design with refractory insulation poured in the floor]. Flame observation port.

F. Casing:

1. Insulation: Minimum 2-inch- (50-mm-) thick, [foil-backed, ]mineral-fiber insulation surrounding the boiler shell.

2. Insulated removable smoke boxes and reversing chamber cover.

3. Flue Connection: Steel [top] [rear].

4. Jacket: Sheet metal, with screw-fastened closures and [baked-enamel] [powder-coated] protective finish.

Select one of four options in first subparagraph below. Type 1 is the most common, and Type 12 is second. Type 4X is used primarily in corrosive environments.

5. Control Compartment Enclosure: NEMA 250, Type [1] [4] [4X] [12] <Insert type>.

6. Mounting base to secure boiler to concrete base.

Retain subparagraph below for projects in seismic areas. If retaining, also retain "Manufacturer Seismic Qualification Certification" Paragraph in Part 1 "Informational Submittals" Article.

a. Seismic Fabrication Requirements: Fabricate mounting base and attachment to boiler, accessories, and components with reinforcement strong enough to withstand seismic forces defined in Section 230548 "Vibration and Seismic Controls for HVAC Piping and Equipment" when mounting base is anchored to building structure.

Retain paragraph below if required by stack draft design conditions.

G. Barometric Damper: Galvanized-steel assembly with flue-gas thermometer having a minimum 3-1/2-inch- (89-mm-) diameter dial.

2.3 BURNER

A. Burner: Welded construction with multivane, stainless-steel, flame-retention diffuser for [natural] [propane] gas.[ Mount burner on hinged access door to permit access to combustion chamber.]

B. Blower: Forward-curved centrifugal fan integral to burner, directly driven by motor; with adjustable, dual-blade damper assembly and locking quadrant to set air-fuel ratio.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Section 230513 "Common Motor Requirements for HVAC Equipment." If different characteristics are required, add subparagraphs below to suit Project.

1. Motors: Comply with requirements specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

a. Motor Sizes: Minimum size as indicated. If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

In first paragraph below, retain any of three control sequences with any of four safety requirements. Availability of three control sequences listed depends on boiler capacity. Consult boiler manufacturer.

C. Gas Train: Control devices and [modulating] [on-off] [low-high-low] control sequence shall comply with requirements in [ASME CSD-1] [FMG] [IRI] [UL].

D. Pilot: [Intermittent] [Interrupted]-electric-spark pilot ignition with 100 percent main-valve and pilot-safety shutoff with electronic supervision of burner flame.

Retain paragraph and subparagraph below to decrease oxides of nitrogen emissions. Not all manufacturers can comply with options listed below. Edit to suit Project.

E. Flue-Gas Recirculation: Burner connections shall be equipped for recirculating flue gas.

1. Maximum Oxides of Nitrogen Emissions: [20] [30] <Insert value> ppm.

Retain one of two "Trim" articles below.

2.4 TRIM

Retain this article for hot-water boilers.

In paragraph below, retain first option if boiler operating pressure exceeds 160 psig (1100 kPa) or boiler temperature exceeds 250 deg F (120 deg C).

A. Include devices sized to comply with [ANSI B31.1, "Power Piping] [ANSI B31.9, "Building Services Piping]."

Retain option in first paragraph below if using modulating or low-high-low firing sequence.

B. Aquastat Controllers: Operating[, firing rate,] and high limit.

C. Safety Relief Valve: ASME rated.

D. Pressure and Temperature Gage: Minimum 3-1/2-inch- (89-mm-) diameter, combination water-pressure and -temperature gage. Gages shall have operating-pressure and -temperature ranges so normal operating range is about 50 percent of full range.

E. Boiler Air Vent: [Automatic] [Manual].

F. Drain Valve: Minimum NPS 3/4 (DN 20) hose-end gate valve.

2.5 TRIM

Retain this article for steam boilers.

In paragraph below, retain first option if boiler operating pressure exceeds 15 psig (104 kPa).

A. Include devices sized to comply with [ANSI B31.1, "Power Piping] [ANSI B31.9, "Building Services Piping]."

Retain option in paragraph below if using modulating or low-high-low firing sequence.

B. Pressure Controllers: Operating[, firing rate,] and high limit.

Retain first paragraph and subparagraphs below if safety valve is a component of boiler. Coordinate with Section 232216 "Steam and Condensate Piping Specialties."

C. Safety Relief Valve:

1. Size and Capacity: As required for equipment according to ASME Boiler and Pressure Vessel Code.

2. Description: Fully enclosed steel spring with adjustable pressure range and positive shutoff; factory set and sealed.

a. Drip-Pan Elbow: Cast iron and having threaded inlet and outlet with threads complying with ASME B1.20.1.

D. Pressure Gage: Minimum 3-1/2-inch (89-mm) diameter. Gage shall have normal operating pressure about 50 percent of full range.

E. Water Column: Minimum 12-inch (300-mm) glass gage with shutoff cocks.

F. Drain Valves: Minimum NPS 3/4 (DN 20) or nozzle size with hose-end connection.

In first paragraph below, retain option if boiler operating pressure exceeds 100 psig (690 kPa).

G. Blowdown Valves: Factory-installed bottom and surface, slow-acting blowdown valves same size as boiler nozzle.[ Blowdown valves shall be combination of slow and quick acting as required by ANSI B31.1.]

H. Stop Valves: Boiler inlets and outlets, except safety relief valves or preheater inlet and outlet, shall be equipped with stop valve in an accessible location as near as practical to boiler nozzle and same size or larger than nozzle. Valves larger than NPS 2 (DN 50) shall have rising stem.

Retain paragraph below for boilers equipped with manhole openings that operate at more than 15 psig (104 kPa) and supply steam to a common steam header with other boilers.

I. Stop-Check Valves: Factory-installed, stop-check valve and stop valve for field installation at boiler outlet with free-blow drain valve for field installation between the two valves and visible when operating stop-check valve.

2.6 CONTROLS

Retain paragraph below if controls are specified in Section 230900 "Instrumentation and Control for HVAC."

A. Refer to Section 230900 "Instrumentation and Control for HVAC."

Delete paragraph above and retain first two paragraphs and associated subparagraphs below if controls are components of boilers. Coordinate with Section 230900 "Instrumentation and Control for HVAC."

B. Boiler operating controls shall include the following devices and features:

1. Control transformer.

2. Set-Point Adjust: Set points shall be adjustable.

Retain two subparagraphs below for steam boilers.

3. Operating Pressure Control: Factory wired and mounted to cycle burner.

4. Low-Water Cutoff and Pump Control: Cycle feedwater pump(s) for makeup water control.

Retain one of three subparagraphs below for operating control sequences. Retain one of first two subparagraphs for hot-water boilers; or third, for steam boilers.

5. Sequence of Operation: Electric, factory-fabricated and field-installed panel to control burner firing rate to maintain space temperature in response to thermostat with heat anticipator located in heated space.

6. Sequence of Operation: Electric, factory-fabricated and field-installed panel to control burner firing rate to reset supply-water temperature inversely with outside-air temperature. At [0 deg F (minus 17 deg C)] <Insert temperature> outside-air temperature, set supply-water temperature at [200 deg F (93 deg C)] <Insert temperature>; at [60 deg F (15 deg C)] <Insert temperature> outside-air temperature, set supply-water temperature at [140 deg F (60 deg C)] <Insert temperature>.

7. Sequence of Operation: Electric, factory-fabricated and field-installed panel to control burner firing rate to maintain a constant steam pressure. Maintain pressure set point plus or minus 10 percent.

Retain subparagraph below with any of three "Sequence of Operation" subparagraphs above.

a. Include automatic, alternating-firing sequence for multiple boilers to ensure maximum system efficiency throughout the load range and to provide equal runtime for boilers.

C. Burner Operating Controls: To maintain safe operating conditions, burner safety controls limit burner operation.

In subparagraph below, retain "temperature" option for hot-water boiler and "pressure" option for steam boiler.

1. High Cutoff: [Manual] [Automatic] reset stops burner if operating conditions rise above maximum boiler design [temperature] [pressure].

In first subparagraph below, retain first option for hot-water boilers and second option for steam boilers.

2. Low-Water Cutoff Switch: [Electronic] [Float and electronic] probe shall prevent burner operation on low water. Cutoff switch shall be [manual] [automatic]-reset type.

3. Audible Alarm: Factory mounted on control panel with silence switch; shall sound alarm for above conditions.

Retain paragraph and subparagraphs below if boiler controls interface with building automation system.

D. Building Automation System Interface: Factory-install hardware and software to enable building automation system to monitor, control, and display boiler status and alarms.

Retain subparagraph and associated subparagraphs below if interface with building automation system is through hardwired points and minimal interface is required. If extensive interface is required, delete below and retain second subparagraph below.

1. Hardwired Points:

a. Monitoring: On/off status, [common trouble alarm] [low water level alarm] <Insert monitoring>.

b. Control: On/off operation, [hot water supply temperature set-point adjustment] [steam pressure adjustment] <Insert control>.

Retain subparagraph below if extensive interface with building automation system is required and is beyond that than can be provided by hardwired points. Requirement may exclude some manufacturers listed.

2. A communication interface with building automation system shall enable building automation system operator to remotely control and monitor the boiler from an operator workstation. Control features available, and monitoring points displayed, locally at boiler control panel shall be available through building automation system.

2.7 ELECTRICAL POWER

Retain one of two paragraphs and associated subparagraphs in this article. Retain first if single-point field power connection is not applicable; retain second if single-point field power connection is applicable.

A. Controllers, Electrical Devices, and Wiring: Electrical devices and connections are specified in electrical Sections.

B. Single-Point Field Power Connection: Factory-installed and -wired switches, motor controllers, transformers, and other electrical devices necessary shall provide a single-point field power connection to boiler.

Select one of four options in first subparagraph below. Type 1 is the most common, and Type 12 is second. Type 4X is used primarily in corrosive environments.

1. House in NEMA 250, Type [1] [4] [4X] [12] <Insert type> enclosure.

2. Wiring shall be numbered and color-coded to match wiring diagram.

3. Install wiring outside of an enclosure in a [metal ]raceway.

4. Field power interface shall be to [wire lugs] [fused disconnect switch] [nonfused disconnect switch] [circuit breaker].

5. Provide branch power circuit to each motor and to controls[ with a disconnect switch or circuit breaker].

6. Provide each motor with overcurrent protection.

2.8 CAPACITIES AND CHARACTERISTICS

If Project has more than one type or configuration of boiler, delete this article and schedule boilers on Drawings.

A. Heating Medium: [Hot water] [Steam].

Retain one of first two paragraphs below. Retain first for hot-water boilers and second for steam boilers. In paragraph below, 30- and 125-psig (207- and 860-kPa) ratings are available only in horizontal, fire-tube design.

B. Design Pressure Rating: [30 psig (207 kPa)] [60 psig (420 kPa)] [100 psig (690 kPa)] [125 psig (860 kPa)] [140 psig (966 kPa)] [160 psig (1100 kPa)] <Insert value>.

In first paragraph below, 200- and 300-psig (1380- and 2070-kPa) ratings are available only in horizontal, fire-tube boilers.

C. Design Pressure Rating: [15 psig (104 kPa)] [150 psig (1035 kPa)] [200 psig (1380 kPa)] [250 psig (1725 kPa)] [300 psig (2070 kPa)] [350 psig (2415 kPa)] <Insert value>.

D. Safety Relief Valve Setting: <Insert psig (kPa).>

Retain four paragraphs below for hot-water boilers; delete for steam boilers.

E. Entering-Water Temperature: <Insert deg F (deg C).>

F. Leaving-Water Temperature: <Insert deg F (deg C).>

G. Design Water Flow Rate: <Insert gpm (L/s).>

H. Design Pressure Drop: <Insert psig (kPa).>

Retain two paragraphs below for steam boilers; delete for hot-water boilers.

I. Steam Operating Pressure: <Insert psig (kPa).>

J. Steam Flow Rate: <Insert lb/h (kg/s).>

Retain one of first three paragraphs below. Specify standing or intermittent pilot with minimum AFUE. LEED Prerequisite EA 1 requires compliance with ASHRAE/IESNA 90.1. LEED Credit EA 1 requires efficiency in excess of minimum efficiency required by ASHRAE/IESNA 90.1.

K. Minimum Efficiency AFUE: <Insert number> percent.

L. Minimum Thermal Efficiency: <Insert number> percent.

M. Minimum Combustion Efficiency: <Insert number> percent.

N. Number of Passes: [Two] [Four] <Insert number>.

Retain one of first three paragraphs below.

O. AGA Input: <Insert MBh (kW).>

P. I=B=R Input: <Insert MBh (kW).>

Consider actual Btu content of fuel source if retaining paragraph below. Contact fuel supplier and boiler manufacturers to determine impact. Add text indicating Btu content of fuel if applicable.

Q. Gas Input: <Insert cfh (mL/s).>

Retain one of three paragraphs below for rating methods.

R. AGA Output Capacity: <Insert MBh (kW).>

S. DOE Output Capacity: <Insert MBh (kW).>

T. Equivalent Direct Radiation: <Insert EDR (W).>

Consider impact of site altitude on fan and motor.

U. Burner Blower:

1. Motor Horsepower: <Insert value.>

2. RPM: <Insert value.>

V. Electrical Characteristics:

1. Volts: [115] [208] [230] [460] <Insert value> V.

2. Phase: [Single] [Three].

3. Hertz: [50] [60].

4. Full-Load Amperes: <Insert value.>

5. Minimum Circuit Ampacity: <Insert value.>

6. Maximum Overcurrent Protection: <Insert amperage.>

2.9 SOURCE QUALITY CONTROL

A. Test and inspect factory-assembled boilers, before shipping, according to ASME Boiler and Pressure Vessel Code.

B. Burner and Hydrostatic Test: Factory adjust burner to eliminate excess oxygen, carbon dioxide, oxides of nitrogen emissions, and carbon monoxide in flue gas and to achieve combustion efficiency; perform hydrostatic test.

PART 3 -  EXECUTION

3.1 BOILER INSTALLATION

A. Equipment Mounting:

Retain first subparagraph below to require equipment to be installed on cast-in-place concrete equipment bases.

1. Install boilers on cast-in-place concrete equipment base(s). Comply with requirements for equipment bases and foundations specified in [Section 033000 "Cast-in-Place Concrete."] [Section 033053 "Miscellaneous Cast-in-Place Concrete."]

Retain one of two subparagraphs below. Retain first for projects in seismic areas; retain second for projects not in seismic areas. Indicate vibration isolation and seismic-control device type and minimum deflection in supported equipment schedule on Drawings.

2. Comply with requirements for vibration isolation and seismic control devices specified in Section 230548 "Vibration and Seismic Controls for HVAC."

3. Comply with requirements for vibration isolation devices specified in Section 230548.13 "Vibration Controls for HVAC."

B. Install gas-fired boilers according to NFPA 54.

C. Assemble and install boiler trim.

D. Install electrical devices furnished with boiler but not specified to be factory mounted.

E. Install control wiring to field-mounted electrical devices.

3.2 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Piping installation requirements are specified in other Sections. Drawings indicate general arrangement of piping, fittings, and specialties.

B. Install piping adjacent to boiler to allow service and maintenance.

C. Connect gas piping to boiler gas-train inlet with union. Piping shall be at least full size of gas train connection. Provide a reducer if required.

D. Connect hot-water piping to supply- and return-boiler tappings with shutoff valve and union or flange at each connection.

Retain paragraph above for hot-water boilers and first paragraph below for steam boilers.

E. Connect steam and condensate piping to supply-, return-, and blowdown-boiler tappings with shutoff valve and union or flange at each connection.

Retain one of first two paragraphs below. Retain first for hot-water boilers and second for steam boilers. Delete both if safety valves are specified in Section 232116 Hydronic Piping Specialties" or Section 232216 "Steam and Condensate Piping Specialties."

F. Install piping from safety relief valves to nearest floor drain.

G. Install piping from safety valves to drip-pan elbow and to nearest floor drain.

H. Install piping from equipment drain connection to nearest floor drain. Piping shall be at least full size of connection. Provide an isolation valve if required.

I. Connect breeching full size to boiler outlet. Comply with requirements in Section 235100 "Breechings, Chimneys, and Stacks" for venting materials.

J. Install flue-gas recirculation duct from vent to burner. Comply with requirements in Section 235100 "Breechings, Chimneys, and Stacks" for recirculation duct materials.

K. Ground equipment according to Section 260526 "Grounding and Bonding for Electrical Systems."

L. Connect wiring according to Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

3.3 FIELD QUALITY CONTROL

Retain "Testing Agency," "Manufacturer's Field Service," and "Perform the following tests and inspections" paragraphs below to identify who shall perform tests and inspections. If retaining second option in "Testing Agency" Paragraph or if retaining "Manufacturer's Field Service" or "Perform the following tests and inspections" Paragraph, retain "Field quality-control reports" Paragraph in "Informational Submittals" Article.

A. Testing Agency: [Owner will engage] [Engage] a qualified testing agency to perform tests and inspections.

Retain "Manufacturer's Field Service" Paragraph below to require a factory-authorized service representative to perform tests and inspections.

B. Manufacturer's Field Service: Engage a factory-authorized service representative to test and inspect components, assemblies, and equipment installations, including connections.

Retain "Perform the following tests and inspections" Paragraph below to require Contractor to perform tests and inspections.

C. Perform the following tests and inspections[ with the assistance of a factory-authorized service representative]:

1. Perform installation and startup checks according to manufacturer's written instructions.

2. Leak Test: Hydrostatic test. Repair leaks and retest until no leaks exist.

3. Operational Test: Start units to confirm proper motor rotation and unit operation. Adjust air-fuel ratio and combustion.

4. Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.

a. Check and adjust initial operating set points and high- and low-limit safety set points of fuel supply, water level, and [water temperature] [steam pressure].

b. Set field-adjustable switches and circuit-breaker trip ranges as indicated.

D. Remove and replace malfunctioning units and retest as specified above.

E. Prepare test and inspection reports.

F. Occupancy Adjustments: When requested within [12 months of date of Substantial Completion] <Insert time period>, provide on-site assistance in adjusting system to suit actual occupied conditions. Provide up to [two] <Insert number> visits to Project during other than normal occupancy hours for this purpose.

3.4 DEMONSTRATION

A. [Engage a factory-authorized service representative to train] [Train] Owner's maintenance personnel to adjust, operate, and maintain boilers.[ Video training sessions.] Refer to Section 017900 "Demonstration and Training."

END OF SECTION 235239

	FIRE-TUBE BOILERS
	235239 - 1



