Copyright 2011 AIA
MasterSpec Professional
09/11

Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 235313 - BOILER FEEDWATER PUMPS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. This Section includes feedwater pumps and receivers.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product indicated. Include rated capacity, temperature and NPSH required, pump performance curves with selection points clearly indicated, and furnished specialties and accessories.

B. Shop Drawings: Include plans, elevations, sections, details, dimensions, weights, loadings, required clearances, method of field assembly, and attachments to other work.

1. Wiring Diagrams: Power, signal, and control wiring.

1.3 INFORMATIONAL SUBMITTALS

Retain first paragraph below if required by seismic criteria applicable to Project. Coordinate with Section 230548 "Vibration and Seismic Controls for HVAC."

A. Manufacturer Seismic Qualification Certification: Submit certification that feedwater equipment, accessories, and components will withstand seismic forces defined in Section 230548 "Vibration and Seismic Controls for HVAC."

B. Field quality-control test reports.

1.4 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

1.5 QUALITY ASSURANCE

A. Regulatory Requirements: Fabricate and test unit according to ASME PTC 12.1, "Closed Feedwater Heaters."

B. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

C. ASME Compliance: [ASME B31.1, "Power Piping," for systems more than 15 psig (104 kPa)] [ASME B31.9, "Building Services Piping," for systems equal to or less than 15 psig (104 kPa)]. Safety valves and pressure vessels shall bear the appropriate ASME label.

PART 2 -  PRODUCTS

2.1 FEEDWATER UNITS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. Retain one of first three paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Available Manufacturers: Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

C. If retaining first paragraph below, also retain "Capacities and Characteristics" Paragraph at the end of this Article.

D. Basis-of-Design Product
: Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. AESYS Technologies, LLC; Boiler Div.

2. Alyan Pump.

3. Aurora Pump; Pentair Pump Group.

4. BFS Industries, LLC.

5. Bryan Boilers; Bryan Steam, LLC.

6. Cleaver-Brooks; Div. of Aqua-Chem, Inc.

7. Deaerating Designs; a division of Precision Boilers, Inc.

8. Eastern Industrial Products, Inc.; Smith-Koch, Inc., Div.

9. Domestic Pump; a unit of ITT Fluid Technology.

10. Flotronics, Inc.

11. Gerow Equipment Co.; Pump & Hydraulic Division.

12. Hurst Boiler & Welding Company, Inc.

13. Industrial Steam.

14. Lattner Boiler Manufacturing.

15. Lockwood Products, Inc.; Sub. of John L. Underwood Co., Inc.

16. MEPCO (Marshall Engineered Products Co.).

17. Parker Boiler Co.

18. PVI Industries, LLC.

19. Roth Pump Company; a subsidiary of Roy E. Roth Co.

20. Sellers Engineering Co.

21. Shippensburg Pump Co., Inc.

22. Skidmore.

23. Stickle Steam Specialties Co., Inc.

24. Superior Boiler Works, Inc.

25. U.S. Deaerator Co.

26. US Filter.

27. <Insert manufacturer's name.>

E. Description: Factory-assembled and -tested unit consisting of a receiver, [simplex] [duplex] feedwater pumps, controls, and the following features and accessories:

1. [Liquid-filled industrial] [Bimetal dial-type] thermometer graduated in [Fahrenheit] [Celsius] [both Fahrenheit and Celsius].

2. Level gage glass[, reflex flat type,] with stops at top and bottom.

3. Lifting eyes.

4. Companion flanges.

5. Pump, suction and discharge isolation valve, inlet strainer, discharge check valve, and liquid-filled pressure gage.

Coordinate first subparagraph below with sequence of operation.

6. Makeup Water Assembly: [Float operated with integral valve] [Electric level controller and valve]; with inlet strainer and three-valve bypass.

7. Feedwater Heater: Sparge tube, thermostat, and control valve.

8. Factory-Installed Pipe, NPS 2-1/2 (DN 65) and Smaller: ASTM A 53/A 53M, Type S (seamless), Grade B; or ASTM A 106, Type S, Grade B, Schedule [40] [80]; with threaded joints and fittings.

a. Cast-Iron Threaded Fittings: ASME B16.4; Class [125] [250].

b. Malleable-Iron Threaded Fittings: ASME B16.3, Class [150] [300].

c. Malleable-Iron Unions: ASME B16.39; Class [150] [300].

9. Factory-Installed Pipe, NPS 3 (DN 80) and Larger: ASTM A 53/A 53M, Type E (electric-resistance welded), Grade B; or ASTM A 106, Type S, Grade B, Schedule [40] [80]; with welded joints and carbon-steel fittings and flanges.

a. Wrought-Steel Fittings: ASME B16.9, wall thickness to match adjoining pipe.

b. Wrought Cast- and Forged-Steel Flanges and Flanged Fittings: ASME B16.5, Class [150] [300], including bolts, nuts, and gaskets.

F. Receiver:

If more than one feedwater unit is required, delete subparagraph below and indicate material in a schedule on Drawings.

1. Material: [Close-grain cast iron] [Welded carbon steel] [Welded carbon steel galvanized after fabrication] [Stainless steel].

Retain subparagraph below for carbon-steel tanks only.

2. Additional corrosion protection: [0.07-inch (1.8-mm)] [0.13-inch (3.3-mm)] [0.19-inch (4.8-mm)] <Insert thickness> thickness allowance.

Retain first subparagraph below for cast-iron and carbon-steel receivers only. First option is most common.

3. Finish: [Primer] [Primer under enamel topcoat] [Primer under epoxy topcoat].

4. Factory-Applied Insulation and Jacket: Minimum thickness of [2 inches (50 mm)] <Insert thickness> for mineral-fiber pipe and tank insulation. Cover insulation with [painted steel] [stucco-embossed aluminum] [stainless-steel] jacket.

If more than one feedwater unit is required, delete first subparagraph below and indicate mounting arrangement in a schedule on Drawings.

5. Mounting Arrangement: [Recessed below floor] [Floor mounted].

6. Mounting Frame: Structural-steel stand to support receiver and pumps.[ Fabricate stand with bracing adequate for seismic forces according to authorities having jurisdiction and to allow anchoring mounting frame to floor.]

Retain one of first two paragraphs and associated subparagraphs below and edit for desired pump construction.

G. Vertical Feedwater Pump: Flange-mounted, close-coupled, [single-stage,] [multistage,] radially split-case-design centrifugal pump; rated for [175-psig (1205-kPa)] <Insert pressure> minimum working pressure and a continuous water temperature of at least [225 deg F (107 deg C)] <Insert temperature>; with the following features:

1. Impeller: [Bronze] [Stainless steel].

2. Seals: Mechanical.

Confirm availability of third option in subparagraph below with manufacturer for pump size and configuration selected. Some pump configurations may exclude the third option and necessitate the second.

3. Motor: [Open dripproof] [Totally enclosed] [Totally enclosed fan-cooled] enclosure. Comply with requirements in Section 230513 "Common Motor Requirements for HVAC Equipment."

H. Horizontal Feedwater Pump: Base-mounted, [single-stage,] [multistage,] radially split-case-design centrifugal pump; rated for [175-psig (1205-kPa)] <Insert pressure> minimum working pressure and a continuous water temperature of at least [225 deg F (107 deg C)] <Insert temperature>; with the following features:

1. Impeller: [Bronze] [Stainless steel].

2. Coupling: [Close] [Flexible].

3. Seals: Mechanical.

Confirm availability of third option in subparagraph below with manufacturer for pump size and configuration selected. Some pump configurations may exclude the third option and necessitate the second.

4. Motor: [Open dripproof] [Totally enclosed] [Totally enclosed fan-cooled] enclosure. Comply with requirements in Section 230513 "Common Motor Requirements for HVAC Equipment."

I. Control panel shall be unit mounted and factory wired and include the following:

Type 1 in subparagraph below is most common and a standard product offering. Type 12 is second most common. Type 4X is used primarily in corrosive environments.

1. NEMA 250, Type [1] [4] [4X] [12] <Insert type> enclosure.

Retain first subparagraph and associated subparagraph below for single-point field power connection to unit.

2. Single-point field power interface to [fused disconnect switch] [nonfused disconnect switch] [circuit breaker].

a. Branch power circuit to each motor and to controls[ with a disconnect switch or circuit breaker].

3. NEMA-rated motor controller for each motor, and include a hand-off-auto switch and overcurrent protection.

a. Alternating controls for duplex units with intermittent operation as indicated by control sequence.

4. Terminal blocks with numbered and color-coded wiring to match wiring diagram.

5. Make connections to motor with liquidtight conduit.

6. Removable control mounting plate.

7. Visual indication of status and alarm.

8. Visual indication of elapsed run time, graduated in hours.

9. Fused control-circuit transformer.

J. Feedwater Duplex-Pump Control Sequence:

1. Boiler water-level controller starts and stops lead pump to maintain boiler water-level set point.

2. Lead and lag pumps alternate [after each start] [to equalize run time].

3. Lead pump failure, lag pump [automatically starts if lead pump cannot maintain set point] [is started manually].

4. Visual indication of pump on[ and off] status.

5. Visual indication of pump lead/lag status.

6. Visual[ and audible] alarm indication of pump failure.

K. Receiver Makeup Water Control Sequence:

1. Mechanical float operates integral valve to maintain water-level set point.

2. Visual alarm indication of low receiver-water level.

L. Building Management System Interface: Factory install hardware to enable building management system to monitor and display points.

1. Hardwired Monitoring Points: On/off status for each pump.

If Project has more than one type or configuration of feedwater unit, delete paragraph and subparagraphs below and schedule feedwater units on Drawings. If retaining below, retain "Basis-of-Design Product" Paragraph at the beginning of this Article and insert manufacturer's name and product name or designation there.

M. Capacities and Characteristics:

1. Condensate Receiver:

a. Volume: <Insert gal. (L).>

Retain subparagraph above or first two subparagraphs below.

b. Diameter: <Insert inches (mm).>

c. Length: <Insert inches (mm).>

d. Height to Condensate Inlet: <Insert inches (mm).>

e. Condensate Return Minimum Inlet Size: <Insert NPS (DN).>

f. Makeup Water Minimum Inlet Size: <Insert NPS (DN).>

g. Sparge-Tube Steam Supply: <Insert lb/h (kW).>

2. Feedwater Pumps:

a. No. of Pumps: [Simplex] [Duplex] <Insert number>.

b. Flow Rate: <Insert gpm (L/s).>

c. NPSH Required: <Insert psig (kPa).>

d. Rated Operating Temperature: <Insert deg F (deg C).>

e. Head Pressure: <Insert psig (kPa).>

f. Horsepower: <Insert horsepower.>

g. Speed: <Insert value> RPM.

h. Volts: [115] [208] [230] [460] <Insert value> V.

i. Phase: [Single] [Three].

j. Hertz: 60.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Equipment Mounting:

Retain first subparagraph below to require equipment to be installed on cast-in-place concrete equipment bases.

1. Install feedwater units on cast-in-place concrete equipment base(s). Comply with requirements for equipment bases and foundations specified in [Section 033000 "Cast-in-Place Concrete."] [Section 033053 "Miscellaneous Cast-in-Place Concrete."]

Retain one of two subparagraphs below. Retain first for projects in seismic areas; retain second for projects not in seismic areas. Indicate vibration isolation and seismic-control device type and minimum deflection in supported equipment schedule on Drawings.

2. Comply with requirements for vibration isolation and seismic control devices specified in Section 230548 "Vibration and Seismic Controls for HVAC."

3. Comply with requirements for vibration isolation devices specified in Section 230548.13 "Vibration Controls for HVAC."

B. Install unit to permit access for maintenance.

C. Support piping independent of pumps.

D. Install base-mounted pumps on concrete bases with grouted base frames.

E. Install parts and accessories shipped loose.

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

F. Piping installation requirements are specified in other Division 23 Sections. Drawings indicate general arrangement of piping, fittings, and specialties.

G. Install piping adjacent to machine to allow service and maintenance.

H. Connect makeup water piping and cooling-water piping with reduced-pressure backflow preventers.

I. Install overflow drain piping to nearest floor drain.

J. Install vents and extend to outdoors; terminate with elbow turned down and an insect screen.

K. Adjust boiler water-level controls to properly stage unit.

L. Set field-adjustable, makeup water and cooling-water controls.

3.2 FIELD QUALITY CONTROL

A. Perform tests and inspections and prepare test reports.

Retain subparagraph below to require a factory-authorized service representative to assist Contractor with inspections, tests, and adjustments.

1. Manufacturer's Field Service: Engage a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

B. Tests and Inspections:

1. Inspect field-assembled components, equipment installation, and piping and electrical connections for compliance with manufacturer's written instructions.

2. Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.

3. Check bearing lubrication.

4. Verify proper motor rotation.

5. Start up service.

6. Report results in writing.

C. Remove and replace malfunctioning units and retest as specified above.

END OF SECTION 235313

	BOILER FEEDWATER PUMPS
	235313 - 1



