Copyright 2011 AIA
MasterSpec Professional
03/11

Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 235400 - FURNACES
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

This Section includes requirements for the LEED Rating System. However, equipment specified in this Section may not qualify for LEED Rating System prerequisites and credits. Verify with manufacturers that the requirements for prerequisites and credits can be met. To achieve prerequisites and obtain credits, HVAC system design alternatives that do not include furnaces may be required.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. This Section includes the following:

Adjust list below to suit Project.

1. [Gas-fired, noncondensing] [Gas-fired, condensing] [Electric] furnaces and accessories complete with controls.

2. Air filters.

3. Air cleaners.

4. Humidifiers.

5. Refrigeration components.

1.2 ACTION SUBMITTALS

A. Product Data: Include rated capacities, operating characteristics, furnished specialties, and accessories for each of the following:

1. Furnace.

2. Thermostat.

3. Humidistat.

4. Air filter.

5. Air cleaner.

6. Humidifier.

7. Refrigeration components.

B. LEED Submittals:

Coordinate "Product Data for Credit EA 4" Subparagraph below with requirements for refrigerants.

1. Product Data for Credit EA 4: Documentation indicating that equipment and refrigerants comply.

2. Product Data for Prerequisite IEQ 1: Documentation indicating that units comply with ASHRAE 62.1, Section 5 - "Systems and Equipment."

"Product Data for Credit IEQ 4.1" Subparagraph below applies to LEED-NC, LEED-CI, and LEED-CS; coordinate with requirements for solvent cements and adhesive primers.

3. Product Data for Credit IEQ 4.1: For solvent cements and adhesive primers, documentation including printed statement of VOC content.

"Laboratory Test Reports for Credit IEQ 4" Subparagraph below applies to LEED for Schools.

4. Laboratory Test Reports for Credit IEQ 4: For solvent cements and adhesive primers, documentation indicating that products comply with the testing and product requirements of the California Department of Health Services' "Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers."

1.3 INFORMATIONAL SUBMITTALS

A. Warranty.

1.4 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

1.5 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

Retain "ASHRAE Compliance" Paragraph below for LEED Prerequisite IEQ 1, which requires compliance with ASHRAE 62.1, including requirements for controls, surfaces in contact with the airstream, particulate and gaseous filtration, humidification and dehumidification, drain pan construction and connection, finned-tube coil selection and cleaning, and equipment access. Verify, with manufacturers, availability of units with components and features that comply with these requirements.

B. ASHRAE Compliance: Applicable requirements in ASHRAE 62.1, Section 5 - "Systems and Equipment" and Section 7 - "Construction and Startup."

"ASHRAE/IESNA 90.1 Compliance" Paragraph may be required to comply with Project requirements or authorities having jurisdiction. Also, LEED Prerequisite EA 2 requires compliance with ASHRAE/IESNA 90.1.

C. ASHRAE/IESNA 90.1 Compliance: Applicable requirements in ASHRAE/IESNA 90.1, Section 6 - "Heating, Ventilating, and Air-Conditioning."

D. Comply with NFPA 70.

1.6 WARRANTY

A. Special Warranty: Manufacturer's standard form in which manufacturer agrees to repair or replace the following components of furnaces that fail in materials or workmanship within specified warranty period:

1. Warranty Period, Commencing on Date of Substantial Completion:

Verify available warranties for units and components and insert numbers in subparagraphs below.

a. Furnace Heat Exchanger: [10 years] [20 years] [Lifetime] <Insert value>.

b. Integrated Ignition and Blower Control Circuit Board: [Five years] <Insert value>.

c. Draft-Inducer Motor: [Five years] <Insert value>.

d. High-Efficiency Oil Furnace Burner: [Three years] <Insert value>.

e. Refrigeration Compressors: [10 years] [Lifetime] <Insert value>.

f. Evaporator and Condenser Coils: [Five years] <Insert value>.

g. <Insert components requiring extended warranty>.

PART 2 -  PRODUCTS

2.1 GAS-FIRED FURNACES, NONCONDENSING

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. Retain one of first three paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Available Manufacturers: Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product: Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Adams Manufacturing Company.

2. Amana Heating & Air Conditioning; Goodman Manufacturing Company, L.P.

3. American Standard Companies, Inc.

4. Arcoaire Air Conditioning & Heating; a division of International Comfort Products, LLC.

5. Armstrong Air Conditioning Inc.

6. Bard Manufacturing Company.

7. Bryant Heating & Cooling Systems; Div. of United Technologies Corp.

8. Carrier Corporation; Div. of United Technologies Corp.

9. Clare Brothers.

10. Comfort-Aire; a division of Heat Controller, Inc.

11. Comfortmaker Air Conditioning & Heating; a division of International Comfort Products, LLC.

12. Dornback Furnace.

13. Goodman Manufacturing Company, L.P.

14. Heil Heating & Cooling Products; a division of International Comfort Products, LLC.

15. Lennox Industries Inc.

16. Luxaire Corporation; a division of Unitary Products Group.

17. Rheem Manufacturing Company; Air Conditioning Division.

18. Ruud Air Conditioning Division.

19. Tempstar Heating & Cooling Products; a division of International Comfort Products, LLC.

20. Thermo Products, Inc.; a division of Burnham Holdings Inc.

21. Trane.

22. York International Corp.; a division of Unitary Products Group.

23. <Insert manufacturer's name>.

D. General Requirements for Gas-Fired, Noncondensing Furnaces: Factory assembled, piped, wired, and tested; complying with ANSI Z21.47/CSA 2.3, "Gas-Fired Central Furnaces," and with NFPA 54.

In first paragraph below, galvanized steel is offered by some but not all manufacturers.

E. Cabinet: [Steel] [Galvanized steel].

1. Cabinet interior around heat exchanger shall be factory-installed insulation.

2. Lift-out panels shall expose burners and all other items requiring access for maintenance.

3. Factory paint external cabinets in manufacturer's standard color.

"Airstream Surfaces" Subparagraph below may be required to comply with Project requirements or authorities having jurisdiction. Also, LEED Prerequisite IEQ 1 requires compliance with ASHRAE 62.1.

4. Airstream Surfaces: Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1.

F. Fan: Centrifugal, factory balanced, resilient mounted, [direct drive] [belt drive] [direct or belt drive] [drive type indicated on Drawings].

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Section 230513 "Common Motor Requirements for HVAC Equipment." If different characteristics are required, add subparagraphs below to suit Project.

1. Fan Motors: Comply with requirements in Section 230513 "Common Motor Requirements for HVAC Equipment."

Retain one or more of three subparagraphs below, as applicable.

2. Special Motor Features: Single speed, Premium (TM) efficiency, as defined in Section 230513 "Common Motor Requirements for HVAC Equipment," and with internal thermal protection and permanent lubrication.

3. Special Motor Features: Multitapped, multispeed with internal thermal protection and permanent lubrication.

4. Special Motor Features: Electronically controlled motor (ECM) controlled by integrated furnace/blower control.

G. Type of Gas: [Natural] [Propane].

H. Heat Exchanger: [Aluminized] [Stainless] steel.

I. Burner:

In first subparagraph below, two-stage and modulating gas valves are options.

1. Gas Valve: 100 percent safety [two-stage] [modulating] main gas valve, main shutoff valve, pressure regulator, safety pilot with electronic flame sensor, limit control, transformer, and combination ignition/fan timer control board.

2. Ignition: Electric pilot ignition, with hot-surface igniter or electric spark ignition.

J. Gas-Burner Safety Controls:

1. Electronic Flame Sensor: Prevents gas valve from opening until pilot flame is proven; stops gas flow on ignition failure.

2. Flame Rollout Switch: Installed on burner box; prevents burner operation.

3. Limit Control: Fixed stop at maximum permissible setting; de-energizes burner on excessive bonnet temperature; automatic reset.

K. Combustion-Air Inducer: Centrifugal fan with thermally protected motor and sleeve bearings prepurges heat exchanger and vents combustion products; pressure switch prevents furnace operation if combustion-air inlet or flue outlet is blocked.

L. Furnace Controls: Solid-state board integrates ignition, heat, cooling, and fan speeds; adjustable fan-on and fan-off timing; terminals for connection to accessories.

M. Vent Materials: Comply with requirements in Section 235100 "Breechings, Chimneys, and Stacks" for Type B metal vents.

If Project has more than one furnace, delete paragraph and subparagraphs below and schedule furnace and other components.

N. Capacities and Characteristics:

1. Airflow Configuration: [Upflow] [Counterflow] [Horizontal].

2. Gas:

a. Type: [Natural] [Propane].

b. Venting Type: [Power venter] [Power venter with combustion-air intake].

Retain one of first three subparagraphs below. Specify standing or intermittent pilot with minimum AFUE. LEED Prerequisite EA 2 requires compliance with ASHRAE/IESNA 90.1. LEED Credit EA 1 requires efficiency in excess of minimum efficiency required by ASHRAE/IESNA 90.1.

c. Minimum Efficiency AFUE: <Insert number> percent.

d. Minimum Thermal Efficiency: <Insert number> percent.

e. Minimum Combustion Efficiency: <Insert number> percent.

f. Input: <Insert MBh (kW)>.

g. Heat Output: <Insert MBh (kW)>.

h. Gas Connection Size: <Insert NPS (DN)>.

i. Draft-Inducer Motor:

1) Size: <Insert horsepower>.

2) Speed: <Insert rpm>.

j. Combustion-Air Inlet Size: <Insert inches (mm)>.

k. Combustion-Air Inlet Material: [Galvanized steel] [Stainless steel] [PVC].

l. Heat-Exchanger Condensate Drain Size: <Insert Nps (DN)>.

m. Vent Size: <Insert inches (mm)>.

3. Fan:

a. Airflow: <Insert cfm (L/s)>.

b. External Static Pressure: <Insert inches wg (Pa)>.

c. Motor:

1) Size: <Insert horsepower>.

2) Speed: <Insert rpm>.

d. Volts: <Insert value>.

e. Phase: <Insert value>.

f. Hertz: <Insert value>.

g. Full-Load Amperes: <Insert value>.

h. Minimum Circuit Ampacity: <Insert value>.

i. Maximum Overcurrent Protection: <Insert amperage>.

4. Furnace Electrical Connection:

a. Volts: <Insert value>.

b. Phase: <Insert value>.

c. Hertz: <Insert value>.

d. Full-Load Amperes: <Insert value>.

e. Minimum Circuit Ampacity: <Insert value>.

f. Maximum Overcurrent Protection: <Insert amperage>.

2.2 GAS-FIRED FURNACES, CONDENSING

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. Retain one of first three paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Available Manufacturers: Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product: Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Adams Manufacturing Company.

2. Amana Heating & Air Conditioning; Goodman Manufacturing Company, L.P.

3. American Standard Companies, Inc.

4. Arcoaire Air Conditioning & Heating; a division of International Comfort Products, LLC.

5. Armstrong Air Conditioning Inc.

6. Bryant Heating & Cooling Systems; Div. of United Technologies Corp.

7. Carrier Corporation; Div. of United Technologies Corp.

8. Clare Brothers.

9. Comfort-Aire; a division of Heat Controller, Inc.

10. Comfortmaker Air Conditioning & Heating; a division of International Comfort Products, LLC.

11. Dornback Furnace.

12. Goodman Manufacturing Company, L.P.

13. Heil Heating & Cooling Products; a division of International Comfort Products, LLC.

14. Lennox Industries Inc.

15. Luxaire Corporation; a division of Unitary Products Group.

16. Rheem Manufacturing Company; Air Conditioning Division.

17. Ruud Air Conditioning Division.

18. Tempstar Heating & Cooling Products; a division of International Comfort Products, LLC.

19. Thermo Products, Inc.; a division of Burnham Holdings Inc.

20. Trane.

21. York International Corp.; a division of Unitary Products Group.

22. <Insert manufacturer's name>.

D. General Requirements for Gas-Fired, Condensing Furnaces: Factory assembled, piped, wired, and tested; complying with ANSI Z21.47/CSA 2.3, "Gas-Fired Central Furnaces," and with NFPA 54.

In first paragraph below, galvanized steel is offered by some but not all manufacturers.

E. Cabinet: [Steel] [Galvanized steel].

1. Cabinet interior around heat exchanger shall be factory-installed insulation.

2. Lift-out panels shall expose burners and all other items requiring access for maintenance.

3. Factory paint external cabinets in manufacturer's standard color.

"Airstream Surfaces" Subparagraph below may be required to comply with Project requirements or authorities having jurisdiction. Also, LEED Prerequisite IEQ 1 requires compliance with ASHRAE 62.1.

4. Airstream Surfaces: Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1.

F. Fan: Centrifugal, factory balanced, resilient mounted, direct drive.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Section 230513 "Common Motor Requirements for HVAC Equipment." If different characteristics are required, add subparagraphs below to suit Project.

1. Fan Motors: Comply with requirements in Section 230513 "Common Motor Requirements for HVAC Equipment."

Retain one or more of three subparagraphs below, as applicable.

2. Special Motor Features: Single speed, Premium (TM) efficiency, as defined in Section 230513 "Common Motor Requirements for HVAC Equipment," and with internal thermal protection and permanent lubrication.

3. Special Motor Features: Multitapped, multispeed with internal thermal protection and permanent lubrication.

4. Special Motor Features: Electronically controlled motor (ECM) controlled by integrated furnace/blower control.

G. Type of Gas: [Natural] [Propane].

H. Heat Exchanger:

1. Primary: [Aluminized] [Stainless] steel.

2. Secondary: [Polyethylene-coated] [Stainless] steel.

I. Burner:

1. Gas Valve: 100 percent safety [two-stage] [modulating] main gas valve, main shutoff valve, pressure regulator, safety pilot with electronic flame sensor, limit control, transformer, and combination ignition/fan timer control board.

2. Ignition: Electric pilot ignition, with hot-surface igniter or electric spark ignition.

J. Gas-Burner Safety Controls:

1. Electronic Flame Sensor: Prevents gas valve from opening until pilot flame is proven; stops gas flow on ignition failure.

2. Flame Rollout Switch: Installed on burner box; prevents burner operation.

3. Limit Control: Fixed stop at maximum permissible setting; de-energizes burner on excessive bonnet temperature; automatic reset.

K. Combustion-Air Inducer: Centrifugal fan with thermally protected motor and sleeve bearings prepurges heat exchanger and vents combustion products; pressure switch prevents furnace operation if combustion-air inlet or flue outlet is blocked.

L. Furnace Controls: Solid-state board integrates ignition, heat, cooling, and fan speeds; adjustable fan-on and fan-off timing; terminals for connection to accessories[; diagnostic light with viewport].

M. Accessories:

1. Combination Combustion-Air Intake and Vent: PVC plastic fitting to combine combustion-air inlet and vent through [outside wall] [roof].

2. CPVC Plastic Vent Materials.

Retain one of two subparagraphs and associated subparagraphs below.

a. CPVC Plastic Pipe: Schedule 40, complying with ASTM F 441/F 441M.

b. CPVC Plastic Fittings: Schedule 40, complying with ASTM F 438, socket type.

c. CPVC Solvent Cement: ASTM F 493.

One or both of first two subparagraphs below may be required to comply with Project requirements or authorities having jurisdiction. Retain first two subparagraphs if required for LEED-NC, LEED-CI, or LEED-CS Credit IEQ 4.1.

1) CPVC solvent cement shall have a VOC content of 490 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

2) Adhesive primer shall have a VOC content of 550 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

Retain subparagraph below if required for LEED for Schools Credit IEQ 4.

3) Solvent cement and adhesive primer shall comply with the testing and product requirements of the California Department of Health Services' "Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers."

3. PVC Plastic Vent Materials:

a. PVC Plastic Pipe: Schedule 40, complying with ASTM D 1785.

b. PVC Plastic Fittings: Schedule 40, complying with ASTM D 2466, socket type.

c. PVC Solvent Cement: ASTM D 2564.

One or both of first two subparagraphs below may be required to comply with Project requirements or authorities having jurisdiction. Retain first two subparagraphs if required for LEED-NC, LEED-CI, or LEED-CS Credit IEQ 4.1.

1) PVC solvent cement shall have a VOC content of 510 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

2) Adhesive primer shall have a VOC content of 550 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

Retain subparagraph below if required for LEED for Schools Credit IEQ 4.

3) Solvent cement and adhesive primer shall comply with the testing and product requirements of the California Department of Health Services' "Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers."

If Project has more than one furnace, delete paragraph and subparagraphs below and schedule furnace and other components.

N. Capacities and Characteristics:

1. Airflow Configuration: [Upflow] [Counterflow] [Horizontal].

2. Gas:

a. Type: [Natural] [Propane].

b. Venting Type: [Power venter] [Power venter with combustion-air intake].

Retain one of first three subparagraphs below. Specify standing or intermittent pilot with minimum AFUE. LEED Prerequisite EA 1 requires compliance with ASHRAE/IESNA 90.1. LEED Credit EA 1 requires efficiency in excess of minimum efficiency required by ASHRAE/IESNA 90.1.

c. Minimum Efficiency AFUE: <Insert number> percent.

d. Minimum Thermal Efficiency: <Insert number> percent.

e. Minimum Combustion Efficiency: <Insert number> percent.

f. Input: <Insert MBh (kW)>.

g. Heat Output: <Insert MBh (kW)>.

h. Gas Connection Size: <Insert NPS (DN)>.

i. Draft-Inducer Motor:

1) Size: <Insert horsepower>.

2) Speed: <Insert rpm>.

j. Combustion-Air Inlet Size: <Insert inches (mm)>.

k. Combustion-Air Inlet Material: [CPVC] [PVC].

l. Heat-Exchanger Condensate Drain Size: <Insert Nps (DN)>.

m. Vent Size: <Insert inches (mm)>.

n. Vent Material: [CPVC] [PVC].

3. Fan:

a. Airflow: <Insert cfm (L/s)>.

b. External Static Pressure: <Insert inches wg (Pa)>.

c. Motor:

1) Size: <Insert horsepower>.

2) Speed: <Insert rpm>.

d. Volts: <Insert value>.

e. Phase: <Insert value>.

f. Hertz: <Insert value>.

g. Full-Load Amperes: <Insert value>.

h. Minimum Circuit Ampacity: <Insert value>.

i. Maximum Overcurrent Protection: <Insert amperage>.

4. Furnace Electrical Connection:

a. Volts: <Insert value>.

b. Phase: <Insert value>.

c. Hertz: <Insert value>.

d. Full-Load Amperes: <Insert value>.

e. Minimum Circuit Ampacity: <Insert value>.

f. Maximum Overcurrent Protection: <Insert amperage>.

2.3 ELECTRIC FURNACES

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. Retain one of first three paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Available Manufacturers: Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product: Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Amana Heating & Air Conditioning; Goodman Manufacturing Company, L.P.

2. Armstrong Air Conditioning Inc.

3. Bryant Heating & Cooling Systems; Div. of United Technologies Corp.

4. Carrier Corporation; Div. of United Technologies Corp.

5. Comfort-Aire; a division of Heat Controller, Inc.

6. Comfortmaker Air Conditioning & Heating; a division of International Comfort Products, LLC.

7. Eubank Manufacturing Enterprise, Inc.

8. Lennox Industries Inc.

9. Luxaire Corporation; a division of Unitary Products Group.

10. Rheem Manufacturing Company; Air Conditioning Division.

11. Ruud Air Conditioning Division.

12. York International Corp.; a division of Unitary Products Group.

13. <Insert manufacturer's name>.

D. General Requirements for Electric Furnaces: Factory assembled, piped, wired, and tested.

E. Cabinet: Steel, with duct liner[ downstream from cooling coil].

1. Duct Liner: Fiberglass, minimum [1/2 inch (13 mm)] [3/4 inch (19 mm)] thick, complying with ASTM C 1071 and having a coated surface exposed to airstream complying with NFPA 90A or NFPA 90B and with NAIMA's "Fibrous Glass Duct Liner Standard."

"Airstream Surfaces" Subparagraph below may be required to comply with Project requirements or authorities having jurisdiction. Also, LEED Prerequisite IEQ 1 requires compliance with ASHRAE 62.1.

a. Airstream Surfaces: Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1.

2. Factory paint external cabinets in manufacturer's standard color.

F. Fan: Centrifugal, factory balanced, resilient mounted, direct drive.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Section 230513 "Common Motor Requirements for HVAC Equipment." If different characteristics are required, add subparagraphs below to suit Project.

1. Fan Motors: Comply with requirements in Section 230513 "Common Motor Requirements for HVAC Equipment."

Retain one or more of three subparagraphs below, as applicable.

2. Special Motor Features: Single speed, Premium (TM) efficiency, as defined in Section 230513 "Common Motor Requirements for HVAC Equipment," and with internal thermal protection and permanent lubrication.

3. Special Motor Features: Multitapped, multispeed with internal thermal protection and permanent lubrication.

4. Special Motor Features: Electronically controlled motor (ECM) controlled by integrated furnace/blower control.

G. Electric-Resistant Heating Elements: Helix-wound, nickel-chromium wire-heating elements in ceramic insulators mounted on steel supports.

H. Heating-Element Control: Sequencer relay with relay for each element; switches elements on and off, with delay between each increment; initiates, stops, or changes fan speed.

I. Summer Fan Switch: Connected to permit independent on-off switch of unit fan.

If Project has more than one furnace, delete paragraph and subparagraphs below and schedule furnace and other components.

J. Capacities and Characteristics:

1. Airflow Configuration: [Upflow] [Counterflow] [Horizontal].

2. Electric Heating Element:

a. Capacity: <Insert MBh (kW)>.

b. Number of Steps: <Insert number>.

c. Volts: <Insert value>.

d. Phase: <Insert value>.

e. Hertz: <Insert value>.

f. Full-Load Amperes: <Insert value>.

g. Minimum Circuit Ampacity: <Insert value>.

h. Maximum Overcurrent Protection: <Insert amperage>.

3. Fan:

a. Airflow: <Insert cfm (L/s)>.

b. External Static Pressure: <Insert inches wg (Pa)>.

c. Motor:

1) Size: <Insert horsepower>.

2) Speed: <Insert rpm>.

d. Volts: <Insert value>.

e. Phase: <Insert value>.

f. Hertz: <Insert value>.

g. Full-Load Amperes: <Insert value>.

h. Minimum Circuit Ampacity: <Insert value>.

i. Maximum Overcurrent Protection: <Insert amperage>.

4. Furnace Electrical Connection:

a. Volts: <Insert value>.

b. Phase: <Insert value>.

c. Hertz: <Insert value>.

d. Full-Load Amperes: <Insert value>.

e. Minimum Circuit Ampacity: <Insert value>.

f. Maximum Overcurrent Protection: <Insert amperage>.

2.4 THERMOSTATS[ AND HUMIDISTATS]

LEED Prerequisite EA 2 requires compliance with ASHRAE/IESNA 90.1, in which Section 6.4.3, defines requirements for controls.

A. Controls shall comply with requirements in ASHRAE/IESNA 90.1, "Controls."

Retain one of five paragraphs below.

B. Solid-State Thermostat: [Wall-mounting] [Freestanding] [Wireless], programmable, microprocessor-based unit with [automatic] [manual] switching from heating to cooling, preferential rate control, seven-day programmability with minimum of four temperature presets per day, [vacation mode, ]and battery backup protection against power failure for program settings.

C. Single-Stage, Heating-Cooling Thermostat: Adjustable, heating-cooling, wall-mounting unit with fan on-automatic selector.

D. Two-Stage, Heating-Cooling Thermostat: Adjustable, heating-cooling, wall-mounting unit with fan on-automatic selector.

E. [Single] [Two]-Stage, Heating-Only Thermostat: Wall-mounting unit with fan on-automatic selector.

F. Solid-State, Combination Thermostat and Humidistat: [Wall-mounting] [Freestanding] [Wireless], programmable, microprocessor-based unit with automatic switching from heating to cooling and humidifying to dehumidifying, preferential rate control, seven-day programmability with minimum of four temperature presets per day, [vacation mode, ]and battery backup protection against power failure for program settings.

Retain first paragraph below if humidifier is specified.

G. Humidistat: Adjustable, [wall] [duct]-mounting unit.

H. Control Wiring: Unshielded twisted-pair cabling.

1. No. 24 AWG, 100 ohm, four pair.

2. Cable Jacket Color: [Blue] <Insert color>.

2.5 AIR FILTERS

Retain this Article for furnaces using air filters. Retain one or more of four paragraphs below. If Project has more than one filter type, indicate filter type for each unit on Drawings.

LEED Prerequisite IEQ 1 requires compliance with ASHRAE 62.1, in which a MERV rating of 6 or higher is required. First paragraph below does not comply; second paragraph complies.

A. Washable Filters: 1-inch- (25-mm-) thick, urethane pad.

B. Disposable Filters: [1-inch- (25-mm-)] <Insert dimension> thick fiberglass media[ with ASHRAE 52.2 MERV rating of 6 or higher] in sheet metal frame.

C. Charged Media Air Filters: Sheet metal housing arranged to be ducted in return-air duct connection to furnace, generates electrostatic charge; MERV 10 rating.

D. HEPA Air Filter Units: Sheet metal housing with fan arranged to be ducted to return-air duct connection to furnace, with activated carbon prefilter, high-efficiency particulate air (HEPA) disposable filter[, and carbon VOC]. HEPA shall be as follows:

1. Standard: UL 586, "High-Efficiency, Particulate, Air Filter Units."

2. Rating: ASHRAE 52.1, dust-spot efficiency of 65 percent; ASHRAE 52.2, 99.97 percent efficiency to 0.03-micrometer particle size.

2.6 AIR CLEANERS

Retain this Article for air filtration using air cleaners. If Project uses both air filters and air cleaners, indicate type for each unit on Drawings.

A. Electronic Air Cleaners: Packaged system, including sheet metal housing, prefilter, power supply, and automatic control device, arranged for mounting in return-air duct at furnace; equip with on-off and test switches and pilot light.

1. Standard: UL 586, "High-Efficiency, Particulate, Air Filter Units."

2. Rating: ASHRAE 52.2, particle size to 0.01 micrometer.

3. Static Pressure Drop: Maximum 0.14-inch wg (35 Pa) at 300-fpm (1.52-m/s) air velocity.

If Project has more than one air cleaner, delete paragraph and subparagraphs below and schedule air cleaner and other components.

B. Capacities and Characteristics:

1. Volts: <Insert value>.

2. Phase: <Insert value>.

3. Hertz: <Insert value>.

4. Minimum Circuit Ampacity: <Insert value>.

5. Maximum Overcurrent Protection: <Insert amperage>.

2.7 HUMIDIFIERS

A. Minimum capacity rating indicated according to ARI 610, "Central System Humidifiers for Residential Applications."

Retain one of four paragraphs below. Indicate location, mounting arrangement, and piping connections on Drawings.

B. Media-wheel bypass type with bypass damper and motor-driven media wheel in reservoir with float-valve level control; arranged for mounting on return duct or plenum with bypass connection to supply duct.

C. Wetted-pad, continuous-drain, bypass type with bypass damper and water-flow control orifice; arranged for mounting on return duct or plenum with bypass connection to supply duct.

D. Fan-powered, wetted-pad, continuous-drain type with water-flow control orifice and motor; arranged for mounting on duct or plenum.

E. Pumped, fan-powered, wetted-pad type with reservoir-level control and pump and fan motors; arranged for mounting on duct or plenum.

First paragraph below may be required to comply with Project requirements or authorities having jurisdiction. Also, LEED Prerequisite IEQ 1 requires compliance with ASHRAE 62.1, which defines requirements for drain pans, humidifier water quality, obstructions, and accessibility.

F. Comply with applicable requirements in ASHRAE 62.1.

If Project has more than one humidifier, delete paragraph and subparagraphs below and schedule humidifier and other components.

G. Capacities and Characteristics:

1. Type: [Media wheel] [Wetted pad with reservoir] [Wetted pad with continuous drain] [Wetted-pad bypass].

Retain two subparagraphs below for media wheel and wetted-pad humidifiers.

2. Water Connection Size: <Insert Nps (Dn)>.

3. Drain Connection Size: <Insert Nps (Dn)>.

Retain subparagraphs below for media-wheel, fan-powered, and pumped, fan-powered humidifiers.

4. Volts: <Insert value>.

5. Phase: <Insert value>.

6. Hertz: <Insert value>.

7. Minimum Circuit Ampacity: <Insert value>.

8. Maximum Overcurrent Protection: <Insert amperage>.

2.8 REFRIGERATION COMPONENTS

A. General Refrigeration Component Requirements:

First subparagraph below may be required to comply with Project requirements or authorities having jurisdiction. Also, LEED Prerequisite EA 3 requires using CFC-free refrigerants in new HVAC&R systems.

1. Refrigeration compressor, coils, and specialties shall be designed to operate with CFC-free refrigerants.

First paragraph below may be required to comply with Project requirements or authorities having jurisdiction. Also, LEED Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1.

2. Energy Efficiency: Equal to or greater than prescribed by ASHRAE/IESNA 90.1, "Energy Standard for Buildings except Low-Rise Residential Buildings."

First paragraph below may be required to comply with Project requirements or authorities having jurisdiction. Also, LEED Prerequisite IEQ 1 requires compliance with ASHRAE 62.1, which defines requirements for drain pans, humidifier water quality, obstructions, and accessibility.

B. Refrigerant Coil: Copper tubes mechanically expanded into aluminum fins. Comply with ARI 210/240, "Unitary Air-Conditioning and Air-Source Heat Pump Equipment." Match size with furnace. Include condensate drain pan with accessible drain outlet[ complying with ASHRAE 62.1].

1. Refrigerant Coil Enclosure: Steel, matching furnace and evaporator coil, with access panel and flanges for integral mounting at or on furnace cabinet and galvanized sheet metal drain pan coated with black asphaltic base paint.

Retain one of first two paragraphs and associated subparagraph below for refrigerant piping. Retain first paragraph for precharged refrigerant line kits if Project conditions allow standard lengths of tubing without joints; retain second for refrigerant tubing if distance does not allow refrigerant tubing kits.

C. Refrigerant Line Kits: Annealed-copper suction and liquid lines factory cleaned, dried, pressurized with nitrogen, sealed, and with suction line insulated. Provide in standard lengths for installation without joints, except at equipment connections.

LEED Prerequisite EA 2 requires that pipe insulation thickness comply with ASHRAE/IESNA 90.1, "Minimum Pipe Insulation Thickness." Requirements for minimum insulation thickness vary by pipe size and temperature.

1. Flexible Elastomeric: Closed-cell, sponge- or expanded-rubber materials. Comply with ASTM C 534, Type I, [1/2 inch (13 mm)] [1 inch (25 mm)] <Insert dimension> thick.

D. Refrigerant Piping: Comply with requirements in Section 232300 "Refrigerant Piping."

E. Air-Cooled, Compressor-Condenser Unit:

1. Casing: Steel, finished with baked enamel, with removable panels for access to controls, weep holes for water drainage, and mounting holes in base. Provide brass service valves, fittings, and gage ports on exterior of casing.

2. Compressor: Hermetically sealed [reciprocating] [scroll] [reciprocating or scroll] type.

a. Crankcase heater.

b. [Restrained vibration] [Vibration] isolation mounts for compressor.

c. Compressor motor shall have thermal- and current-sensitive overload devices, start capacitor, relay, and contactor.

d. Two-speed compressor motors shall have manual-reset high-pressure switch and automatic-reset low-pressure switch.

Retain one of first two subparagraphs below to require a specific refrigerant type; delete both if any refrigerant type is acceptable. LEED-NC, LEED-CS, and LEED for Schools Credit EA 4; LEED-CI Prerequisite EA 3; and LEED-EB Credit EA 5 requires HVAC&R equipment to meet requirements for enhanced refrigerant management. Retain second or third option in first subparagraph or retain second subparagraph for Credit EA 4.

e. Refrigerant Charge: [R-22] [R-407C] [R-410A] <Insert type>.

f. Refrigerant: R-407C or R-410A.

3. Refrigerant Coil: Copper tube, with mechanically bonded aluminum fins, complying with ARI 210/240, and with liquid subcooler.

4. Heat-Pump Components: Reversing valve and low-temperature air cut-off thermostat.

5. Fan: Aluminum-propeller type, directly connected to motor.

6. Motor: Permanently lubricated, with integral thermal-overload protection.

7. Low Ambient Kit: Permits operation down to 45 deg F (7 deg C).

8. Mounting Base: Polyethylene.

If Project has more than one refrigeration component, delete paragraph and subparagraphs below and schedule refrigeration component and other components.

F. Capacities and Characteristics:

1. Refrigerant Coil:

a. Total Cooling Capacity: <Insert Btu/h (kW)>.

b. Sensible Cooling Capacity: <Insert Btu/h (kW)>.

c. Heating Capacity: <Insert Btu/h (kW)>.

d. Maximum Air Pressure Drop: <Insert inches wg (Pa)>.

e. Condensate Drain Size: <Insert Nps (DN)>.

2. Compressor-Condenser Unit:

LEED Prerequisite EA 2 requires compliance with ASHRAE/IESNA 90.1. LEED Credit EA 1 requires efficiency in excess of minimum efficiency required by ASHRAE/IESNA 90.1.

a. Cooling Energy Efficiency[ (EER)] [ (SEER)]: <Insert value>.

Retain first subparagraph below for heat pump applications.

b. Heating Coefficient of Performance: <Insert value>.

c. Volts: <Insert value>.

d. Phase: <Insert value>.

e. Hertz: <Insert value>.

f. Full-Load Amperes: <Insert value>.

g. Minimum Circuit Ampacity: <Insert value>.

h. Maximum Overcurrent Protection: <Insert amperage>.

i. Fan Motor Full-Load Amperes: <Insert value>.

j. Compressor Running Load Amperes: <Insert value>.

k. Compressor Motor Full-Load Amperes: <Insert value>.

PART 3 -  EXECUTION

3.1 INSTALLATION

Retain first paragraph below for gas-fired furnaces.

A. Install gas-fired furnaces and associated fuel and vent features and systems according to NFPA 54.

B. Suspended Units: Suspend from structure using threaded rods, spring hangers, and building attachments. Secure rods to unit hanger attachments. Adjust hangers so unit is level and plumb.

Delete subparagraph below if Project site is aseismic.

1. Install seismic restraints to limit movement of furnace by resisting code-required seismic acceleration.

C. Base-Mounted Units: Secure units to substrate. Provide optional bottom closure base if required by installation conditions.

Delete subparagraph below if Project site is aseismic.

1. Anchor furnace to substrate to resist code-required seismic acceleration.

D. Controls: Install thermostats and humidistats at mounting height of 60 inches (1500 mm) above floor.

E. Wiring Method: Install control wiring in accessible ceiling spaces and in gypsum board partitions where unenclosed wiring method may be used. Conceal control wiring except in unfinished spaces.

Retain one of first two paragraphs below.

F. Install ground-mounted, compressor-condenser components on 4-inch- (100-mm-) thick, reinforced concrete base; 4 inches (100 mm) larger on each side than unit. Concrete, reinforcement, and formwork are specified in [Section 033000 "Cast-in-Place Concrete."] [Section 033053 "Miscellaneous Cast-in-Place Concrete."] Coordinate anchor installation with concrete base.

G. Install ground-mounted, compressor-condenser components on polyethylene mounting base.

H. Install roof-mounted, compressor-condenser components on equipment supports specified in Section 077200 "Roof Accessories." Anchor units to supports with removable, cadmium-plated fasteners.

3.2 CONNECTIONS

A. Gas piping installation requirements are specified in [Section 231123 "Facility Natural-Gas Piping."] [Section 231126 "Facility Liquefied-Petroleum Gas Piping."] Drawings indicate general arrangement of piping, fittings, and specialties. Connect gas piping with union or flange and appliance connector valve.

B. Install piping adjacent to equipment to allow service and maintenance.

Retain paragraph below for furnaces with humidifiers.

C. Water piping installation requirements are specified in Section 221116 "Domestic Water Piping." Drawings indicate general arrangement of piping, fittings, and specialties. Connect water piping with union and ball valve.

Retain one of first two paragraphs and associated subparagraphs below to indicate type of venting required, or revise to suit Project.

D. Vent Connection, Noncondensing, Gas-Fired Furnaces: Connect Type B vents to furnace vent connection and extend outdoors. Type B vents and their installation requirements are specified in Section 235100 "Breechings, Chimneys, and Stacks."

E. Vent and Outside-Air Connection, Condensing, Gas-Fired Furnaces: Connect plastic piping vent material to furnace connections and extend outdoors. Terminate vent outdoors with a cap and in an arrangement that will protect against entry of birds, insects, and dirt.

1. Ream ends of pipes and tubes and remove burrs. Bevel plain ends of steel pipe.

2. Remove scale, slag, dirt, and debris from inside and outside of pipe and fittings before assembly.

3. Plastic Piping Solvent-Cement Joints: Clean and dry joining surfaces. Join pipe and fittings according to the following:

a. Comply with ASTM F 402 for safe-handling practice of cleaners, primers, and solvent cements.

b. CPVC Piping: Join according to ASTM D 2846/D 2846M Appendix.

c. PVC Pressure Piping: Join schedule number ASTM D 1785, PVC pipe and PVC socket fittings according to ASTM D 2672. Join other-than-schedule-number PVC pipe and socket fittings according to ASTM D 2855.

d. Requirements for Low-Emitting Materials:

One or more of first four subparagraphs below may be required to comply with Project requirements or authorities having jurisdiction. Retain first three subparagraphs below if required for LEED-NC, LEED-CI, or LEED-CS Credit IEQ 4.1.

1) CPVC solvent cement shall have a VOC content of 490 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

2) PVC solvent cement shall have a VOC content of 510 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

3) Adhesive primer shall have a VOC content of 550 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

Retain first subparagraph below if required for LEED for Schools Credit IEQ 4.

4) Solvent cement and adhesive primer shall comply with the testing and product requirements of the California Department of Health Services' "Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers."

4. Slope pipe vent back to furnace or to outside terminal.

F. Connect ducts to furnace with flexible connector. Comply with requirements in Section 233300 "Air Duct Accessories."

Retain one of first two paragraphs and associated subparagraphs below for refrigerant piping. Retain first paragraph for precharged refrigerant line kits if Project conditions allow standard lengths of tubing without joints; retain second for refrigerant tubing if distance does not allow refrigerant tubing kits.

G. Connect refrigerant tubing kits to refrigerant coil in furnace and to air-cooled, compressor-condenser unit.

Retain one of three subparagraphs below. See the Evaluations in Section 232300 "Refrigerant Piping" for a discussion on soldering and brazing refrigerant piping.

1. Flared Joints: Use ASME B16.26 fitting and flared ends, following procedures in CDA's "Copper Tube Handbook."

2. Soldered Joints: Apply ASTM B 813, water-flushable flux, unless otherwise indicated, to tube end. Construct joints according to ASTM B 828 or CDA's "Copper Tube Handbook," using lead-free solder alloy complying with ASTM B 32.

3. Brazed Joints: Construct joints according to AWS's "Brazing Handbook," "Pipe and Tube" Chapter, using copper-phosphorus brazing filler metal complying with AWS A5.8.

H. Comply with requirements in Section 232300 "Refrigerant Piping" for installation and joint construction of refrigerant piping.

I. Complete installation and startup checks and start units according to manufacturer's written instructions.

J. Verify proper operation of capacity control device.

K. Adjust airflow and initial temperature and humidity set points.

L. Set controls, burner, and other adjustments for optimum heating performance and efficiency. Adjust heat-distribution features, including shutters, dampers, and relays, to provide optimum heating performance and system efficiency.

M. After completing installation, clean furnaces internally according to manufacturer's written instructions.

N. Install new filters in each furnace within 14 days after Substantial Completion.

3.3 FIELD QUALITY CONTROL

A. Perform the following field tests and inspections and prepare test reports:

1. Perform electrical test and visual and mechanical inspection.

2. Leak Test: After installation, charge systems with refrigerant and oil and test for leaks. Repair leaks, replace lost refrigerant and oil, and retest until no leaks exist.

3. Operational Test: After electrical circuitry has been energized, start units to confirm proper operation, product capability, and compliance with requirements.

4. Verify that fan wheel is rotating in the correct direction and is not vibrating or binding.

5. Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.

B. Verify that vibration isolation and flexible connections properly dampen vibration transmission to structure.

END OF SECTION 235400

	FURNACES
	235400 - 1



