Copyright 2011 AIA
MasterSpec Professional
09/11

Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 235513 - FUEL-FIRED DUCT HEATERS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

This Section includes requirements for the LEED Rating System. However, equipment specified in this Section may not qualify for LEED Rating System prerequisites and credits. Verify with manufacturers that the requirements for prerequisites and credits can be met. To achieve prerequisites and obtain credits, HVAC system design alternatives that do not include duct heaters may be required.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. This Section includes gas-fired duct heaters.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of duct heater indicated. Include rated capacities, operating characteristics, and accessories.

B. Shop Drawings: Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

1. Wiring Diagrams: Signal and control wiring.

1.3 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

1.4 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

Retain "ASHRAE/IESNA 90.1 Compliance" Paragraph below to require compliance with ASHRAE 90.1. LEED Prerequisite EA 2 requires compliance with ASHRAE/IESNA 90.1.

B. ASHRAE/IESNA 90.1 Compliance: Applicable requirements in ASHRAE/IESNA 90.1, Section 6 - "Heating, Ventilating, and Air-Conditioning."

1.5 WARRANTY

A. Special Warranty: Manufacturer's standard form in which manufacturer agrees to repair or replace heat exchanger of gas-fired duct heater that fails in materials or workmanship within specified warranty period.

Verify available warranties for units and components and insert number in subparagraph below.

1. Warranty Period: [Two] [Five] <Insert number> years from date of Substantial Completion.

PART 2 -  PRODUCTS

2.1 MANUFACTURED UNITS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. Retain one of first three paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Available Manufacturers: Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product: Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Lennox Industries, Inc.

2. Modine Manufacturing Company.

3. Reznor/Thomas & Betts Corporation.

4. Sterling HVAC Products; Div. of Mestek Technology Inc.

5. <Insert manufacturer's name.>

D. Description: Factory assembled, piped, and wired; and complying with ANSI Z83.8/CSA 2.6.

E. Fuel Type: Design burner for [natural] [propane] gas having characteristics same as those of gas available at Project site.

F. Type of Venting: [Gravity] [Power] [Indoor, separated combustion, power] vented.

Retain subparagraph below with third option in paragraph above.

1. Concentric, Terminal Vent Assembly: Combined combustion-air inlet and power-vent outlet with wall or roof caps. Include adapter assembly for connection to inlet and outlet pipes, and flashing for wall or roof penetration.

G. Housing: Steel cabinet with integral support inserts and removable bottom arranged to serve as drain pan.

H. Internal Casing: Aluminized steel, arranged to contain airflow, with duct flanges at inlet and outlet.

I. Heat Exchanger: [Aluminized] [Stainless] steel.

J. Burner Material: [Aluminized steel with stainless-steel inserts] [Stainless steel].

Retain first paragraph below for power-vented model.

K. Power Venter: Integral, motorized centrifugal fan interlocked with gas valve.

L. Controls: Regulated redundant gas valve containing pilot solenoid valve, electric gas valve, pilot filter, pressure regulator, pilot shutoff, and manual shutoff all in one body.

1. Gas Control Valve: [Single stage] [Two stage] [Modulating].

2. Ignition: [Standing pilot] [Electronically controlled electric spark with flame sensor].

3. Fan Thermal Switch: Operates fan on heat-exchanger temperature.

First option in first subparagraph below is for gravity-vented units; second option is for units with a power venter.

4. Vent Flow Verification: [Flame rollout switch] [Differential pressure switch to verify open vent].

5. Control transformer.

6. High Limit: Thermal switch or fuse to stop burner.

7. Thermostat: Devices and wiring are specified in Section 230900 "Instrumentation and Control for HVAC."

Retain subparagraph above or one of four subparagraphs below, or revise to suit selected equipment.

8. Thermostat: Single-stage, wall-mounting type with 50 to 90 deg F (10 to 32 deg C) operating range and fan on switch.

9. Thermostat: 2-stage, wall-mounting type with 50 to 90 deg F (10 to 32 deg C) operating range and fan on switch.

10. Thermostat: Single-stage type with duct-mounting sensor and 50 to 90 deg F (10 to 32 deg C) operating range.

11. Thermostat: 2-stage type with duct-mounting sensor and 50 to 90 deg F (10 to 32 deg C) operating range.

If Project has more than one type or configuration of gas-fired duct heater, delete paragraph and subparagraphs below and schedule duct heaters on Drawings.

M. Capacities and Characteristics:

1. Flue Outlet: <Insert inches (mm)> diameter.

2. Gas Input: <Insert Btu/h (kW).>

3. Gas Output: <Insert Btu/h (kW).>

LEED Prerequisite EA 2 requires compliance with ASHRAE/IESNA 90.1. LEED Credit EA 1 requires efficiency in excess of minimum efficiency required by ASHRAE/IESNA 90.1.

4. Minimum Combustion Efficiency: [80] <Insert number> percent.

5. Minimum Airflow: <Insert cfm (L/s).>

6. External Static Pressure: <Insert inches wg (kPa).>

PART 3 -  EXECUTION

3.1 INSTALLATION

Retain first option in first paragraph below for projects in the U.S.; retain second option for projects in Canada.

A. Install and connect gas-fired duct heaters and associated fuel and vent features and systems according to [NFPA 54] [CAN/CSA B149.1], applicable local codes and regulations, and manufacturer's written installation instructions.

B. Suspended Units: Suspend from substrate using threaded rods, spring hangers, and building attachments. Secure rods to unit hanger attachments. Adjust hangers so unit is level and plumb.

C. Install piping adjacent to gas-fired duct heaters to allow service and maintenance.

D. Gas Piping: Comply with [Section 231123 "Facility Natural-Gas Piping."] [Section 231126 "Facility Liquefied-Petroleum Gas Piping] Connect gas piping to gas train inlet; provide union with enough clearance for burner removal and service.

E. Vent Connections: Comply with Section 235100 "Breechings, Chimneys, and Stacks."

F. Duct Connections: Comply with [Section 233113 "Metal Ducts."] [Section 233116 "Nonmetal Ducts."]

G. Electrical Connections: Comply with applicable requirements in electrical Sections.

1. Install electrical devices furnished with heaters but not specified to be factory mounted.

H. Adjust initial temperature set points.

I. Adjust burner and other unit components for optimum heating performance and efficiency.

3.2 FIELD QUALITY CONTROL

A. Tests and Inspections: Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.

END OF SECTION 235513

	FUEL-FIRED DUCT HEATERS
	235513 - 1



