Copyright 2011 AIA
MasterSpec Professional
09/11

Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 235533 - FUEL-FIRED UNIT HEATERS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

This Section includes requirements for the LEED Rating System. However, equipment specified in this Section may not qualify for LEED Rating System prerequisites and credits. Verify with manufacturers that the requirements for prerequisites and credits can be met. To achieve prerequisites and obtain credits, HVAC system design alternatives that do not include fuel-fired unit heaters may be required.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. This Section includes [gas] [oil]-fired unit heaters.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of fuel-fired unit heater indicated. Include rated capacities, operating characteristics, and accessories.

B. Shop Drawings: Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

1. Wiring Diagrams: Power[, signal, and control] wiring.

1.3 INFORMATIONAL SUBMITTALS

A. Field quality-control test reports.

1.4 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

1.5 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

Retain "ASHRAE/IESNA 90.1 Compliance" Paragraph below to require compliance with ASHRAE 90.1. LEED Prerequisite EA 2 requires compliance with ASHRAE/IESNA 90.1.

B. ASHRAE/IESNA 90.1 Compliance: Applicable requirements in ASHRAE/IESNA 90.1, Section 6 - "Heating, Ventilating, and Air-Conditioning."

1.6 WARRANTY

A. Special Warranty: Manufacturer's standard form in which manufacturer agrees to repair or replace heat exchanger of fuel-fired unit heater that fails in materials or workmanship within specified warranty period.

Verify available warranties for units and components and insert number in subparagraph below. Two-year warranty is applicable to aluminized heat exchangers; five-year warranty, to stainless-steel heat exchangers.

1. Warranty Period: [Two] [Five] <Insert number> years from date of Substantial Completion.

PART 2 -  PRODUCTS

2.1 GAS-FIRED UNIT HEATERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. Retain one of first three paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Available Manufacturers: Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product: Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Lennox Industries, Inc.

2. Modine Manufacturing Company.

3. Reznor/Thomas & Betts Corporation.

4. Sterling HVAC Products; Div. of Mestek Technology Inc.

5. <Insert manufacturer's name.>

D. Description: Factory assembled, piped, and wired, and complying with ANSI Z83.8/CSA 2.6.

E. Fuel Type: Design burner for [natural] [propane] gas having characteristics same as those of gas available at Project site.

Retain first paragraph below unless more than one type of venting is required; in which case, delete below and indicate type of venting in a schedule on Drawings. See the sample schedule in the Evaluations.

F. Type of Venting: [Gravity] [Powered] [Indoor, separated combustion, power] vented.

G. Housing: Steel, with integral draft hood and inserts for suspension mounting rods.

H. Heat Exchanger: [Aluminized] [Stainless] steel.

I. Burner Material: [Aluminized steel with stainless-steel inserts] [Stainless steel].

J. Unit Fan: Propeller blades riveted to heavy-gage steel spider bolted to cast-iron hub, dynamically balanced, and resiliently mounted.

K. Controls: Regulated redundant gas valve containing pilot solenoid valve, electric gas valve, pilot filter, pressure regulator, pilot shutoff, and manual shutoff all in one body.

1. Gas Control Valve: [Single stage] [Two stage] [Modulating].

2. Ignition: [Standing pilot] [Electronically controlled electric spark with flame sensor].

3. Fan Thermal Switch: Operates fan on heat-exchanger temperature.

4. Vent Flow Verification: [Flame rollout switch] [Differential pressure switch to verify open vent].

5. Control transformer.

6. High Limit: Thermal switch or fuse to stop burner.

7. Thermostats: Devices and wiring are specified in Section 230900 "Instrumentation and Control for HVAC."

Retain subparagraph above or one of four subparagraphs below, or revise to suit selected equipment.

8. Thermostat: Single-stage, wall-mounting type with 50 to 90 deg F (10 to 32 deg C) operating range and fan on switch.

9. Thermostat: 2-stage, wall-mounting type with 50 to 90 deg F (10 to 32 deg C) operating range and fan on switch.

10. Thermostat: Single-stage type with duct-mounting sensor and 50 to 90 deg F (10 to 32 deg C) operating range.

11. Thermostat: 2-stage type with duct-mounting sensor and 50 to 90 deg F (10 to 32 deg C) operating range.

L. Discharge Louvers: Independently adjustable horizontal blades.

M. Accessories:

Retain one or more of seven optional accessories below.

1. Vertical discharge louvers.

2. Discharge Nozzle: Discharge at [25 to 65 degrees (0.44 to 1.13 radians)] [50 to 90 degrees (0.87 to 1.57 radians)] from horizontal.

3. Four-point suspension kit.

4. Summer fan switch.

5. Unit-mounted thermostat bracket.

Retain subparagraph below for power-vented model.

6. Power Venter: Centrifugal aluminized-steel fan, with stainless-steel shaft; 120-V ac motor.

Retain subparagraph below for separated-combustion model.

7. Concentric, Terminal Vent Assembly: Combined combustion-air inlet and power-vent outlet with wall or roof caps. Include adapter assembly for connection to inlet and outlet pipes, and flashing for wall or roof penetration.

If Project has more than one type or configuration of fuel-fired unit heater, delete paragraph and subparagraphs below and schedule unit heaters on Drawings.

N. Capacities and Characteristics:

1. Gas Input: <Insert Btu/h (kW).>

2. Gas Output: <Insert Btu/h (kW).>

LEED Prerequisite EA 2 requires compliance with ASHRAE/IESNA 90.1. LEED Credit EA 1 requires efficiency in excess of minimum efficiency required by ASHRAE/IESNA 90.1.

3. Minimum Combustion Efficiency: [80] <Insert number> percent.

4. Minimum Airflow: <Insert cfm (L/s).>

5. External Static Pressure: <Insert inches wg (kPa).>

6. Motor Size: <Insert horsepower.>

7. Motor Speed: <Insert number> rpm.

8. Electrical Characteristics:

a. Volts: [120] [208] [230] <Insert value> V.

b. Phase: [Single] [Three].

c. Hertz: 60.

d. Full-Load Amperes: <Insert value.>

e. Minimum Circuit Ampacity: <Insert value.>

f. Maximum Overcurrent Protection: <Insert amperage.>

2.2 OIL-FIRED UNIT HEATERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. Retain one of first three paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Available Manufacturers: Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product: Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Modine Manufacturing Company.

2. Reznor/Thomas & Betts Corporation.

3. Sterling HVAC Products; Div. of Mestek Technology Inc.

4. <Insert manufacturer's name.>

D. Description: Factory assembled, piped, and wired, and complying with UL 731.

E. Housing: Steel, with inserts for suspension mounting rods.

F. Heat Exchanger: Minimum 0.09-inch (2.2-mm) steel.

G. Burners: Flame-retention, pressure-atomizing, forced-draft, gun type; with integral fuel pump and electronic spark ignition and flame safety.

1. Safety Device: Oil-pressure switch.

H. Unit Fan: Propeller fan with aluminum blades dynamically balanced and resiliently mounted.

I. Controls: Factory piped and prewired to electrical junction box mounted on unit, including the following:

1. Control Transformer: Integrally mounted, 120 to 24 V ac.

2. Cad-cell safety system.

3. Manual reset safety.

4. Thermostat: Devices and wiring are specified in Section 230900 "Instrumentation and Control for HVAC."

Retain subparagraph above or one of four subparagraphs below, or revise to suit selected equipment.

5. Thermostat: Single-stage, 24-V ac, wall-mounting type with 50 to 90 deg F (10 to 32 deg C) operating range and fan on switch.

6. Thermostat: 2-stage, 24-V ac, wall-mounting type with 50 to 90 deg F (10 to 32 deg C) operating range and fan on switch.

7. Thermostat: Single-stage, 24-V ac type with duct-mounting sensor and 50 to 90 deg F (10 to 32 deg C) operating range.

8. Thermostat: 2-stage, 24-V ac type with duct-mounting sensor and 50 to 90 deg F (10 to 32 deg C) operating range.

J. Automatic Fan Thermal Switch: Fan operates with heat-exchanger temperature more than 135 deg F (58 deg C).

K. Discharge Louvers: Independently adjustable horizontal blades.

L. Accessories:

Retain one or more of seven optional accessories below.

1. Vertical discharge louvers.

2. Discharge Nozzle: Discharge at [25 to 65 degrees (0.44 to 1.13 radians)] [50 to 90 degrees (0.87 to 1.57 radians)] from horizontal.

3. Summer fan switch.

4. Unit-mounted thermostat bracket.

5. Oil Booster Pump: [30-gph (108-L/h)] [70-gph (252-L/h)] capacity; motor and 2-stage fuel unit with pressure-regulating valve and strainer.

6. Oil safety valve.

7. Outdoor Combustion-Air Adapter: Sealed to housing and fitted with quick access cover or door and fitting for terminating outdoor-air duct.

If Project has more than one type or configuration of fuel-fired unit heater, delete paragraph and subparagraphs below and schedule unit heaters on Drawings.

M. Capacities and Characteristics:

1. Oil Input: <Insert gph (L/s).>

2. Heat Output: <Insert Btu/h (kW).>

LEED Prerequisite EA 2 requires compliance with ASHRAE/IESNA 90.1. LEED Credit EA 1 requires efficiency in excess of minimum efficiency required by ASHRAE/IESNA 90.1.

3. Minimum Combustion Efficiency: [80] <Insert number> percent.

4. Minimum Airflow: <Insert cfm (L/s).>

5. External Static Pressure: <Insert inches wg (kPa).>

6. Motor Size: <Insert horsepower.>

7. Motor Speed: <Insert number> rpm.

8. Electrical Characteristics:

a. Volts: [120] [208] [230] <Insert value> V.

b. Phase: [Single] [Three].

c. Hertz: 60.

d. Full-Load Amperes: <Insert value.>

e. Minimum Circuit Ampacity: <Insert value.>

f. Maximum Overcurrent Protection: <Insert amperage.>

PART 3 -  EXECUTION

3.1 INSTALLATION

Retain paragraph below for gas-fired units. Retain first option for projects in the U.S.; retain second option for projects in Canada.

A. Install and connect gas-fired unit heaters and associated fuel and vent features and systems according to [NFPA 54] [CAN/CSA B149.1], applicable local codes and regulations, and manufacturer's written installation instructions.

Retain first paragraph below for oil-fired units. Retain first option for projects in the U.S.; retain second option for projects in Canada.

B. Install and connect oil-fired unit heaters and associated fuel and vent piping according to [NFPA 31] [CAN/CSA B139], applicable local codes and regulations, and manufacturer's written installation instructions.

C. Suspended Units: Suspend from substrate using threaded rods, spring hangers, and building attachments. Secure rods to unit hanger attachments. Adjust hangers so unit is level and plumb.

D. Install piping adjacent to fuel-fired unit heater to allow service and maintenance.

Retain paragraph below for gas-fired units.

E. Gas Piping: Comply with [Section 231123 "Facility Natural-Gas Piping."] [Section 231126 "Facility Liquefied-Petroleum Gas Piping."] Connect gas piping to gas train inlet; provide union with enough clearance for burner removal and service.

Retain first paragraph below for oil-fired units.

F. Fuel Oil Piping: Comply Section 231113 "Facility Fuel-Oil Piping." Connect to fuel oil supply and return piping with shutoff valve and union at each connection.

G. Vent Connections: Comply with Section 235100 "Breechings, Chimneys, and Stacks."

H. Electrical Connections: Comply with applicable requirements in electrical Sections.

1. Install electrical devices furnished with heaters but not specified to be factory mounted.

I. Adjust initial temperature set points.

J. Adjust burner and other unit components for optimum heating performance and efficiency.

3.2 FIELD QUALITY CONTROL

A. Tests and Inspections: Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.

END OF SECTION 235533

	FUEL-FIRED UNIT HEATERS
	235533 - 1



