Copyright 2011 AIA
MasterSpec Professional
09/11

Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 235700 - HEAT EXCHANGERS FOR HVAC
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section includes [shell-and-tube] [and] [plate] heat exchangers.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product.

1. Include rated capacities, operating characteristics, and furnished specialties and accessories.

Retain "Shop Drawings" Paragraph below if heat exchangers are required to withstand specific design loads and Architect either has delegated design responsibility to Contractor or wants to review structural data as another way to verify equipment's compliance with performance requirements. Professional engineer qualifications are specified in Section 014000 "Quality Requirements."

B. Shop Drawings: Signed and sealed by a qualified professional engineer. Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

1. Design Calculations: Calculate requirements for selecting seismic restraints and for designing bases.

2. Base Details: Detail fabrication including anchorages and attachments to structure and to supported equipment.

Retain "Delegated-Design Submittal" Paragraph below if design services have been delegated to Contractor.

C. Delegated-Design Submittal: Details and design calculations for seismic restraints for heat exchangers.

1.3 INFORMATIONAL SUBMITTALS

Retain "Coordination Drawings" Paragraph below for situations where limited space necessitates maximum utilization for efficient installation of different components or if coordination is required for installation of products and materials by separate installers.

A. Coordination Drawings: Equipment room, drawn to scale, on which the following items are shown and coordinated with each other, using input from installers of the items involved:

1. Tube-removal space.

2. Structural members to which heat exchangers will be attached.

Retain "Seismic Qualification Certificates" Paragraph below if required by seismic criteria applicable to Project. Coordinate with Section 230548 "Vibration and Seismic Controls for HVAC." See ASCE/SEI 7 for certification requirements for equipment and components.

B. Seismic Qualification Certificates: For heat exchanger, accessories, and components, from manufacturer.

C. Source quality-control reports.

D. Field quality-control reports.

E. Sample warranty.

1.4 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

1.5 WARRANTY

A. Special Warranty: Manufacturer's standard form in which manufacturer agrees to repair or replace components of domestic-water heat exchangers that fail in materials or workmanship within specified warranty period.

Verify available warranties for units and components with manufacturers.

1. Warranty Periods: From date of Substantial Completion.

a. Shell-and-Tube, Domestic-Water Heat Exchangers:

1) Tube Coil: [One] <Insert number> year(s).

2) Other Components: [One] <Insert number> year(s).

b. Plate, Domestic-Water Heat Exchangers:

1) Brazed-Plate Type: [One] <Insert number> year(s).

2) Plate-and-Frame Type: [One] <Insert number> year(s).

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

2.1 PERFORMANCE REQUIREMENTS

Retain "Delegated Design" Paragraph below if Contractor is required to assume responsibility for design.

A. Delegated Design: Engage a qualified professional engineer, as defined in Section 014000 "Quality Requirements," to design seismic restraints for heat exchangers.

Retain "Seismic Performance" Paragraph below with "Seismic Qualification Certificates" Paragraph in "Informational Submittals" Article for projects requiring seismic design. Delete paragraph if performance requirements are indicated on Drawings. Model building codes and ASCE/SEI 7 establish criteria for buildings subject to earthquake motions. Coordinate requirements with structural engineer.

B. Seismic Performance: Heat exchangers shall withstand the effects of earthquake motions determined according to [ASCE/SEI 7] <Insert requirement>.

Retain first subparagraph below to define the term "withstand" as it applies to this Project. Definition varies with type of building and occupancy and is critical to valid certification. Option is used for essential facilities where equipment must operate immediately after an earthquake.

1. The term "withstand" means "the unit will remain in place without separation of any parts when subjected to the seismic forces specified[ and the unit will be fully operational after the seismic event]."

For life-safety components required to function after an earthquake (such as components that contain hazardous content and storage racks in structures open to the public), the Component Importance Factor is 1.5. For other components, the Component Importance Factor is 1.0 unless the structure is in Seismic Use Group III and component is necessary for continued operation of facility or failure of component could impair continued operation of facility, in which case the Component Importance Factor is 1.5.

2. Component Importance Factor is [1.5] [1.0].

See ASCE/SEI 7, "Coefficients for Architectural Component Table" and "Seismic Coefficients for Mechanical and Electrical Components Table," for requirements to be inserted in subparagraph below.

3. <Insert requirements for Component Amplification Factor and Component Response Modification Factor>.

2.2 SHELL-AND-TUBE HEAT EXCHANGERS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. API Heat Transfer Inc.

2. Armstrong Pumps, Inc.

3. ITT Corporation; Bell & Gossett.

4. TACO Incorporated.

5. Thrush Company, Inc.

6. <Insert manufacturer's name>.

C. Description: Packaged assembly of tank, heat-exchanger coils, and specialties.

D. Construction: Fabricate and label heat exchangers to comply with ASME Boiler and Pressure Vessel Code, Section VIII, "Pressure Vessels," Division 1.

E. Configuration: U-tube with removable bundle.

F. Shell Materials: Steel.

G. Head:

1. Materials: Cast iron.

2. Flanged and bolted to shell.

H. Tube:

1. Seamless copper tubes.

2. Tube diameter is determined by manufacturer based on service.

I. Tubesheet Materials: Steel.

J. Baffles: Steel.

K. Piping Connections:

1. NPS 2 (DN 50) and Smaller: Threaded ends according to ASME B1.20.1.

2. NPS 2-1/2 (DN 65) and Larger: Flanged ends according to ASME B16.5 for steel and stainless-steel flanges and according to ASME B16.24 for copper and copper-alloy flanges.

L. Support Saddles:

1. Fabricated of material similar to shell.

2. Fabricate foot mount with provision for anchoring to support.

Retain subparagraph below for projects in seismic areas.

3. Fabricate attachment of saddle supports to pressure vessel with reinforcement strong enough to resist heat-exchanger movement during seismic event when heat-exchanger saddles are anchored to building structure.

If Project has more than one type or configuration of shell-and-tube heat exchanger, delete "Capacities and Characteristics" Paragraph below and schedule on Drawings.

M. Capacities and Characteristics:

1. General:

a. Shell Diameter: <Insert NPS (DN)>.

b. Heat-Exchanger Length: <Insert inches (mm)>.

c. Heat-Exchanger Surface Area: <Insert sq. ft. (sq. m)>.

d. Number of Passes: <Insert number>.

e. Heat Exchanged: <Insert Btu/h (kW)>.

f. Operating Weight: <Insert lb (kg)>.

2. Shell Side:

a. Fluid: [Water] [Steam] <Insert type>.

b. Working Pressure: <Insert psig (kPa)>.

Retain "Supply Pressure" Subparagraph below for steam-to-water or steam-to-steam heat exchangers.

c. Supply Pressure: <Insert psig (kPa)>.

d. Steam Flow Rate: <Insert lb/h (kg/h)>.

Retain "Water Flow Rate" Subparagraph below for steam-to-water or water-to-water heat exchangers.

e. Water Flow Rate: <Insert gpm (L/s)>.

f. Pressure Drop: <Insert psig (kPa)>.

g. Inlet Temperature: <Insert deg F (deg C)>.

h. Outlet Temperature: <Insert deg F (deg C)>.

i. Fouling Factor: <Insert value>.

j. Inlet Size: <Insert NPS (DN)>.

k. Outlet Size: <Insert NPS (DN)>.

3. Tube Side:

a. Fluid: [Water] [Steam] <Insert type>.

b. Working Pressure: <Insert psig (kPa)>.

Retain "Supply Pressure" Subparagraph below for steam-to-water or steam-to-steam heat exchangers.

c. Supply Pressure: <Insert psig (kPa)>.

d. Steam Flow Rate: <Insert lb/h (kg/h)>.

Retain "Water Flow Rate" Subparagraph below for steam-to-water or water-to-water heat exchangers.

e. Water Flow Rate: <Insert gpm (L/s)>.

f. Pressure Drop: <Insert psig (kPa)>.

g. Inlet Temperature: <Insert deg F (deg C)>.

h. Outlet Temperature: <Insert deg F (deg C)>.

i. Fouling Factor: <Insert value>.

j. Inlet Size: <Insert NPS (DN)>.

k. Outlet Size: <Insert NPS (DN)>.

2.3 GASKETED-PLATE HEAT EXCHANGERS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Alfa Laval Inc.

2. API Heat Transfer Inc.

3. APV; a brand of SPX Corporation.

4. Armstrong Pumps, Inc.

5. Delta T Heat Exchangers.

6. ITT Corporation; Bell & Gossett.

7. Mueller, Paul, Company.

8. Polaris Plate Heat Exchangers.

9. SEC Heat Exchangers.

10. TACO Incorporated.

11. Thermo Dynamics Ltd.

12. Tranter, Inc.

13. <Insert manufacturer's name>.

C. Configuration: Freestanding assembly consisting of frame support, top and bottom carrying and guide bars, fixed and movable end plates, tie rods, individually removable plates, and one-piece gaskets.

Use "Construction" Paragraph below when system pressures and application dictate that heat exchangers are pressure vessels.

D. Construction: Fabricate and label heat exchangers to comply with ASME Boiler and Pressure Vessel Code, Section VIII, "Pressure Vessels," Division 1.

E. Frame:

1. Capacity to accommodate [20] <Insert number> percent additional plates.

2. Painted carbon steel with provisions for anchoring to support.

F. Top and Bottom Carrying and Guide Bars: Painted carbon steel, aluminum, or stainless steel.

Retain subparagraph below for projects in seismic areas.

1. Fabricate attachment of heat-exchanger carrying and guide bars with reinforcement strong enough to resist heat-exchanger movement during seismic event when heat-exchanger carrying and guide bars are anchored to building structure.

G. End-Plate Material: Painted carbon steel.

H. Tie Rods and Nuts: Steel or stainless steel.

I. Plate Material: [0.024 inch (0.6 mm)] <Insert thickness> thick before stamping; Type 304 stainless steel.

J. Gasket Materials: Nitrile rubber.

K. Piping Connections:

1. NPS 2 (DN 50) and Smaller: Threaded ends according to ASME B1.20.1.

2. NPS 2-1/2 (DN 65) and Larger: Flanged ends according to ASME B16.5 for steel and stainless-steel flanges and according to ASME B16.24 for copper and copper-alloy flanges.

L. Enclose plates in solid aluminum removable shroud.

If Project has more than one type or configuration of gasketed-plate heat exchanger, delete "Capacities and Characteristics" Paragraph below and schedule on Drawings.

M. Capacities and Characteristics:

1. General:

a. Heat-Exchanger Surface Area: <Insert sq. ft. (sq. m)>.

b. Number of Plates: <Insert number>.

c. Number of Passes: [One] <Insert number>.

d. Heat Exchanged: <Insert Btu/h (kW)>.

e. Operating Weight: <Insert lb (kg)>.

2. Hot Side:

a. Fluid: [Water] [Steam] <Insert type>.

b. Working Pressure: <Insert psig (kPa)>.

Retain "Supply Pressure" Subparagraph below for steam-to-water or steam-to-steam heat exchangers.

c. Supply Pressure: <Insert psig (kPa)>.

d. Steam Flow Rate: <Insert lb/h (kg/h)>.

Retain "Water Flow Rate" Subparagraph below for steam-to-water or water-to-water heat exchangers.

e. Water Flow Rate: <Insert gpm (L/s)>.

f. Pressure Drop: <Insert psig (kPa)>.

g. Inlet Temperature: <Insert deg F (deg C)>.

h. Outlet Temperature: <Insert deg F (deg C)>.

i. Fouling Factor: <Insert value>.

j. Inlet Size: <Insert NPS (DN)>.

k. Outlet Size: <Insert NPS (DN)>.

3. Cold Side:

a. Fluid: [Water] [Steam] <Insert type>.

b. Working Pressure: <Insert psig (kPa)>.

Retain "Supply Pressure" Subparagraph below for steam-to-water or steam-to-steam heat exchangers.

c. Supply Pressure: <Insert psig (kPa)>.

d. Steam Flow Rate: <Insert lb/h (kg/h)>.

Retain "Water Flow Rate" Subparagraph below for steam-to-water or water-to-water heat exchangers.

e. Water Flow Rate: <Insert gpm (L/s)>.

f. Pressure Drop: <Insert psig (kPa)>.

g. Inlet Temperature: <Insert deg F (deg C)>.

h. Outlet Temperature: <Insert deg F (deg C)>.

i. Fouling Factor: <Insert value>.

j. Inlet Size: <Insert NPS (DN)>.

k. Outlet Size: <Insert NPS (DN)>.

2.4 BRAZED-PLATE HEAT EXCHANGERS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Alfa Laval Inc.

2. API Heat Transfer Inc.

3. APV; a brand of SPX Corporation.

4. Armstrong Pumps, Inc.

5. GEA PHE Systems North America Inc.

6. ITT Corporation; Bell & Gossett.

7. Mueller, Paul, Company.

8. Polaris Plate Heat Exchangers.

9. Tranter, Inc.

10. <Insert manufacturer's name>.

C. Configuration: Brazed assembly consisting of embossed or pressed stainless-steel plates brazed together and two end plates, one with threaded nozzles and one with pattern-embossed plates.

Use "Construction" Paragraph below when system pressures and application dictate that heat exchangers are pressure vessels.

D. Construction: Fabricate and label heat exchangers to comply with ASME Boiler and Pressure Vessel Code, Section VIII, "Pressure Vessels," Division 1.

E. End-Plate Material: Type 316 stainless steel.

F. Threaded Nozzles: Type 316 stainless steel.

G. Plate Material: Type 316 stainless steel.

H. Brazing Material: Copper.

If Project has more than one type or configuration of brazed-plate heat exchanger, delete "Capacities and Characteristics" Paragraph below and schedule on Drawings.

I. Capacities and Characteristics:

1. General:

a. Heat-Exchanger Surface Area: <Insert sq. ft. (sq. m)>.

b. Heat Exchanged: <Insert Btu/h (kW)>.

c. Operating Weight: <Insert lb (kg)>.

2. Hot Side:

a. Fluid: [Water] [Steam] <Insert type>.

b. Working Pressure: <Insert psig (kPa)>.

Retain "Supply Pressure" Subparagraph below for steam-to-water or steam-to-steam heat exchangers.

c. Supply Pressure: <Insert psig (kPa)>.

d. Steam Flow Rate: <Insert lb/h (kg/h)>.

Retain "Water Flow Rate" Subparagraph below for steam-to-water or water-to-water heat exchangers.

e. Water Flow Rate: <Insert gpm (L/s)>.

f. Pressure Drop: <Insert psig (kPa)>.

g. Inlet Temperature: <Insert deg F (deg C)>.

h. Outlet Temperature: <Insert deg F (deg C)>.

i. Fouling Factor: <Insert value>.

j. Inlet Size: <Insert NPS (DN)>.

k. Outlet Size: <Insert NPS (DN)>.

3. Cold Side:

a. Fluid: [Water] [Steam] <Insert type>.

b. Working Pressure: <Insert psig (kPa)>.

Retain "Supply Pressure" Subparagraph below for steam-to-water or steam-to-steam heat exchangers.

c. Supply Pressure: <Insert psig (kPa)>.

d. Steam Flow Rate: <Insert lb/h (kg/h)>.

Retain "Water Flow Rate" Subparagraph below for steam-to-water or water-to-water heat exchangers.

e. Water Flow Rate: <Insert gpm (L/s)>.

f. Pressure Drop: <Insert psig (kPa)>.

g. Inlet Temperature: <Insert deg F (deg C)>.

h. Outlet Temperature: <Insert deg F (deg C)>.

i. Fouling Factor: <Insert value>.

j. Inlet Size: <Insert NPS (DN)>.

k. Outlet Size: <Insert NPS (DN)>.

2.5 SOURCE QUALITY CONTROL

Retain "Factory Tests" Paragraph below for factory-assembled heat exchangers. Factory tests are an added cost option and may not be available from some manufacturers. Verify requirement with Owner.

A. Factory Tests: Test and inspect heat exchangers according to ASME Boiler and Pressure Vessel Code, Section VIII, "Pressure Vessels," Division 1. Affix ASME label.

B. Hydrostatically test heat exchangers to minimum of one and one-half times pressure rating before shipment.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

C. Heat exchangers will be considered defective if they do not pass tests and inspections.

D. Prepare test and inspection reports.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Equipment Mounting:

Retain first subparagraph below to require equipment to be installed on cast-in-place concrete equipment bases.

1. Install heat exchangers on cast-in-place concrete equipment bases. Comply with requirements for equipment bases and foundations specified in [Section 033000 "Cast-in-Place Concrete."] [Section 033053 "Miscellaneous Cast-in-Place Concrete."]

Retain one of two subparagraphs below. Retain first for projects in seismic areas; retain second for projects not in seismic areas. Indicate vibration isolation and seismic-control device type and minimum deflection in supported equipment schedule on Drawings.

2. Comply with requirements for vibration isolation and seismic control devices specified in Section 230548 "Vibration and Seismic Controls for HVAC."

3. Comply with requirements for vibration isolation devices specified in Section 230548.13 "Vibration Controls for HVAC."

Retain first paragraph below for contractor-fabricated saddle supports. Delete if factory-fabricated cradle supports are retained.

B. Install shell-and-tube heat exchangers on saddle supports.

C. Install gasketed-plate heat exchanger on custom-designed wall supports anchored to structure as indicated on Drawings.

D. Install metal shroud over installed gasketed-plate heat exchanger according to manufacturer's written instructions.

E. Install brazed-plate heat exchanger on custom-designed wall supports anchored to structure as indicated on Drawings.

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

F. Comply with requirements for piping specified in Section 232113 "Hydronic Piping" and Section 232116 "Hydronic Piping Specialties."Section 15179 "Hydronic Piping Specialties." Drawings indicate general arrangement of piping, fittings, and specialties.

Retain first paragraph below for steam heat exchangers.

G. Comply with requirements for steam and condensate piping specified in Section 232213 "Steam and Condensate Heating Piping" and Section 232216 "Steam and Condensate Piping Specialties."

H. Maintain manufacturer's recommended clearances for tube removal, service, and maintenance.

I. Install piping adjacent to heat exchangers to allow space for service and maintenance of heat exchangers. Arrange piping for easy removal of heat exchangers.

J. Install shutoff valves at heat-exchanger inlet and outlet connections.

K. Install relief valves on heat-exchanger heated-fluid connection and install pipe relief valves, full size of valve connection, to floor drain.

L. Install vacuum breaker at heat-exchanger steam inlet connection.

Retain first paragraph below for shell-and-tube heat exchangers.

M. Install hose end valve to drain shell.

N. Install thermometer on heat-exchanger and[ inlet and] outlet piping, and install thermometer on heating-fluid[ inlet and] outlet piping. Comply with requirements for thermometers specified in Section 230519 "Meters and Gages for HVAC Piping."

O. Install pressure gages on heat-exchanger and heating-fluid piping. Comply with requirements for pressure gages specified in Section 230519 "Meters and Gages for HVAC Piping."

3.2 FIELD QUALITY CONTROL

Retain first paragraph below to require Contractor to perform tests and inspections.

A. Perform the following tests and inspections[ with the assistance of a factory-authorized service representative]:

1. Leak Test: After installation, charge system and test for leaks. Repair leaks and retest until no leaks exist.

2. Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

B. Heat exchanger will be considered defective if it does not pass tests and inspections.

C. Prepare test and inspection reports.

3.3 CLEANING

A. After completing system installation, including outlet fitting and devices, inspect exposed finish. Remove burrs, dirt, and construction debris and repair damaged finishes.

END OF SECTION 235700

	HEAT EXCHANGERS FOR HVAC
	235700 - 1



