Copyright 2011 AIA
MasterSpec Professional
12/11

Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 236200 - PACKAGED COMPRESSOR AND CONDENSER UNITS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section includes packaged, air-cooled, refrigerant compressor and condenser units.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product indicated.

B. LEED Submittals:

1. Product Data for Prerequisite EA 2: Documentation indicating that units comply with applicable requirements in ASHRAE/IESNA 90.1.

Coordinate "Product Data for Credit EA 4" Subparagraph below with requirements for refrigerants.

2. Product Data for Credit EA 4: Documentation indicating that compressor and condenser units and refrigerants comply.

C. Shop Drawings: For compressor and condenser units. Include plans, elevations, sections, details, and attachments to other work.

1. Wiring Diagrams: For power, signal, and control wiring.

1.3 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

B. Fabricate and label refrigeration system according to ASHRAE 15, "Safety Standard for Refrigeration Systems."

Retain "ASHRAE/IESNA 90.1 Compliance" Paragraph below to require compliance with ASHRAE/IESNA 90.1. Also, LEED Prerequisite EA 2 requires compliance with ASHRAE/IESNA 90.1.

C. ASHRAE/IESNA 90.1 Compliance: Applicable requirements in ASHRAE/IESNA 90.1, Section 6, "Heating, Ventilating, and Air-Conditioning."

1.4 WARRANTY

Warranties vary among manufacturers from covering the whole unit up to four years, to only the compressor for five to 10 years or the condenser coil for five years. Extended special warranties are limited to units in the 1- to 5-ton (3.5- to 17.6-kW) range, and then are usually restricted to residential applications.

A. Special Warranty: Manufacturer's standard form in which manufacturer agrees to repair or replace components of compressor and condenser units that fail in materials or workmanship within specified warranty period.

1. Failures include, but are not limited to, the following:

a. Compressor failure.

b. Condenser coil leak.

Verify available warranties and warranty periods for units and components with manufacturers listed in Part 2 articles.

2. Warranty Period: [Five] [10] <Insert number> years from date of Substantial Completion.

3. Warranty Period (Compressor Only): [Five] [Seven] [10] <Insert number> years from date of Substantial Completion.

4. Warranty Period (Components Other Than Compressor): [Five] [10] <Insert number> years from date of Substantial Completion.

5. Warranty Period (Condenser Coil Only): [Five] <Insert number> years from date of Substantial Completion.

PART 2 -  PRODUCTS

2.1 COMPRESSOR AND CONDENSER UNITS, AIR COOLED, 1 TO 5 TONS (3.5 TO 17.6 kW)
See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Carrier Corporation; Commercial HVAC Systems.

2. Lennox International Inc.

3. Rheem Air Conditioning Division.

4. Ruud Air Conditioning Division.

5. Trane; a business of American Standard Companies.

6. YORK; a Johnson Controls company.

7. <Insert manufacturer's name>.

C. Description: Factory assembled and tested; consisting of compressor, condenser coil, fan, motors, refrigerant reservoir, and operating controls.

D. Compressor: Scroll, hermetically sealed, with rubber vibration isolators.

1. Motor: [Single] [Two] speed, and includes thermal- and current-sensitive overload devices, start capacitor, relay, and contactor.

Two-speed compressor in first subparagraph below is not available from all manufacturers.

2. Two-Speed Compressor: Include manual-reset, high-pressure switch and automatic-reset, low-pressure switch.

Accumulator in subparagraph below is available only on 4- and 5-ton (14- and 17.6-kW) units.

3. Accumulator: Suction tube.

Retain one of two "Refrigerant" paragraphs below to require a specific refrigerant type; delete both if any refrigerant type is acceptable. LEED-NC, LEED-CS, and LEED for Schools Credit EA 4 requires HVAC&R equipment to comply with requirements for enhanced refrigerant management. Retain second or third option in first paragraph or retain second paragraph for Credit EA 4.

E. Refrigerant: [R-22] [R-407C] [R-410A] <Insert type>.

F. Refrigerant: R-407C or R-410A.

G. Condenser Coil: Seamless copper-tube, aluminum-fin coil; circuited for integral liquid subcooler, with removable drain pan and brass service valves with service ports.

H. Condenser Fan: Direct-drive, aluminum propeller fan; with permanently lubricated, totally enclosed fan motor with thermal-overload protection[ and ball bearings].

I. Accessories:

Revise list of accessories below to suit Project. Not all accessories are available from all manufacturers.

1. Coastal Filter: Mesh screen to protect condenser coil from salt damage.

2. Crankcase heater.

3. Cycle Protector: Automatic-reset timer to prevent rapid compressor cycling.

4. [Electronic programmable thermostat] [Low-voltage thermostat and subbase] to control compressor and condenser unit and evaporator fan.

5. Evaporator Freeze Thermostat: Temperature-actuated switch that stops unit when evaporator reaches freezing temperature.

6. Filter-dryer.

7. High-Pressure Switch: Automatic-reset switch cycles compressor off on high refrigerant pressure.

8. Liquid-line solenoid.

Retain one of two "Low-Ambient Controller" subparagraphs below if required.

9. Low-Ambient Controller: Cycles condenser fan to permit operation down to [30 deg F (minus 1 deg C)] [0 deg F (minus 18 deg C)] [ with time-delay relay to bypass low-pressure switch].

10. Low-Ambient Controller: Controls condenser fan speed to permit operation down to minus 20 deg F (minus 29 deg C)[ with time-delay relay to bypass low-pressure switch].

11. Low-Pressure Switch: Automatic-reset switch cycles compressor off on low refrigerant pressure.

12. PE mounting base.

13. Precharged and insulated suction and liquid tubing.

14. Sound Hood: Wraps around sound attenuation cover for compressor.

15. Thermostatic expansion valve.

16. Time-Delay Relay: Continues operation of evaporator fan after compressor shuts off.

Retain first subparagraph below for heat pump units.

17. Reversing valve.

18. <Insert accessories>.

J. Unit Casing: Galvanized steel, finished with baked enamel; with removable panels for access to controls, weep holes for water drainage, and mounting holes in base. Mount service valves, fittings, and gage ports on exterior of casing.

If Project has more than one type or configuration of compressor and condenser unit, delete paragraph below and schedule the units on Drawings.

K. Capacities and Characteristics:

1. Compressor and Condenser Unit:

a. Full-Load Cooling Capacity: <Insert MBh (kW)>.

Retain one of first three subparagraphs below. LEED Prerequisite EA 2 requires compliance with ASHRAE/IESNA 90.1. LEED Credit EA 1 requires efficiency in excess of minimum efficiency required by ASHRAE/IESNA 90.1.

b. Energy-Efficiency Ratio (EER): <Insert value>.

c. Seasonal Energy-Efficiency Ratio (SEER): <Insert value>.

d. Coefficient of Performance (COP): <Insert value>.

e. Compressor Suction Temperature: <Insert deg F (deg C)>.

f. Capacity Steps: <Insert number>.

Repeat first subparagraph below for multiple-circuit units.

2. Refrigerant Connections:

a. Liquid Pipe Size: <Insert NPS (DN)>.

b. Suction Pipe Size: <Insert NPS (DN)>.

3. Compressor:

a. Rated-Load Amperes: <Insert value>.

b. Locked-Rotor Amperes: <Insert value>.

c. Power Input: <Insert kilowatts>.

4. Air-Cooled Condenser:

a. Ambient-Air Temperature: <Insert deg F (deg C)>.

b. Airflow: <Insert cfm (L/s)>.

c. Number of Condenser Fans: <Insert number>.

d. Condenser Fan Motor Size: <Insert horsepower>.

5. Electrical Characteristics:

a. Kilowatt Input: <Insert value>.

b. Volts: <Insert value>.

c. Phase: <Insert value>.

d. Hertz: <Insert value>.

e. Maximum Circuit Ampacity: <Insert value>.

f. Maximum Instantaneous Current Flow during Startup: <Insert value>.

g. Maximum Overcurrent Protection: <Insert amperage>.

2.2 COMPRESSOR AND CONDENSER UNITS, AIR COOLED, 6 TO 120 TONS (21 TO 422 kW)
See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Carrier Corporation; Commercial HVAC Systems.

2. Continental Products.

3. Dunham-Bush, Inc.

4. Engineered Air.

5. Lennox International Inc.

6. McQuay International.

7. Rheem Air Conditioning Division.

8. Ruud Air Conditioning Division.

9. Trane; a business of American Standard Companies.

10. YORK; a Johnson Controls company.

11. <Insert manufacturer's name>.

C. Description: Factory assembled and tested, air cooled; consisting of casing, compressors, condenser coils, condenser fans and motors, and unit controls.

Retain one of two "Compressor" paragraphs below.

D. Compressor: Hermetic scroll compressor designed for service with crankcase sight glass, crankcase heater, and backseating service access valves on suction and discharge ports.

1. Capacity Control: [On-off compressor cycling] [Hot-gas bypass].

E. Compressor: Hermetic or semihermetic rotary screw compressor designed for service with crankcase sight glass, crankcase heater, and backseating service access valves on suction and discharge ports.

1. Capacity Control: [On-off compressor cycling] [Modulating slide-valve assembly or port unloaders] [Variable-frequency controller] [Hot-gas bypass].

Retain one of two "Refrigerant" paragraphs below to require a specific refrigerant type; delete both if any refrigerant type is acceptable. LEED-NC, LEED-CS, and LEED for Schools Credit EA 4 requires HVAC&R equipment to comply with requirements for enhanced refrigerant management. Retain second, third, or fourth option in first paragraph or retain second paragraph for Credit EA 4.

F. Refrigerant: [R-22] [R-407C] [R-410A] [R-134a] <Insert type>.

G. Refrigerant: R-407C, R-410A, or R-134a.

H. Condenser Coil: Seamless copper-tube, aluminum-fin coil, including subcooling circuit and backseating liquid-line service access valve. Factory pressure test coils, then dehydrate by drawing a vacuum and fill with a holding charge of nitrogen or refrigerant.

I. Condenser Fan: Propeller-type vertical discharge; either directly or belt driven. Include the following:

1. Permanently lubricated, ball-bearing[ totally enclosed] motors.

2. Separate motor for each fan.

3. Dynamically and statically balanced fan assemblies.

J. Operating and safety controls include the following:

1. Manual-reset, high-pressure cutout switches.

2. Automatic-reset, low-pressure cutout switches.

3. Low-oil-pressure cutout switch.

4. Compressor-winding thermostat cutout switch.

5. Three-leg, compressor-overload protection.

6. Control transformer.

7. Magnetic contactors for compressor and condenser fan motors.

8. Timer to prevent excessive compressor cycling.

K. Accessories:

Revise list of accessories below to suit Project. Not all accessories are available from all manufacturers.

1. [Electronic programmable thermostat] [Low-voltage thermostat and subbase] to control compressor and condenser unit and evaporator fan.

Retain one of two "Low-Ambient Controller" subparagraphs below if required.

2. Low-Ambient Controller: Cycles condenser fan to permit operation down to 0 deg F (minus 18 deg C)[ with time-delay relay to bypass low-pressure switch].

3. Low-Ambient Controller: Controls condenser fan speed to permit operation down to minus 20 deg F (minus 29 deg C)[ with time-delay relay to bypass low-pressure switch].

4. Gage Panel: Package with refrigerant circuit suction and discharge gages.

5. Hot-gas bypass kit.

6. Part-winding-start timing relay, circuit breakers, and contactors.

Retain first subparagraph below for heat pump units.

7. Reversing valve.

8. <Insert accessories>.

L. Unit Casings: Designed for outdoor installation with weather protection for components and controls and with removable panels for required access to compressors, controls, condenser fans, motors, and drives. Additional features include the following:

1. Steel, galvanized or zinc coated, for exposed casing surfaces; treated and finished with manufacturer's standard paint coating.

2. Perimeter base rail with forklift slots and lifting holes to facilitate rigging.

3. Gasketed control panel door.

4. Nonfused disconnect switch, factory mounted and wired, for single external electrical power connection.

Subparagraph below describes optional accessories, which may not be available from all manufacturers.

5. Condenser coil [hail guard] [grille].

If Project has more than one type or configuration of compressor and condenser unit, delete paragraph below and schedule the units on Drawings.

M. Capacities and Characteristics:

1. Compressor and Condenser Unit:

a. Full-Load Cooling Capacity: <Insert MBh (kW)>.

Retain one of first three subparagraphs below. LEED Prerequisite EA 2 requires compliance with ASHRAE/IESNA 90.1. LEED Credit EA 1 requires efficiency in excess of minimum efficiency required by ASHRAE/IESNA 90.1.

b. Energy-Efficiency Ratio (EER): <Insert value>.

c. Seasonal Energy-Efficiency Ratio (SEER): <Insert value>.

d. Coefficient of Performance (COP): <Insert value>.

e. Compressor Suction Temperature: <Insert deg F (deg C)>.

f. Capacity Steps: <Insert number>.

Repeat first subparagraph below for multiple-circuit units.

2. Refrigerant Connections:

a. Liquid Pipe Size: <Insert NPS (DN)>.

b. Suction Pipe Size: <Insert NPS (DN)>.

3. Compressors:

a. Number of Compressors: <Insert number>.

b. Rated-Load Amperes: <Insert value>.

c. Locked-Rotor Amperes: <Insert value>.

d. Power Input: <Insert kilowatts>.

4. Air-Cooled Condenser:

a. Ambient-Air Temperature: <Insert deg F (deg C)>.

b. Airflow: <Insert cfm (L/s)>.

c. Number of Condenser Fans: <Insert number>.

d. Condenser Fan Motor Size: <Insert horsepower>.

5. Electrical Characteristics:

a. Kilowatt Input: <Insert value>.

b. Volts: <Insert value>.

c. Phase: <Insert value>.

d. Hertz: <Insert value>.

e. Maximum Circuit Amperes: <Insert value>.

f. Maximum Instantaneous Current Flow during Startup: <Insert value>.

g. Maximum Overcurrent Protection: <Insert amperage>.

2.3 SOURCE QUALITY CONTROL

Retain "Energy Efficiency" Paragraph below to require compliance with ASHRAE/IESNA 90.1. LEED Prerequisite EA 2 requires compliance with ASHRAE/IESNA 90.1.

A. Energy Efficiency: Equal to or greater than prescribed by ASHRAE/IESNA 90.1, "Energy Efficient Design of New Buildings except Low-Rise Residential Buildings," Section 6, "Heating, Ventilating, and Air-Conditioning."

B. Testing Requirements: Factory test sound-power-level ratings according to [ARI 270] [ARI 370].

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Install units level and plumb, firmly anchored in locations indicated.

Retain first paragraph below and delete "Equipment Mounting" paragraph below if units are installed on roof.

B. Install roof-mounting units on equipment supports specified in Section 077200 "Roof Accessories."

C. Equipment Mounting:

Retain first subparagraph below to require equipment to be installed on cast-in-place concrete equipment bases.

1. Install compressor and condenser units on cast-in-place concrete equipment bases. Comply with requirements for equipment bases and foundations specified in [Section 033000 "Cast-in-Place Concrete."] [Section 033053 "Miscellaneous Cast-in-Place Concrete."]

Retain one of two subparagraphs below. Retain first for projects in seismic areas; retain second for projects not in seismic areas. Indicate vibration isolation and seismic-control device type and minimum deflection in supported equipment schedule on Drawings.

2. Comply with requirements for vibration isolation and seismic control devices specified in Section 230548 "Vibration and Seismic Controls for HVAC."

3. Comply with requirements for vibration isolation devices specified in Section 230548.13 "Vibration Controls for HVAC."

D. Maintain manufacturer's recommended clearances for service and maintenance.

E. Loose Components: Install electrical components, devices, and accessories that are not factory mounted.

3.2 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Comply with requirements for piping in Section 232113 "Hydronic Piping" and Section 232116 "Hydronic Piping Specialties."Section 15179 "Hydronic Piping Specialties." Drawings indicate general arrangement of piping, fittings, and specialties.

B. Where installing piping adjacent to equipment, allow space for service and maintenance of equipment.

C. Connect precharged refrigerant tubing to unit's quick-connect fittings. Install tubing so it does not interfere with access to unit. Install furnished accessories.

Retain last paragraph above for units using precharged tubing or paragraph below for assembled systems.

D. Connect refrigerant piping to air-cooled compressor and condenser units; maintain required access to unit. Install furnished field-mounted accessories. Refrigerant piping and specialties are specified in Section 232300 "Refrigerant Piping."

3.3 FIELD QUALITY CONTROL

A. Perform tests and inspections.

B. Tests and Inspections:

1. Perform each visual and mechanical inspection and electrical test. Certify compliance with test parameters.

2. Leak Test: After installation, charge system with refrigerant and oil and test for leaks. Repair leaks, replace lost refrigerant and oil, and retest until no leaks exist.

3. Operational Test: After electrical circuitry has been energized, start units to confirm proper motor operation and unit operation, product capability, and compliance with requirements.

4. Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.

5. Verify proper airflow over coils.

C. Verify that vibration isolation and flexible connections properly dampen vibration transmission to structure.

END OF SECTION 236200

	PACKAGED COMPRESSOR AND CONDENSER UNITS
	236200 - 1



