Copyright 2011 AIA
MasterSpec Professional
09/11

Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 236313 - AIR-COOLED REFRIGERANT CONDENSERS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section includes packaged, air-cooled refrigerant condensers for [outdoor] [indoor] installation.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product indicated.

B. LEED Submittals:

1. Product Data for Prerequisite EA 2: Documentation indicating that units comply with applicable requirements in ASHRAE/IESNA 90.1.

Coordinate "Product Data for Credit EA 4" Subparagraph below with requirements for refrigerants.

2. Product Data for Credit EA 4: Documentation indicating that air-cooled refrigerant condensers and refrigerants comply.

C. Shop Drawings: For air-cooled refrigerant condensers. Include plans, elevations, sections, details, and attachments to other work.

1. Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

2. Wiring Diagrams: For power, signal, and control wiring.

1.3 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

1.4 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

Retain "ASHRAE/IESNA 90.1 Compliance" Paragraph below to require compliance with ASHRAE/IESNA 90.1. LEED Prerequisite EA 2 requires compliance with ASHRAE/IESNA 90.1.

B. ASHRAE/IESNA 90.1 Compliance: Applicable requirements in ASHRAE/IESNA 90.1, Section 6 - "Heating, Ventilating, and Air-Conditioning."

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of two paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Carrier Corporation; Commercial HVAC Systems.

2. Colmac Coil Manufacturing, Inc.

3. Coolenheat Inc.

4. Dunham-Bush, Inc.

5. Engineered Air.

6. Heatcraft Refrigeration Products LLC.

7. McQuay International.

8. Trane; a business of American Standard Companies.

9. USA Coil & Air.

10. YORK; a Johnson Controls company.

11. <Insert manufacturer's name>.

2.2 MANUFACTURED UNITS

A. Description: Factory assembled and tested; consisting of casing, condenser coils, condenser fans and motors, and unit controls.

Retain one of two "Refrigerant" paragraphs below to require a specific refrigerant type; delete both if any refrigerant type is acceptable. LEED-NC, LEED-CS, and LEED for Schools Credit EA 4 requires HVAC&R equipment to comply with requirements for enhanced refrigerant management. Retain second or third option in first paragraph or retain second paragraph for Credit EA 4.

B. Refrigerant: [R-22] [R-407C] [R-410A] <Insert type>.

C. Refrigerant: R-407C or R-410A.

D. Condenser Coil: Factory tested at 425 psig (2930 kPa).

1. Tube: [1/2-inch- (13-mm-) diameter seamless copper.] [3/8-inch- (10-mm-) diameter seamless copper.] [5/8-inch- (16-mm-) diameter seamless copper.] [5/8-inch- (16-mm-) diameter steel.]

2. Coil Fin: [Aluminum] [Steel].

Retain first subparagraph below if all coils require the same coating. If Project requires multiple coil materials with different coatings or if some coils do not require coatings, delete subparagraph and indicate coatings for each coil in schedule on Drawings.

3. Coating: [Thermoplastic vinyl] [Epoxy] [Zinc] [Synthetic resin] [Phenolic] [Polytetrafluoroethylene] [Vinyl ester] [Hot-dip galvanized] [Powder-baked enamel]; <Insert manufacturer's name; trade name>.

4. Circuit: To match compressors[ with liquid subcooling coil].

Retain one of two "Condenser Fans and Drives" paragraphs below for fan type.

E. Condenser Fans and Drives: Propeller fans with [aluminum or galvanized-steel] [galvanized-steel] [stainless-steel] fan blades, for [vertical] [horizontal] air discharge; directly driven with [permanently lubricated] [grease-lubricated] ball-bearing motors with integral current- and thermal-overload protection.

1. Weather-proof motors with rain shield and shaft slinger.

2. Extend grease lines to outside of casing.

F. Condenser Fans and Drives: Forward-curved centrifugal fans for [vertical] [horizontal] air discharge.

1. Fan on steel shaft with self-aligning ball bearings.

2. V-belt drive with minimum of two belts; variable pitch drive pulley.

3. Motor mounted on adjustable slide base.

G. Operating and Safety Controls: Include condenser fan motor thermal and overload cutouts; 115-V control transformer, if required; magnetic contactors for condenser fan motors and a nonfused factory-mounted and -wired disconnect switch for single external electrical power connection.

1. Fan Cycling Control: [Head pressure switches] [Ambient thermostats].

H. Casings: [Galvanized or zinc-coated steel treated and finished with manufacturer's standard paint coating] [Aluminum] [Stainless steel], designed for outdoor installation with weather protection for components and controls, and with the following:

1. Removable panels for access to controls, condenser fans, motors, and drives.

2. [Plated] [Stainless]-steel fan guards.

3. Lifting eyes.

Retain one of four options in subparagraph below for leg height; 20 inches (500 mm) is standard.

4. Removable legs, [20 inches (500 mm)] [30 inches (760 mm)] [36 inches (910 mm)] [42 inches (1060 mm)] high.

2.3 CAPACITIES AND CHARACTERISTICS

If Project has more than one type or configuration of air-cooled refrigerant condenser unit, delete this article and schedule the units on Drawings.

A. Heat-Rejection Capacity: <Insert MBh (kW)>.

B. Condensing Temperature:

1. Saturated Discharge Temperature: <Insert deg F (deg C)>.

2. Saturated Suction Temperature: <Insert deg F (deg C)>.

3. Subcooling Temperature: <Insert deg F (deg C)>.

C. Ambient-Air Temperature: <Insert deg F (deg C)>.

D. Refrigerant Pipe Connections:

1. Number of Connections: <Insert number>.

2. Liquid Pipe Size: <Insert NPS (DN)>.

3. Suction Pipe Size: <Insert NPS (DN)>.

E. Coils:

1. Arrangement: <Insert description>.

2. Number of Rows: <Insert number>.

3. Fin Spacing: [12 fins/inch (2 mm)] <Insert value>.

4. Total Face Area: <Insert sq. ft. (sq. m)>.

F. Fans:

1. Number of Condenser Fans: <Insert number>.

2. Diameter: <Insert inches (mm)>.

3. RPM: <Insert number>.

4. Total Airflow: <Insert cfm (L/s)>.

5. Condenser Fan Motor Size: <Insert horsepower>.

G. Electrical Characteristics:

1. Kilowatts: <Insert value>.

2. Volts: <Insert value>.

3. Phase: <Insert value>.

4. Hertz: <Insert value>.

5. Maximum Circuit Ampacity: <Insert value>.

6. Maximum Instantaneous Current Flow during Startup: <Insert value>.

7. Maximum Overcurrent Protection: <Insert amperage>.

2.4 MOTORS

Default motor characteristics are specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

A. Comply with NEMA designation, temperature rating, service factor, enclosure type, and efficiency requirements for motors specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

Retain first subparagraph below if enclosure is not open-dripproof type.

1. Enclosure Type: Totally enclosed, fan cooled.

2. Motor Sizes: Minimum size as indicated. If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

Retain first subparagraph below to require enclosed switches to be supplied with unit.

3. Mount unit-mounted disconnect switches on [exterior] [interior] of unit.

If unique characteristics are required for motors in this Section, insert subparagraphs below.

4. <Insert unique motor characteristics>.

2.5 SOURCE QUALITY CONTROL

A. Testing Requirements: Factory test sound-power-level ratings according to ARI 270.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Install units level and plumb, firmly anchored in locations indicated; maintain manufacturer's recommended clearances.

B. Equipment Mounting:

Retain first subparagraph below to require equipment to be installed on cast-in-place concrete equipment bases.

1. Install air-cooled condenser refrigerant condensers on cast-in-place concrete equipment bases. Comply with requirements for equipment bases and foundations specified in [Section 033000 "Cast-in-Place Concrete."] [Section 033053 "Miscellaneous Cast-in-Place Concrete."]

Retain one of two subparagraphs below. Retain first for projects in seismic areas; retain second for projects not in seismic areas. Indicate vibration isolation and seismic-control device type and minimum deflection in supported equipment schedule on Drawings.

2. Comply with requirements for vibration isolation and seismic control devices specified in Section 230548 "Vibration and Seismic Controls for HVAC."

3. Comply with requirements for vibration isolation devices specified in Section 230548.13 "Vibration Controls for HVAC."

C. Maintain manufacturer's recommended clearances for service and maintenance.

D. Loose Components: Install electrical components, devices, and accessories that are not factory mounted.

3.2 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Piping installation requirements are specified in Section 232113 "Hydronic Piping" and Section 232116 "Hydronic Piping Specialties."Section 15179 "Hydronic Piping Specialties." Drawings indicate general arrangement of piping, fittings, and specialties.

B. Install piping adjacent to machine to allow service and maintenance.

C. Refrigerant Piping: Connect piping to unit with pressure relief, service valve, filter-dryer, and moisture indicator on each refrigerant-circuit liquid line. Refrigerant piping and specialties are specified in Section 232300 "Refrigerant Piping."

3.3 FIELD QUALITY CONTROL

A. Perform tests and inspections.

B. Tests and Inspections:

1. Perform electrical test and visual and mechanical inspection.

2. Leak Test: After installation, charge system and test for leaks. Repair leaks and retest until no leaks exist.

3. Operational Test: After electrical circuitry has been energized, start units to confirm proper motor rotation and unit operation. Complete manufacturer's starting checklist.

4. Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.

5. Verify proper airflow over coils.

C. Verify that vibration isolation and flexible connections properly dampen vibration transmission to structure.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

D. Air-cooled refrigerant condensers will be considered defective if they do not pass tests and inspections.

E. Prepare test and inspection reports.

END OF SECTION 236313

	AIR-COOLED REFRIGERANT CONDENSERS
	236313 - 1



