Copyright 2012 AIA
MasterSpec Professional
03/12

Copyright 2012 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 236333 - EVAPORATIVE REFRIGERANT CONDENSERS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes: Factory-assembled and -tested, [forced] [induced]-draft evaporative refrigerant condensers.

1.2 PERFORMANCE REQUIREMENTS

Retain first paragraph below if Contractor is required to assume responsibility for design.

A. Delegated Design: Design evaporative refrigerant condenser support structure[ and seismic restraints] [ and wind restraints], including comprehensive engineering analysis by a qualified professional engineer, using performance requirements and design criteria indicated.

Retain first paragraph below if Contractor is to design structural supports for evaporative refrigerant condensers. Delete if these supports are part of the structural design and are indicated on Drawings.

B. Structural Performance: Evaporative refrigerant condenser support structure shall withstand the effects of gravity loads and the following loads and stresses within limits and under conditions indicated according to [ASCE/SEI 7] <Insert requirement>.

Consult a structural engineer experienced in engineering evaporative refrigerant condenser structural supports and seismic and wind restraints of type indicated to quantify design loads applicable to Project. Verify compliance with codes. See Evaluations.

Retain subparagraphs below if design loads and load combinations are not indicated on Drawings.

1. Dead Loads: <Insert loads>.

2. Live Loads: <Insert loads>.

3. Roof Loads: <Insert loads>.

4. Snow Loads: <Insert loads>.

5. Seismic Loads: <Insert loads>.

6. Wind Loads: <Insert loads>.

7. <Insert loads or load combinations>.

8. Deflection Limits: Design system to withstand design loads without deflections greater than the following:

a. <Insert deflection limits>.

Retain first paragraph below with "Delegated-Design Submittal" Paragraph in "Action Submittals" Article for projects requiring wind-restraint design. Model building codes and ASCE/SEI 7 establish criteria for wind loads. Verify requirements of authorities having jurisdiction.

C. Wind-Restraint Performance:

Obtain values for items in subparagraphs below from Project structural engineer or from ASCE/SEI 7.

1. Basic Wind Speed: <Insert value>.

2. Building Classification Category: [I] [II] [III] [IV].

3. Minimum 10 lb/sq. ft. (48.8 kg/sq. m) multiplied by the maximum area of the mechanical component projected on a vertical plane that is normal to the wind direction, and 45 degrees either side of normal.

Retain paragraph below with "Seismic Qualification Certificates" Paragraph in "Informational Submittals" Article for projects requiring seismic design. Model building codes and ASCE/SEI 7 establish criteria for buildings subject to earthquake motions. Verify requirements of authorities having jurisdiction.

D. Seismic Performance: Evaporative refrigerant condenser shall withstand the effects of earthquake motions determined according to [ASCE/SEI 7] <Insert requirement>.

Retain subparagraph below to define the term "withstand" as it applies to this Project. Definition varies with type of building and occupancy and is critical to valid certification. Option is used for essential facilities where equipment must operate immediately after an earthquake.

1. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified[ and the unit will be fully operational after the seismic event]."

1.3 ACTION SUBMITTALS

A. Product Data: For each type of product indicated. Include rated capacities, pressure drop, fan performance data, installation instructions, furnished specialties, and accessories.

B. LEED Submittals:

Coordinate "Product Data for Credit EA 4" Subparagraph below with requirements for refrigerants.

1. Product Data for Credit EA 4: Documentation indicating that equipment and refrigerants comply.

C. Shop Drawings: For evaporative refrigerant condensers. Include plans, elevations, sections, details, and attachments to other work.

1. Detail equipment assemblies and indicate dimensions, required clearances, method of field assembly, components, and location and size of each field piping and wiring connection.

2. Wiring Diagrams: Power, signal, and control wiring.

Paragraph below is defined in Section 013300 "Submittal Procedures" as a "Delegated-Design Submittal." Retain if Work of this Section is required to withstand specific design loads and design responsibilities have been delegated to Contractor or if structural data are required as another way to verify compliance with performance requirements. Professional engineer qualifications are specified in Section 014000 "Quality Requirements."

D. Delegated-Design Submittal: For evaporative refrigerant condensers indicated to comply with performance requirements and design criteria, including analysis data signed and sealed by the qualified professional engineer responsible for their preparation.

1. Detail mounting, securing, and flashing of roof curb to roof structure. Indicate coordinating requirements with roof membrane system.

2. [Wind-] [and] [Seismic-]Restraint Details: Detail fabrication and attachment of restraints and snubbers. Show anchorage details and indicate quantity, diameter, and depth of penetration of anchors.

3. Vibration Isolation Base Details: Detail fabrication including anchorages and attachments to structure and to supported equipment. Include handrails, ladders, and equipment mounting frame.

4. Design Calculations: Calculate requirements for selecting vibration isolators [and seismic restraints] and for designing vibration isolation bases.

1.4 INFORMATIONAL SUBMITTALS

Retain first paragraph below if required by seismic criteria applicable to Project. Coordinate with Section 230548 "Vibration and Seismic Controls for HVAC." See ASCE/SEI 7 for certification requirements for equipment and components.

A. Seismic Qualification Certificates: For evaporative refrigerant condensers, accessories, and components, from manufacturer.

B. Warranties.

1.5 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

1.6 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

Retain first paragraph below if Owner prefers the security of a coil designed and fabricated according to ASME Boiler and Pressure Vessel Code or where required by state or local codes.

B. ASME Compliance: Fabricate and label heat-exchanger coils to comply with ASME Boiler and Pressure Vessel Code: Section VIII, Division 1.

C. Comply with NFPA 70.

Retain "ASHRAE/IESNA 90.1 Compliance" Paragraph below to require compliance with ASHRAE/IESNA 90.1. LEED Prerequisite EA 2 requires compliance with ASHRAE/IESNA 90.1.

D. ASHRAE/IESNA 90.1 Compliance: Applicable requirements in ASHRAE/IESNA 90.1, Section 6 - "Heating, Ventilating, and Air-Conditioning" and Section 10 - "Other Equipment."

1.7 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this article are not less than remedies available to Owner under prevailing local laws.

A. Special Warranty: Manufacturer's standard form in which manufacturer agrees to repair or replace components of evaporative refrigerant condensers that fail in materials or workmanship within specified warranty period.

1. Failures include, but are not limited to, the following:

a. Fan, motor, drive shaft, bearings, and motor supports.

b. Tube bundle.

c. External-circuit circulating pump.

d. <Insert failure modes>.

Verify available warranties and warranty periods for units and components with manufacturers listed in Part 2 articles.

2. Warranty Period: [Five] <Insert number> years from date of Substantial Completion.

PART 2 -  PRODUCTS

2.1 FORCED-DRAFT EVAPORATIVE REFRIGERANT CONDENSERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. Retain one of first two paragraphs below. See Section 016000 "Product Requirements."

A. Products: Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

1. Baltimore Aircoil Company.

2. EVAPCO, Inc.

3. Recold.

4. <Insert manufacturer's name; product name or designation>.

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Baltimore Aircoil Company.

2. EVAPCO, Inc.

3. Recold.

4. <Insert manufacturer's name>.

Retain first paragraph below with "Seismic Qualification Certificates" paragraph in "Informational Submittals" Article for projects in seismic areas.

C. Fabricate evaporative refrigerant condenser mounting base with reinforcement strong enough to resist evaporative refrigerant condenser movement during a seismic event when evaporative refrigerant condenser is anchored to field support structure.

D. Evaporative refrigerant condenser designed to resist wind load of [30 lbf/sq. ft. (1.44 kPa)] <Insert value>.

E. Casing and Frame:

1. Casing[ and Frame] Material: [FRP with UV inhibitors] [Galvanized steel, ASTM A 653/A 653M, G210 (Z600) coating] [Galvanized steel, ASTM A 653/A 653M, G235 (Z700) coating] [Polymer-coated galvanized steel] [Stainless steel].

2. Fasteners: [Galvanized] [Stainless] steel.

3. Joints and Seams: Sealed watertight.

4. Welded Connections: Continuous and watertight.

F. Collection Basin:

1. Material: [FRP with UV inhibitors] [Galvanized steel, ASTM A 653/A 653M, G210 (Z600) coating] [Galvanized steel, ASTM A 653/A 653M, G235 (Z700) coating] [Polymer-coated galvanized steel] [Stainless steel].

2. Strainer: Removable[ stainless-steel] strainer with openings smaller than nozzle orifices.

3. Overflow and drain connections.

4. Makeup water connection.

G. Mechanically Operated, Collection Basin Water-Level Control: Manufacturer's standard adjustable, mechanical float assembly and valve.

H. Electric Basin Heater:

1. Stainless-Steel Electric Immersion Heaters: Installed in a threaded coupling on the side of the collection basin.

2. Heater Control Panel: Mounted on the side of each evaporative refrigerant condenser cell.

3. Enclosure: NEMA 250, [Type 3R] [Type 4] [Type 4X].

4. Magnetic contactors controlled by a temperature sensor/controller to maintain collection basin water-temperature set point. Water-level probe shall monitor evaporative refrigerant condenser water level and de-energize the heater when the water reaches low-level set point.

5. Control-circuit transformer with primary and secondary side fuses.

6. Terminal blocks with numbered and color-coded wiring to match wiring diagram.

7. Single-point, field-power connection to a [fused disconnect switch] [nonfused disconnect switch] [circuit breaker] and heater branch circuiting complying with NFPA 70.

8. Factory Wiring Method: Metal raceway for factory-installed wiring outside of enclosures, except make connections to each electric basin heater with liquidtight conduit.

I. Water Distribution Piping: Main header and lateral branch piping designed for even distribution over heat exchanger coil throughout the flow range without the need for balancing valves and for connecting individual, removable, nonclogging spray nozzles.

In first subparagraph below, PVC is manufacturer's most common standard offering. Other requirements may require use of other materials.

1. Pipe Material: [Fiberglass] [PVC] [Galvanized steel] <Insert material>.

2. Spray Nozzle Material: [Plastic] [Polypropylene] [PVC] <Insert material>.

3. Piping Supports: Corrosion-resistant hangers and supports designed to resist movement during operation and shipment.

J. Spray Pump: Close-coupled, end-suction, single-stage, bronze-fitted centrifugal pump; with suction strainer and flow balancing valve, and mechanical seal suitable for outdoor service.

Default motor characteristics are specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

1. General Requirements for Spray Pump Motor: Comply with NEMA designation and temperature-rating requirements specified in Section 230513 "Common Motor Requirements for HVAC Equipment" and not indicated below.

2. Motor Enclosure: Totally enclosed.

3. Energy Efficiency: [Comply with ASHRAE/IESNA 90.1] [NEMA Premium Efficient].

K. Heat-Exchanger Coils:

Some material options in first subparagraph below are limited to specific manufacturers. Consult manufacturers if Project requires specific materials.

1. Tube and Tube Sheet Materials: [Copper tube with stainless-steel sheet] [Stainless-steel tube and sheet] [Prime-coated steel tube and sheet with outer surface of tube and sheet hot-dip galvanized after fabrication].

Retain one of two subparagraphs below. Second subparagraph is only available with hot-dip galvanized steel tubes. Coordinate with subparagraph above and "Quality Assurance" Article.

2. Heat-Exchanger Arrangement: [Serpentine tubes] [Serpentine tubes with removable cover plate on inlet and outlet headers] [Straight tubes with removable header cover plate on both ends of heat exchanger for straight-through access to each tube]; and sloped for complete drainage of fluid by gravity.

3. ASME Compliance: Designed, manufactured, and tested according to ASME Boiler and Pressure Vessel Code: Section VIII, Division 1, and bearing ASME "U" stamp; and sloped for complete drainage of fluid by gravity.

L. [Removable ]Drift Eliminator:

1. Material: [FRP] [PVC] [FRP or PVC] <Insert material>; with maximum flame-spread index of [5] [25] <Insert value> according to ASTM E 84.

2. UV Treatment: Inhibitors to protect against damage caused by UV radiation.

3. Configuration: Multipass, designed and tested to reduce water carryover to achieve performance indicated.

Retain first paragraph below if screens are required.

M. [Removable ]Air-Intake Screens: [Galvanized] [Polymer-coated, galvanized] [Stainless]-steel wire mesh.

N. Centrifugal Fan: Double-width, double-inlet fan with forward-curved blades; and statically and dynamically balanced at the factory after assembly.

O. Belt Drive:

1. Service Factor: [1.5] <Insert value> based on motor nameplate horsepower.

2. Sheaves: Fan and motor shafts shall have taper-lock sheaves fabricated from corrosion-resistant materials.

Retain one of first two subparagraphs below. Second subparagraph provides better performance.

3. Belt: Multiple V-belt design with a matched set of[ cogged] belts.

4. Belt: One-piece, multigrooved, solid-back belt.

5. Belt Material: Oil resistant, nonstatic conducting, and constructed of neoprene polyester cord.

6. Belt-Drive Guard: Comply with OSHA regulations.

P. Fan Motor:

Default motor characteristics are specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

1. General Requirements for Fan Motors: Comply with NEMA designation and temperature-rating requirements specified in Section 230513 "Common Motor Requirements for HVAC Equipment" and not indicated below.

2. Motor Enclosure: Totally enclosed.

3. Energy Efficiency: [Comply with ASHRAE/IESNA 90.1] [NEMA Premium Efficient].

4. Variable-Speed Motors: Inverter-duty rated per NEMA MG-1, Section IV, "Performance Standard Applying to All Machines," Part 31, "Definite-Purpose, Inverter-Fed, Polyphase Motors."

Retain first paragraph below if evaporative refrigerant condenser requires a discharge hood. See Evaluations.

Q. Discharge Hoods:

1. Hood Configuration: [Tapered] [Straight]; totally surrounding drift eliminators and constructed of same material as casing; and having factory-installed access doors.

Retain subparagraph below if discharge dampers are required.

2. Discharge Dampers: Positive-closure, automatic, isolation dampers with electric actuators.

Retain subparagraph below if evaporative refrigerant condensers are not provided with factory-installed and -wired control package.

a. Provide field power and controls to open dampers when pump is energized and close dampers when pump is de-energized.

Retain first paragraph below if Project requires capacity-control dampers to improve leaving-water temperature control.

R. Capacity-Control Dampers: [Galvanized-steel] [Stainless-steel] <Insert material> dampers, with linkages, electric operator, controller, limit switches, transformer, and weatherproof enclosure.

Retain first paragraph below to require a vibration switch furnished with evaporative refrigerant condenser.

S. Vibration Switch: For each fan drive.

1. Enclosure: NEMA 250, [Type 4] [Type 4X] <Insert type>.

2. Provide switch with manual-reset button for hardwired connection to fan motor electrical circuit.

3. Switch shall, on sensing excessive vibration, shut down the fan.

Retain first paragraph below if controls are specified in Section 230900 "Instrumentation and Control for HVAC." Retain second paragraph if controls are provided with evaporative refrigerant condenser.

T. Controls: Comply with requirements in Section 230900 "Instrumentation and Control for HVAC."

Retain first paragraph below, based on Project conditions, to require evaporative refrigerant condenser to be equipped with factory-installed control package. Not all manufacturers offer factory-installed control packages; those that do offer control packages have limited features available with the package. Consult manufacturers for additional information.

U. Control Package: Factory installed and wired, and functionally tested at factory before shipment.

Fourteen subparagraphs below are optional features. Retain applicable subparagraphs, based on Project conditions, to require these features and to correspond with components retained in paragraphs above.

1. NEMA 250, [Type 3R] [Type 4] [Type 4X] enclosure with removable internally mounted backplate.

2. Control-circuit transformer with primary and secondary side fuses.

3. Terminal blocks with numbered and color-coded wiring to match wiring diagram. Spare wiring terminal block for connection to external controls or equipment.

4. Microprocessor-based controller for automatic control of fan and spray pump based on evaporative refrigerant condenser leaving-water temperature with control features to improve operating efficiency based on outdoor ambient wet-bulb temperature by using adaptive logic.

5. Fan motor sequencer for multiple-cell and two-speed applications with automatic lead-stage rotation.

6. Electric basin heaters with temperature control and low-water-level safety switch for each cell, complying with requirements in "Electric Basin Heater" Paragraph.

7. Vibration switch for each fan, complying with requirements in "Vibration Switch" Paragraph.

8. Controls and wiring for "two-motor, single-fan drives" shall be same as two-speed, two-winding motor.

9. Power and controls to open discharge hood dampers when pump is energized and close dampers when pump is de-energized.

10. Single-point, field-power connection to a [fused disconnect switch] [nonfused disconnect switch] [circuit breaker] [for each evaporative refrigerant condenser cell].

a. Branch power circuit to each motor and electric basin heater and to controls with a disconnect switch or circuit breaker.

b. NEMA-rated motor controller, hand-off-auto switch, and overcurrent protection for each motor. Provide variable frequency controller with manual bypass and line reactors for each variable-speed motor indicated.

11. Factory-installed wiring outside of enclosures shall be in metal raceway, except make connections to each motor and electric basin heater with liquidtight conduit.

12. Visual indication of status and alarm for each motor.

Retain first subparagraph below for audible alarm. Coordinate with control sequence.

13. Audible alarm and silence switch.

14. Visual indication of elapsed run time, graduated in hours for each motor.

V. Personnel Access Components:

Four subparagraphs below are optional components. Retain applicable subparagraphs, based on Project conditions, to require these components.

1. Doors: Large enough for personnel to access evaporative refrigerant condenser internal components from evaporative refrigerant condenser end walls.

2. External Ladders with Safety Cages: Aluminum, galvanized- or stainless-steel, fixed ladders with ladder extensions to access external platforms and top of evaporative refrigerant condenser from adjacent grade without the need for portable ladders. Comply with 29 CFR 1910.27.

3. External Platforms with Handrails: Aluminum, FRP, or galvanized-steel bar grating at evaporative refrigerant condenser access doors when evaporative refrigerant condensers are elevated and not accessible from grade.

4. Handrail: Aluminum, galvanized steel, or stainless steel complete with kneerail and toeboard at platforms and around top of evaporative refrigerant condenser. Comply with 29 CFR 1910.23.

If Project has more than one type or configuration of evaporative refrigerant condenser, delete paragraph below and schedule evaporative refrigerant condensers on Drawings.

W. Capacities and Characteristics:

1. Number of Cells: <Insert quantity>.

2. Maximum Drift Loss: [0.005] <Insert number> percent of design water flow.

3. Heat-Exchanger Coil(s):

Retain one of first two subparagraphs below to require a specific refrigerant type; delete both if any refrigerant type is acceptable. Retain second, third, or fourth option in first subparagraph or retain second subparagraph if required for LEED-NC, LEED-CS, and LEED for Schools Credit EA 4.

a. Refrigerant Type: [R-22] [R-407C] [R-410A] [HFC-134a] <Insert type>.

b. Refrigerant Type: R-407C, R-410A, or HFC-134a.

c. Minimum Heat Rejection: <Insert Btu/h (kW)>.

d. Condensing Temperature: <Insert deg F (deg C)>.

e. Entering-Air Wet-Bulb Temperature: <Insert deg F (deg C)>.

4. Fan Location: [Bottom] [Side].

5. Fan Motor:

a. Type: [Single speed] [Two speed, single winding] [Two speed, two winding] [Variable speed].

b. Horsepower/Cell: <Insert horsepower>.

c. Full-Load Ampacity: <Insert value>.

d. Minimum Circuit Ampacity: <Insert value>.

e. Maximum Overcurrent Protection Device: <Insert amperage>.

f. Electrical Characteristics: [208] [240] [480] <Insert value>-V ac, 3 phase, 60 Hz.

6. Spray Pump and Motor:

a. Water Flow/Cell: <Insert gpm (L/s)>.

b. Horsepower/Cell: <Insert horsepower>.

c. Full-Load Ampacity: <Insert value>.

d. Minimum Circuit Ampacity: <Insert value>.

e. Maximum Overcurrent Protection Device: <Insert amperage>.

f. Electrical Characteristics: [120] [208] [240] [277] [480] <Insert value>-V ac, [single] [3] phase, 60 Hz.

7. Sound Pressure Level: <Insert dBA> at <Insert distance in feet (m)> [when measured according to CTI ATC 128].

Retain subparagraph below for projects with basin heaters.

8. Basin Heater:

a. Basin Water Temperature: [40 deg F (5 deg C)] <Insert value>.

b. Outdoor Ambient Temperature: [0 deg F (Minus 18 deg C)] [Minus 20 deg F (Minus 29 deg C)] <Insert value>.

c. Capacity/Cell: <Insert kilowatts>.

d. Full-Load Ampacity: <Insert value>.

e. Minimum Circuit Ampacity: <Insert value>.

f. Maximum Overcurrent Protection Device: <Insert amperage>.

g. Electrical Characteristics: [208] [240] [480] <Insert value>-V ac, 3 phase, 60 Hz.

2.2 INDUCED-DRAFT EVAPORATIVE REFRIGERANT CONDENSERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. Retain one of first two paragraphs below. See Section 016000 "Product Requirements."

A. Products: Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

1. Baltimore Aircoil Company; Series CXV.

2. EVAPCO, Inc; Models ATC.

3. Recold; Series MC.

4. <Insert manufacturer's name; product name or designation>.

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Baltimore Aircoil Company.

2. EVAPCO, Inc.

3. Recold.

4. <Insert manufacturer's name>.

Retain first paragraph below with "Seismic Qualification Certificates" paragraph in "Informational Submittals" Article for projects in seismic areas.

C. Fabricate evaporative refrigerant condenser mounting base with reinforcement strong enough to resist evaporative refrigerant condenser movement during a seismic event when evaporative refrigerant condenser is anchored to field support structure.

D. Evaporative refrigerant condenser designed to resist wind load of [30 lbf/sq. ft. (1.44 kPa)] <Insert value>.

E. Casing and Frame:

1. Casing and Frame Material: [FRP with UV inhibitors] [Galvanized steel, ASTM A 653/A 653M, G210 (Z600) coating] [Galvanized steel, ASTM A 653/A 653M, G235 (Z700) coating] [Stainless steel].

2. Fasteners: [Galvanized] [Stainless] steel.

3. Joints and Seams: Sealed watertight.

4. Welded Connections: Continuous and watertight.

F. Collection Basin:

1. Material: [Galvanized steel, ASTM A 653/A 653M, G210 (Z600) coating] [Galvanized steel, ASTM A 653/A 653M, G235 (Z700) coating] [Stainless steel].

2. Overflow and drain connections.

3. Makeup water connection.

G. Mechanically Operated, Collection Basin Water-Level Control: Manufacturer's standard adjustable, mechanical float assembly and valve.

Retain first paragraph below to require basin heaters for projects subject to freezing conditions. See Evaluations.

H. Electric Basin Heater:

1. Stainless-Steel Electric Immersion Heaters: Installed in a threaded coupling on the side of the collection basin.

2. Heater Control Panel: Mounted on the side of each evaporative refrigerant condenser cell.

3. Enclosure: NEMA 250, [Type 3R] [Type 4] [Type 4X].

4. Magnetic contactors controlled by a temperature sensor/controller to maintain collection basin water-temperature set point. Water-level probe shall monitor evaporative refrigerant condenser water level and de-energize the heater when the water reaches low-level set point.

5. Control-circuit transformer with primary and secondary side fuses.

6. Terminal blocks with numbered and color-coded wiring to match wiring diagram.

7. Single-point, field-power connection to a [fused disconnect switch] [nonfused disconnect switch] [circuit breaker] and heater branch circuiting complying with NFPA 70.

8. Factory Wiring Method: Metal raceway for factory-installed wiring outside of enclosures, except make connections to each electric basin heater with liquidtight conduit.

I. Pressurized Water Distribution Piping: Main header and lateral branch piping designed for even distribution over heat-exchanger coil throughout the flow range without the need for balancing valves and for connecting individual, removable, nonclogging spray nozzles.

In first subparagraph below, PVC is manufacturer's most common standard offering. Other requirements may require use of other materials.

1. Pipe Material: [Fiberglass] [PVC] [Galvanized steel] <Insert material>.

2. Spray Nozzle Material: [Plastic] [Polypropylene] [PVC] <Insert material>.

3. Piping Supports: Corrosion-resistant hangers and supports to resist movement during operation and shipment.

J. Recirculating Piping: PVC.

K. Spray Pump: Close-coupled, end-suction, single-stage, bronze-fitted centrifugal pump; with suction strainer and flow balancing valve, and mechanical seal suitable for outdoor service.

Default motor characteristics are specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

1. General Requirements for Spray Pump Motor: Comply with NEMA designation and temperature-rating requirements specified in Section 230513 "Common Motor Requirements for HVAC Equipment" and not indicated below.

2. Motor Enclosure: Totally enclosed.

3. Energy Efficiency: [Comply with ASHRAE/IESNA 90.1] [NEMA Premium Efficient].

L. Heat-Exchanger Coils:

Some material options in first subparagraph below are limited to specific manufacturers. Consult manufacturers if Project requires specific materials.

1. Tube and Tube Sheet Materials: [Copper tube with stainless-steel sheet] [Stainless-steel tube and sheet] [Prime-coated steel tube and sheet with outer surface of tube and sheet hot-dip galvanized after fabrication].

Retain one of two subparagraphs below. Second subparagraph is only available with hot-dip galvanized-steel tubes. Coordinate with subparagraph above and "Quality Assurance" Article.

2. Heat-Exchanger Arrangement: [Serpentine tubes] [Serpentine tubes with removable cover plate on inlet and outlet headers] [Straight tubes with removable header cover plate on both ends of heat exchanger for straight-through access to each tube]; and sloped for complete drainage of fluid by gravity.

3. ASME Compliance: Designed, manufactured, and tested according to ASME Boiler and Pressure Vessel Code: Section VIII, Division 1, and bearing ASME "U" stamp; and sloped for complete drainage of fluid by gravity.

Retain option in first paragraph below to limit placement of drift eliminators.

M. [Removable ]Drift Eliminator:

1. Material: [FRP] [PVC] [FRP or PVC] <Insert material>; with maximum flame-spread index of [5] [25] <Insert value> according to ASTM E 84.

2. Configuration: Multipass, designed and tested to reduce water carryover to achieve performance indicated.

N. Air-Intake Louvers:

1. Material: [FRP] [PVC] [Matching casing].

2. Louver Blades: Arranged to uniformly direct air into evaporative refrigerant condenser, to minimize air resistance, and to prevent water from splashing out during all modes of operation including operation with fans off.

O. Axial Fan: Balanced at the factory after assembly.

1. Blade Material: [Aluminum] [FRP] [Galvanized steel].

2. Hub Material: Aluminum.

First subparagraph below is an optional feature. Retain, based on Project conditions, to require feature.

3. Blade Pitch: Field adjustable.

4. Protective Enclosure: Removable, galvanized-steel, wire-mesh screens complying with OSHA regulations.

5. Fan Shaft Bearings: Self-aligning, grease-lubricated ball or roller bearings with moisture-proof seals and premium, moisture-resistant grease suitable for temperatures between minus 20 and plus 300 deg F (minus 29 and plus 149 deg C). Bearings designed for an L-10 life of [40,000] [50,000] <Insert value> hours.

6. Bearings Grease Fittings: Extended lubrication lines to an easily accessible location.

P. Belt Drive:

1. Service Factor: [1.5] <Insert value> based on motor nameplate horsepower.

2. Sheaves: Fan and motor shafts shall have taper-lock sheaves fabricated from corrosion-resistant materials.

Retain one of first two subparagraphs below. Second subparagraph provides better performance.

3. Belt: Multiple V-belt design with a matched set of[ cogged] belts.

4. Belt: One-piece, multigrooved, solid-back belt.

5. Belt Material: Oil resistant, nonstatic conducting, and constructed of neoprene polyester cord.

6. Belt-Drive Guard: Comply with OSHA regulations.

Q. Fan Motor:

Default motor characteristics are specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

1. General Requirements for Fan Motors: Comply with NEMA designation and temperature-rating requirements specified in Section 230513 "Common Motor Requirements for HVAC Equipment" and not indicated below.

2. Motor Enclosure: Totally enclosed.

3. Energy Efficiency: [Comply with ASHRAE/IESNA 90.1] [NEMA Premium Efficient].

4. Variable-Speed Motors: Inverter-duty rated per NEMA MG-1, Section IV, "Performance Standard Applying to All Machines," Part 31, "Definite-Purpose, Inverter-Fed, Polyphase Motors."

Retain subparagraph below for belt-drive units.

5. Motor Base: Adjustable, or other suitable provision for adjusting belt tension.

R. Fan Discharge Stack: Material shall match casing.

Retain first subparagraph below if Project requires a minimum stack height to clear an obstruction.

1. Stack Extension: Fabricated to extend above fan deck <Insert distance> unless otherwise indicated.

2. Stack Termination: Wire-mesh, galvanized-steel screens; complying with OSHA regulations.

Retain first paragraph below to require a vibration switch furnished with evaporative refrigerant condenser.

S. Vibration Switch: For each fan drive.

1. Enclosure: NEMA 250, [Type 4] [Type 4X] <Insert type>.

2. Provide switch with manual-reset button for hardwired connection to fan motor electrical circuit.

3. Switch shall, on sensing excessive vibration, shut down the fan.

Retain first paragraph below if controls are specified in Section 230900 "Instrumentation and Control for HVAC." Retain second paragraph if controls are provided with evaporative refrigerant condenser.

T. Controls: Comply with requirements in Section 230900 "Instrumentation and Control for HVAC."

Retain first paragraph below, based on Project conditions, to require evaporative refrigerant condenser to be equipped with factory-installed control package. Not all manufacturers offer factory-installed control packages; those that do offer control packages have limited features available with the package. Consult manufacturers for additional information.

U. Control Package: Factory installed and wired, and functionally tested at factory before shipment.

Twelve subparagraphs below are optional features. Retain applicable subparagraphs, based on Project conditions, to require these features and to correspond with components retained in paragraphs above.

1. NEMA 250, [Type 3R] [Type 4] [Type 4X] enclosure with removable internally mount backplate.

2. Control-circuit transformer with primary and secondary side fuses.

3. Terminal blocks with numbered and color-coded wiring to match wiring diagram. Spare wiring terminal block for connection to external controls or equipment.

4. Microprocessor-based controller for automatic control of fan and spray pump based on evaporative refrigerant condenser leaving-water temperature with control features to improve operating efficiency based on outdoor ambient wet-bulb temperature by using adaptive logic.

5. Fan motor sequencer for multiple-cell and two-speed applications with automatic lead-stage rotation.

6. Electric basin heaters with temperature control and low-water-level safety switch for each cell, complying with requirements in "Electric Basin Heater" Paragraph.

7. Vibration switch for each fan, complying with requirements in "Vibration Switch" Paragraph.

8. Single-point, field-power connection to a fused disconnect switch.

9. Factory-installed wiring outside of enclosures shall be in metal raceway, except make connections to each motor and electric basin heater with liquidtight conduit.

10. Visual indication of status and alarm for each motor.

Retain first subparagraph below for audible alarm. Coordinate with control sequence.

11. Audible alarm and silence switch.

12. Visual indication of elapsed run time, graduated in hours for each motor.

V. Personnel Access Components:

Four subparagraphs below are optional components. Retain applicable subparagraphs, based on Project conditions, to require these components.

1. Doors: Large enough for personnel to access evaporative refrigerant condenser internal components from both evaporative refrigerant condenser end walls. Doors shall be operable from both sides of the door.

2. External Ladders with Safety Cages: Aluminum, galvanized- or stainless-steel, fixed ladders with ladder extensions to access external platforms and top of evaporative refrigerant condenser from adjacent grade without the need for portable ladders. Comply with 29 CFR 1910.27.

3. External Platforms with Handrails: Aluminum, FRP, or galvanized-steel bar grating at evaporative refrigerant condenser access doors when evaporative refrigerant condensers are elevated and not accessible from grade.

4. Handrail: Aluminum, galvanized steel, or stainless steel, complete with kneerail and toeboard at platforms, and around top of evaporative refrigerant condenser. Comply with 29 CFR 1910.23.

If Project has more than one type or configuration of evaporative refrigerant condenser, delete paragraph below and schedule evaporative refrigerant condensers on Drawings.

W. Capacities and Characteristics:

1. Number of Cells: <Insert quantity>.

2. Maximum Drift Loss: [0.005] <Insert number> percent of design water flow.

3. Heat-Exchanger Coil:

Retain one of first two subparagraphs below to require a specific refrigerant type; delete both if any refrigerant type is acceptable. Retain second, third, or fourth option in first subparagraph or retain second subparagraph if required for LEED-NC, LEED-CS, and LEED for Schools Credit EA 4.

a. Refrigerant Type: [R-22] [R-407C] [R-410A] [HFC-134a] <Insert type>.

b. Refrigerant Type: R-407C, R-410A, or HFC-134a.

c. Minimum Heat Rejection: <Insert Btu/h (kW)>.

d. Condensing Temperature: <Insert deg F (deg C)>.

e. Entering-Air Wet-Bulb Temperature: <Insert deg F (deg C)>.

4. Fan Motor:

a. Type: [Single speed] [Two speed, single winding] [Two speed, two winding] [Variable speed].

b. Horsepower/Cell: <Insert horsepower>.

c. Full-Load Ampacity: <Insert value>.

d. Minimum Circuit Ampacity: <Insert value>.

e. Maximum Overcurrent Protection Device: <Insert amperage>.

f. Electrical Characteristics: [208] [240] [480] <Insert value>-V ac, 3 phase, 60 Hz.

5. Spray Pump and Motor:

a. Water Flow/Cell: <Insert gpm (L/s)>.

b. Horsepower/Cell: <Insert horsepower>.

c. Full-Load Ampacity: <Insert value>.

d. Minimum Circuit Ampacity: <Insert value>.

e. Maximum Overcurrent Protection Device: <Insert amperage>.

f. Electrical Characteristics: [120] [208] [240] [277] [480] <Insert value>-V ac, [single] [3] phase, 60 Hz.

6. Sound Pressure Level: <Insert dBA> at <Insert distance in feet (m)> [when measured according to CTI ATC 128].

Retain subparagraph below for projects with basin heaters.

7. Basin Heater:

a. Basin Water Temperature: [40 deg F (5 deg C)] <Insert value>.

b. Outdoor Ambient Temperature: [0 deg F (Minus 18 deg C)] [Minus 20 deg F (Minus 29 deg C)] <Insert value>.

c. Capacity/Cell: <Insert kilowatts>.

d. Full-Load Ampacity: <Insert value>.

e. Minimum Circuit Ampacity: <Insert value>.

f. Maximum Overcurrent Protection Device: <Insert amperage>.

g. Electrical Characteristics: [208] [240] [480] <Insert value>-V ac, 3 phase, 60 Hz.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Equipment Mounting:

Retain first subparagraph below to require equipment to be installed on cast-in-place concrete equipment bases.

1. Install evaporative refrigerant condensers on cast-in-place concrete equipment bases. Comply with requirements for equipment bases and foundations specified in [Section 033000 "Cast-in-Place Concrete."] [Section 033053 "Miscellaneous Cast-in-Place Concrete."]

Retain one of two subparagraphs below. Retain first for projects in seismic areas; retain second for projects not in seismic areas. Indicate vibration isolation and seismic-control device type and minimum deflection in supported equipment schedule on Drawings.

2. Comply with requirements for vibration isolation and seismic control devices specified in Section 230548 "Vibration and Seismic Controls for HVAC."

3. Comply with requirements for vibration isolation devices specified in Section 230548.13 "Vibration Controls for HVAC."

B. Maintain manufacturer's recommended clearances for service and maintenance.

C. Loose Equipment: Install electrical components, devices, and accessories that are not factory mounted.

D. Install piping adjacent to evaporative refrigerant condensers to allow service and maintenance.

E. Install flexible pipe connectors at final connection of evaporative refrigerant condensers mounted on vibration isolators.

F. Run overflow, drain, and bleed lines to sanitary sewage system.

G. Domestic Water Piping: Comply with requirements in Section 221116 "Domestic Water Piping." Connect to water-level control with shutoff valve and union or flange at each connection.

H. Refrigerant Piping: Comply with requirements in Section 232300 "Refrigerant Piping." Connect to evaporative refrigerant condenser coil with isolation valves at each connection.

Retain paragraph below if evaporative refrigerant condenser is installed indoors.

I. Ducts: Comply with requirements in Section 233113 "Metal Ducts." Connect ducts to evaporative refrigerant condenser inlet and outlet, full size of outlet, with flexible duct connection.

3.2 STARTUP SERVICE

A. Inspect field-assembled components, equipment installation, and piping and electrical connections for proper assemblies, installations, and connections.

B. Obtain performance tables from manufacturer.

C. [Engage a factory-authorized service representative to perform] [Perform] startup service.

1. Complete installation and startup checks according to manufacturer's written instructions.

2. Clean entire unit including basins.

3. Verify that accessories are properly installed.

4. Check makeup water float.

5. Verify clearances for airflow and for evaporative refrigerant condenser servicing.

6. Check for vibration isolation and structural support.

7. Lubricate bearings on fans and shafts.

8. Verify fan wheel rotation for correct direction and for vibration or binding. Correct vibration and binding problems.

9. Adjust belts to proper alignment and tension.

Retain first subparagraph below for evaporative refrigerant condensers with variable-speed fans.

10. Operate variable-speed fans through entire operating range and check for harmonic vibration imbalance. Set motor controller to skip speeds resulting in abnormal vibration.

Retain first subparagraph below for evaporative refrigerant condensers with vibration switches.

11. Check vibration switch setting. Verify operation.

12. Verify water level in basin. Fill to proper startup level. Check makeup water-level control and valve.

13. Start external-circuit circulating pumps.

14. Verify operation of evaporative refrigerant condenser basin, makeup line, automatic freeze protect dump, and controlling device. Replace defective and malfunctioning units.

15. Verify operation of basin heater and control thermostat. Replace defective and malfunctioning units.

16. Verify that evaporative refrigerant condenser discharge is not recirculating into air intakes. Recommend corrective action.

17. Check HVAC water treatment system for proper operation, and measure chemical treatment levels. Verify operation of evaporative refrigerant condenser basin automatic blowdown and of controlling device.

3.3 ADJUSTING

A. Adjust water-level control for proper operating level.

3.4 DEMONSTRATION

A. [Engage a factory-authorized service representative to train] [Train] Owner's maintenance personnel to adjust, operate, and maintain evaporative refrigerant condensers.

END OF SECTION 236333

	EVAPORATIVE REFRIGERANT CONDENSERS
	236333 - 1



