Copyright 2012 AIA
MasterSpec Professional
03/12

Copyright 2012 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 236413.13 - DIRECT-FIRED ABSORPTION WATER CHILLERS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Packaged, water-cooled, direct-fired absorption chillers.

1.2 PERFORMANCE REQUIREMENTS

Retain first paragraph below with "Seismic Qualification Certificates" Paragraph in "Informational Submittals" Article for projects requiring seismic design. Model building codes and ASCE/SEI 7 establish criteria for buildings subject to earthquake motions. Verify requirements of authorities having jurisdiction.

A. Seismic Performance: Direct-fired absorption chillers shall withstand the effects of earthquake motions determined according to [ASCE/SEI 7] <Insert requirement>.

Retain subparagraph below to define the term "withstand" as it applies to this Project. Definition varies with type of building and occupancy and is critical to valid certification. Option is used for essential facilities where equipment must operate immediately after an earthquake.

1. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified[ and the unit will be fully operational after the seismic event]."

B. Condenser-Fluid Temperature Performance:

1. Startup Condenser-Fluid Temperature: Chiller shall be capable of starting with an entering condenser-fluid temperature of [60 deg F (16 deg C)] <Insert temperature> and providing stable operation until the system temperature is elevated to the minimum operating entering condenser-fluid temperature.

2. Minimum Operating Condenser-Fluid Temperature: Chiller shall be capable of continuous operation over the entire capacity range indicated with an entering condenser-fluid temperature of [70 deg F (21 deg C)] <Insert temperature>.

3. Make factory modifications to standard chiller design if necessary to comply with performance indicated.

C. Site Altitude: Chiller shall be suitable for altitude at which it is installed without affecting performance indicated. Make adjustments to affected chiller components to account for site altitude.

1.3 ACTION SUBMITTALS

A. Product Data: For each type of product indicated. Include rated capacities, operating characteristics, furnished specialties and accessories.

B. LEED Submittals:

1. Product Data for Prerequisite EA 2: Documentation indicating that units comply with applicable requirements in with ASHRAE/IESNA 90.1.

2. Product Data for Prerequisite EA 3: Documentation indicating that refrigerants comply.

Coordinate "Product Data for Credit EA 4" Subparagraph below with requirements for refrigerants.

3. Product Data for Credit EA 4: Documentation indicating that equipment and refrigerants comply.

C. Shop Drawings: Include plans, elevations, sections, details, and attachments to other work.

1.4 INFORMATIONAL SUBMITTALS

Retain first paragraph below if retaining certification in "Quality Assurance" Article.

A. Certificates: For certification required in "Quality Assurance" Article.

Some manufacturers will not provide certification specified in first paragraph below. Verify availability with manufacturers and retain below if required by seismic criteria applicable to Project. See "Seismic Considerations" Article in the Evaluations. Coordinate below with Section 230548 "Vibration and Seismic Controls for HVAC." See ASCE/SEI 7 for certification requirements for equipment and components.

B. Seismic Qualification Certificates: For chillers, accessories, and components, from manufacturer.

1. Basis for Certification: Indicate whether withstand certification is based on actual test of assembled components or on calculation.

2. Dimensioned Outline Drawings of Equipment Unit: Identify center of gravity and locate and describe mounting and anchorage provisions.

3. Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

C. Startup service reports.

D. Warranty.

1.5 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

1.6 QUALITY ASSURANCE

A. ARI Rating: Rate chiller performance according to requirements in ARI 560.

B. ASHRAE Compliance:

1. ASHRAE 15 for safety code for mechanical refrigeration.

"ASHRAE/IESNA 90.1" Subparagraph below may be required to comply with Project requirements or authorities having jurisdiction. LEED Prerequisite EA 2 requires compliance with requirements in ASHRAE/IESNA 90.1.

2. ASHRAE/IESNA 90.1.

C. ASME Compliance: Fabricate and label chiller pressure vessels to comply with applicable portions of ASME Boiler and Pressure Vessel Code.

D. Comply with NFPA 70.

E. Comply with requirements of UL and UL Canada, and include label by a qualified testing agency showing compliance.

Retain subparagraph below if required by authorities having jurisdiction. Retain second option for combination burners.

1. UL Compliance: [UL 726, "Oil-Fired Boiler Assemblies."] [UL 726, "Oil-Fired Boiler Assemblies"; and UL 795, "Commercial-Industrial Gas Heating Equipment."] [UL 795, "Commercial-Industrial Gas Heating Equipment."]

1.7 WARRANTY

A. Special Warranty: Manufacturer's standard form in which manufacturer agrees to repair or replace components of chillers that fail in materials or workmanship within specified warranty period.

Consult Owner about need for extended warranties.

1. Extended warranties include, but are not limited to, the following:

Retain one of first three subparagraphs below.

a. Complete chiller.

b. [Pumps and motors] [Purge unit] [Burner assembly] <Insert components>.

c. [Absorbent] [Absorbent and refrigerant] only.

d. Parts [only] [and labor].

e. Loss of absorbent and refrigerant for any reason.

Verify available warranties and warranty periods with manufacturers listed in Part 2 article.

2. Warranty Period: [Two] [Three] [Four] [Five] <Insert number> years from date of Substantial Completion.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of two paragraphs and list of manufacturers in this article. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Trane; a division of American Standard.

2. YORK; a Johnson Controls company.

3. <Insert manufacturer's name>.

2.2 MANUFACTURED UNIT

A. Description: Factory-assembled and -tested, hermetic-design chiller complete with absorber, evaporator, condenser, generator, solution heat exchanger, controls, absorbent solution pump with motor, refrigerant pump with motor, purge unit with motor, burner assembly, motor controllers, rupture disk, interconnecting unit piping and wiring, indicated accessories, and mounting frame.

Retain subparagraph below if limited space is available for installation.

1. Disassemble chiller into major assemblies, as required by the installation, after factory testing and before packaging for shipment.

B. Absorbent and Refrigerant:

1. Absorbent: Lithium bromide solution with corrosion inhibitor.

2. Refrigerant: Deionized [or distilled ]water.

3. Performance Enhancer: Heat and mass transfer enhancer to improve performance.

Retain paragraph below for projects in seismic areas. If retaining, also retain "Seismic Performance" Paragraph in "Performance Requirements" Article and "Seismic Qualification Certificates" Paragraph in "Informational Submittals" Article.

C. Seismic Fabrication Requirements: Fabricate mounting base and attachment to chiller, accessories, and components with reinforcement strong enough to withstand seismic forces defined in Section 230548 "Vibration and Seismic Controls for HVAC" when mounting base is anchored to building structure.

2.3 PUMPS

A. Hermetically sealed, self-lubricating, and fitted with self-adjusting, spring-loaded, wear-compensating, tapered carbon bearings.

B. Pump motor assembly shall be designed to operate for not less than 50,000 hours between inspections.

C. Pump motors shall be cooled and bearings lubricated, either by fluid being pumped or by a filtered supply of liquid refrigerant.

D. Pump suction and discharge shall be equipped with isolation valves.

E. Absorbent solution and refrigerant shall have separate and dedicated pumps.

1. Absorbent solution and refrigerant flow-control method shall be manufacturer's choice to comply with operating requirements indicated.

F. Purge System: Unit mounted and factory wired, equipped with controls and a pump to automatically remove noncondensable vapors.

Default motor characteristics are specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

1. Purge Pump Motor: Comply with NEMA designation, temperature rating, service factor, and efficiency requirements for motors specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

Retain first or third option in subparagraph below to restrict enclosure type; retain all three options to allow Contractor the choice. If retaining first or third option, verify availability of enclosure types with manufacturer.

a. Enclosure: [Open dripproof] [or] [totally enclosed].

2.4 HEAT-EXCHANGER Shells

A. Configuration: Two shells; one shell consists of the absorber/evaporator, low-stage generator/condenser and the other shell consists of the high-stage generator. Where indicated, equip chiller with a dedicated hot-water heat exchanger.

B. Construction: Fabricated from continuously welded carbon-steel sheet or plate, or from seamless pipe.

C. Design Pressure and Temperature Rating: Comply with applicable requirements in ASME Boiler and Pressure Vessel Code.

D. End Tube Sheets: Carbon-steel plates continuously welded to each end of shell; drilled and reamed to accommodate tubes, with positive seal between fluid in tubes and refrigerant in shell.

E. Intermediate Tube Sheets: Carbon-steel plates installed in shell and spaced along length of tube at intervals required to eliminate vibration and to avoid tube contact resulting in abrasion and wear.

F. Generator/Condenser Shell Pressure Relief Device: Manufacturer's standard rupture disk complying with requirements in ASHRAE 15 and in applicable portions of ASME Boiler and Pressure Vessel Code.

2.5 ABSORBER

A. Nozzle or Dispersion Trays: Designed to evenly distribute absorbent solution over tubes; constructed of brass, stainless steel, or another material that will not corrode.

B. Tubes:

1. Individually replaceable, straight tubes expanded into tube sheets. Replaceable from either end without damage to tube sheets and other tubes.

Tube materials for all heat exchangers can be independently selected; the choice can be different for each heat exchanger. Tube materials vary among manufacturers and chiller models; verify availability with manufacturer. First option in first subparagraph below is current standard of listed manufacturers.

Copper-nickel alloys available include 95/5 and 06/11. The higher nickel content in 06/11 provides better resistance to corrosion. If required by Project, insert specific alloy.

2. Material: [Copper] [or] [copper-nickel alloy] <Insert material>.

First option in first subparagraph below gives manufacturer the choice; other options limit thickness. Second option is current standard of listed manufacturers but is subject to change. Third and fourth options are upgrades. If using materials other than copper, wall thickness may vary. See Evaluations.

3. Minimum Wall Thickness: [Manufacturer's choice] [0.025 inch (0.6 mm)] [0.028 inch (0.7 mm)] [0.035 inch (0.9 mm)] <Insert dimension>.

4. External Finish: Manufacturer's standard.

First option in subparagraph below is standard of most manufacturers. Third option is for applications with dirty fluids that require frequent tube cleaning. Retain all three options to give manufacturer the choice.

5. Internal Finish: [Enhanced] [or] [smooth].

C. Water Boxes:

1. Carbon-steel construction; arranged to provide visual inspection and cleaning of tubes from either end without disturbing refrigerant in shell.

Retain one of first two subparagraphs below. If retaining first subparagraph, verify availability of marine-type water box with manufacturers.

2. [Standard] [Marine-type] water box with piping connections.

a. Water boxes [and marine-type water-box covers ]shall have lifting lugs or eyebolts.

Retain one of first two subparagraphs below for special applications.

b. [Hinged] [or] [davited] water boxes.

c. [Hinged] [or] [davited] marine-type water-box covers.

3. Standard water box without piping connections.

a. Water boxes shall have lifting lugs or eyebolts.

Retain first subparagraph below for special applications.

b. [Hinged] [or] [davited] water boxes.

4. Nozzle Pipe Connections: [Welded, ASME B16.5, flat-face flange] [Welded, ASME B16.5, raised-face flange] [Grooved for mechanical-joint coupling] [Grooved with mechanical-joint coupling and flange adapter].

5. Thermistor or RTD temperature sensor factory installed in each nozzle.

6. Fit each water box with [3/4-inch (19-mm)] [or] [1-inch (25-mm)] <Insert dimension> drain connection at low point and vent connection at high point, each with threaded plug.

Retain first paragraph below for special applications. Verify availability with manufacturers.

D. Additional Corrosion Protection:

1. Electrolytic corrosion-inhibitor anode.

Retain one of two subparagraphs below.

2. Coat wetted surfaces with a corrosion-resistant finish.

3. Using same material as tubes, clad surfaces of end tube sheets in contact with fluid. Coat other wetted surfaces, including water boxes, with a corrosion-resistant finish.

E. Absorber/Condenser Crossover Piping: Factory-furnished and -installed piping connecting fluid connection of absorber discharge to condenser inlet.

2.6 EVAPORATOR

A. Nozzle or Dispersion Trays: Designed to evenly distribute refrigerant over tubes; constructed of brass, stainless steel, or another material that will not corrode.

B. Refrigerant Holding Pan: Steel or stainless steel.

C. Tubes:

1. Individually replaceable, straight tubes expanded into tube sheets. Replaceable from either end without damage to tube sheets and other tubes.

Tube materials for all heat exchangers can be independently selected; the choice can be different for each heat exchanger. Tube materials vary among manufacturers and chiller models; verify availability with manufacturer. First option in first subparagraph below is current standard of listed manufacturers.

Copper-nickel alloys available include 95/5 and 06/11. The higher nickel content in 06/11 provides better resistance to corrosion. If required by Project, insert specific alloy.

2. Material: [Copper] [or] [copper-nickel alloy] <Insert material>.

First option in first subparagraph below gives manufacturer the choice; other options limit thickness. Second option is current standard of listed manufacturers but is subject to change. Third and fourth options are upgrades. If using materials other than copper, wall thickness may vary. See Evaluations.

3. Minimum Wall Thickness: [Manufacturer's choice] [0.025 inch (0.6 mm)] [0.028 inch (0.7 mm)] [0.035 inch (0.9 mm)] <Insert dimension>.

4. External Finish: Manufacturer's standard.

First option in subparagraph below is standard of most manufacturers. Third option is for applications with dirty fluids that require frequent tube cleaning. Retain all three options to give manufacturer the choice.

5. Internal Finish: [Enhanced] [or] [smooth].

D. Water Boxes:

1. Carbon-steel construction; arranged to provide visual inspection and cleaning of tubes from either end without disturbing refrigerant in shell.

Retain one of first two subparagraphs below. If retaining first subparagraph, verify availability of marine-type water box with manufacturers.

2. [Standard] [Marine-type] water box with piping connections.

a. Water boxes [and marine-type water-box covers ]shall have lifting lugs or eyebolts.

Retain one of first two subparagraphs below for special applications.

b. [Hinged] [or] [davited] water boxes.

c. [Hinged] [or] [davited] marine-type water-box covers.

3. Standard water box without piping connections.

a. Water boxes shall have lifting lugs or eyebolts.

Retain first subparagraph below for special applications.

b. [Hinged] [or] [davited] water boxes.

4. Nozzle Pipe Connections: [Welded, ASME B16.5, flat-face flange] [Welded, ASME B16.5, raised-face flange] [Grooved for mechanical-joint coupling] [Grooved with mechanical-joint coupling and flange adapter].

5. Thermistor or RTD temperature sensor factory installed in each nozzle.

6. Fit each water box with [3/4-inch (19-mm)] [or] [1-inch (25-mm)] <Insert dimension> drain connection at low point and vent connection at high point, each with threaded plug.

2.7 CONDENSER

A. Refrigerant Holding Pan: Steel or stainless steel.

B. Tubes:

1. Individually replaceable, straight tubes expanded into tube sheets. Replaceable from either end without damage to tube sheets and other tubes.

Tube materials for all heat exchangers can be independently selected; the choice can be different for each heat exchanger. Tube materials vary among manufacturers and chiller models; verify availability with manufacturer. First option in first subparagraph below is current standard of listed manufacturers.

Copper-nickel alloys available include 95/5 and 06/11. The higher nickel content in 06/11 provides better resistance to corrosion. If required by Project, insert specific alloy.

2. Material: [Copper] [or] [copper-nickel alloy] <Insert material>.

First option in first subparagraph below gives manufacturer the choice; other options limit thickness. Second option is current standard of listed manufacturers but is subject to change. Third and fourth options are upgrades. If using materials other than copper, wall thickness may vary. See Evaluations.

3. Minimum Wall Thickness: [Manufacturer's choice] [0.025 inch (0.6 mm)] [0.028 inch (0.7 mm)] [0.035 inch (0.9 mm)] <Insert dimension>.

4. External Finish: Manufacturer's standard.

First option in subparagraph below is standard of most manufacturers. Third option is for applications with dirty fluids that require frequent tube cleaning. Retain all three options to give manufacturer the choice.

5. Internal Finish: [Enhanced] [or] [smooth].

C. Water Boxes:

1. Carbon-steel construction; arranged to provide visual inspection and cleaning of tubes from either end without disturbing refrigerant in shell.

Retain one of first two subparagraphs below. If retaining first subparagraph, verify availability of marine-type water box with manufacturers.

2. [Standard] [Marine-type] water box with piping connections.

a. Water boxes [and marine-type water-box covers ]shall have lifting lugs or eyebolts.

Retain one of first two subparagraphs below for special applications.

b. [Hinged] [or] [davited] water boxes.

c. [Hinged] [or] [davited] marine-type water-box covers.

3. Standard water box without piping connections.

a. Water boxes shall have lifting lugs or eyebolts.

Retain first subparagraph below for special applications.

b. [Hinged] [or] [davited] water boxes.

4. Nozzle Pipe Connections: [Welded, ASME B16.5, flat-face flange] [Welded, ASME B16.5, raised-face flange] [Grooved for mechanical-joint coupling] [Grooved with mechanical-joint coupling and flange adapter].

5. Thermistor or RTD temperature sensor factory installed in each nozzle.

6. Fit each water box with [3/4-inch (19-mm)] [or] [1-inch (25-mm)] <Insert dimension> drain connection at low point and vent connection at high point, each with threaded plug.

Retain paragraph below for special applications. Verify availability with manufacturers.

D. Additional Corrosion Protection:

1. Electrolytic corrosion-inhibitor anode.

Retain one of two subparagraphs below.

2. Coat wetted surfaces with a corrosion-resistant finish.

3. Using same material as tubes, clad surfaces of end tube sheets in contact with fluid. Coat other wetted surfaces, including water boxes, with a corrosion-resistant finish.

2.8 FIRST-STAGE GENERATOR

A. Tubes:

1. [Replaceable, ]straight, or U tubes expanded into tube sheets.

First option in first subparagraph below gives manufacturer the choice; other options limit material choice. Second option is standard of Trane and YORK but is subject to change.

2. Material: [Manufacturer's standard] [steel] <Insert material>.

First option in first subparagraph below gives manufacturer the choice. Consult manufacturer for available options.

3. Minimum Wall Thickness: [Manufacturer's choice] <Insert dimension>.

4. External Finish: Manufacturer's standard.

5. Internal Finish: Manufacturer's choice; enhanced or smooth.

B. Water Boxes:

1. Carbon-steel construction; arranged to provide visual inspection and cleaning of tubes from either end without disturbing refrigerant in shell.

2. Standard water box.

3. Water boxes shall have lifting lugs or eyebolts.

4. Nozzle Pipe Connections: [Welded, ASME B16.5, flat-face flange] [Welded, ASME B16.5, raised-face flange] [Grooved for mechanical-joint coupling] [Grooved with mechanical-joint coupling and flange adapter].

5. Thermistor or RTD temperature sensor factory installed in each nozzle.

6. Fit each water box with [3/4-inch (19-mm)] [or] [1-inch (25-mm)] <Insert dimension> drain connection at low point and vent connection at high point, each with threaded plug.

2.9 SECOND-STAGE GENERATOR

A. Tubes:

1. Individually replaceable, straight tubes expanded into tube sheets. Replaceable from either end without damage to tube sheets and other tubes.

First option in first subparagraph below is standard of listed manufacturers. Verify availability of optional tube materials with manufacturers.

2. Material: [Copper] [or] [copper-nickel alloy] <Insert material>.

First option in first subparagraph below gives manufacturer the choice; other options limit thickness. Consult manufacturer for available options.

3. Minimum Wall Thickness: [Manufacturer's choice] [0.025 inch (0.6 mm)] [0.028 inch (0.7 mm)] [0.035 inch (0.9 mm)] <Insert dimension>.

4. External Finish: Manufacturer's standard.

5. Internal Finish: Manufacturer's standard.

B. Water Boxes:

1. Carbon-steel construction; arranged to provide visual inspection and cleaning of tubes from either end without disturbing refrigerant in shell.

2. Standard type.

3. Water boxes shall have lifting lugs or eyebolts.

4. Nozzle Pipe Connections: [Welded, ASME B16.5, flat-face flange] [Welded, ASME B16.5, raised-face flange] [Grooved for mechanical-joint coupling] [Grooved with mechanical-joint coupling and flange adapter].

5. Thermistor or RTD temperature sensor factory installed in each nozzle.

6. Fit each water box with [3/4-inch (19-mm)] [or] [1-inch (25-mm)] <Insert dimension> drain connection at low point and vent connection at high point, each with threaded plug.

2.10 DEDICATED HOT-WATER HEAT EXCHANGER

Retain this article for individual chillers requiring simultaneous heating and cooling.

A. Tubes:

1. Individually replaceable, straight tubes expanded into tube sheets. Replaceable from either end without damage to tube sheets and other tubes.

First option in first subparagraph below is standard of listed manufacturers. Verify availability of optional tube materials with manufacturers.

2. Material: [Copper] [or] [copper-nickel alloy] <Insert material>.

First option in first subparagraph below gives manufacturer the choice; other options limit thickness. Consult manufacturer for available options.

3. Minimum Wall Thickness: [Manufacturer's choice] [0.025 inch (0.6 mm)] [0.028 inch (0.7 mm)] [0.035 inch (0.9 mm)] <Insert dimension>.

4. External Finish: Manufacturer's standard.

5. Internal Finish: Manufacturer's standard.

B. Water Boxes:

1. Carbon-steel construction; arranged to provide visual inspection and cleaning of tubes from either end without disturbing refrigerant in shell.

2. Standard type.

3. Water boxes shall have lifting lugs or eyebolts.

4. Nozzle Pipe Connections: [Welded, ASME B16.5, flat-face flange] [Welded, ASME B16.5, raised-face flange] [Grooved for mechanical-joint coupling] [Grooved with mechanical-joint coupling and flange adapter].

5. Thermistor or RTD temperature sensor factory installed in each nozzle.

6. Fit each water box with [3/4-inch (19-mm)] [or] [1-inch (25-mm)] <Insert dimension> drain connection at low point and vent connection at high point, each with threaded plug.

2.11 SOLUTION HEAT EXCHANGER

A. Description: Shell-and-tube or brazed-plate heat exchanger, an integral part of chiller, increases cycle efficiency by preheating the weak solution on its way to the generator while precooling the strong solution returning from the generator.

2.12 BURNER ASSEMBLY

A. Burner: Welded construction with multivane, stainless-steel, flame-retention diffuser suitable for [natural gas] [propane] [and] [fuel oil].[ Mount burner on hinged access door to permit access to combustion chamber.]

B. Blower: Centrifugal fan integral to burner, directly driven by motor; with adjustable damper assembly and locking quadrant to set air-fuel ratio.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Section 230513 "Common Motor Requirements for HVAC Equipment." If different characteristics are required, insert subparagraphs below to suit Project.

1. Motors: Comply with requirements specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

a. Motor Sizes: Minimum size as indicated. If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

Retain first two paragraphs below for fuel-oil burners. Verify availability of safety options with manufacturer.

C. Oil Supply: Control devices and modulating control sequence shall comply with requirements of [ASME CSD-1] [FMG] [IRI] [UL].

1. Oil Pump: Two-stage, gear-type oil pump shall be capable of producing 300-psig (2070-kPa) discharge pressure and 15-in. Hg (50.7-kPa) vacuum.

2. Oil Piping Specialties:

a. Suction-line, manual, gate valve.

b. Removable-mesh oil strainer.

c. 0- to 30-in. Hg (0- to 101.3-kPa) vacuum; 0- to 30-psig (0- to 207-kPa) vacuum-pressure gage.

d. 0- to 300-psig (0- to 2070-kPa) oil-nozzle pressure gage.

e. Nozzle-line, solenoid-safety-shutoff oil valve.

D. Oil Pilot: [Intermittent] [Interrupted]-electric-spark pilot ignition with 100 percent main-valve and pilot-safety shutoff solenoid with [cadmium sulfide] [UV scanner] flame-safety control.

Retain first two paragraphs below for fuel-gas burners. Verify availability of safety options with manufacturers.

E. Gas Train: Control devices and modulating control sequence shall comply with requirements of [ASME CSD-1] [FMG] [IRI] [UL].

F. Gas Pilot: [Intermittent] [Interrupted]-electric-spark pilot ignition with 100 percent main-valve and pilot-safety shutoff with electronic supervision of burner flame.

Retain paragraph below to limit exhaust gas emissions. Verify availability with manufacturers.

G. Burner assembly shall be equipped to limit nitrogen oxide emissions to [20] [30] <Insert value> ppm.

2.13 ELECTRICAL

A. Factory installed and wired, and functionally tested at factory before shipment.

Retain first paragraph below for single-point, field-power connection. Requirement is limited to chillers equipped with factory-mounted motor controllers.

B. Single-point, field-power connection to [fused disconnect switch] [nonfused disconnect switch] [circuit breaker]. Minimum withstand rating shall be as required by electrical power distribution system, but not less than [42,000] [65,000] <Insert value> A.

1. Branch power circuit to each motor, dedicated electrical load, and to controls[ with disconnect switch or circuit breaker].

If retaining option in subparagraph above, retain first two subparagraphs below.

a. NEMA KS 1, heavy-duty fusible switch with rejection-type fuse clips rated for fuses. Select and size fuses to provide Type 2 protection according to IEC 60947-4-1.

b. NEMA AB 1, motor-circuit protector (circuit breaker) with field-adjustable, short-circuit-trip set point.

2. NEMA ICS 2, Class A, full-voltage, nonreversing motor controller, hand-off-auto switch, and overcurrent protection for each motor.

3. Control-circuit transformer with primary and secondary side fuses.

C. Terminal blocks with numbered [and color-coded ]wiring to match wiring diagram. Spare wiring terminal block for connection to external controls or equipment.

Retain paragraph below to enclose wiring. Chiller manufacturers do not normally enclose all wiring. Consult manufacturer for availability.

D. Wiring Outside of Enclosures: Factory installed in metal raceway except make terminal connections with not more than a 24-inch (610-mm) length of [liquidtight] [or] [flexible metallic] conduit.

2.14 CONTROLS

Coordinate this article with Section 230900 "Instrumentation and Control for HVAC."

A. Chiller control panel shall be separate from burner control panel.

B. Burner Control Panel: Factory[ or field] mounted. Maintains safe operating conditions, burner safety limits, burner operation, and interface with chiller controls; include the following components:

1. On-off switch.

2. Flame safeguard.

3. Contacts for remote monitoring of flame failure.

4. Contacts for proof of combustion air.

5. Exhaust gas temperature limit switch.

6. Control-circuit transformer.

7. Burner motor controls.

8. Fuel-oil pump controls, if chiller is equipped with fuel-oil pump.

9. Visual indication of on/off status of ignition, blower, and main fuel.

10. Alarm bell.

C. Control: Standalone and microprocessor based, with all memory stored in nonvolatile memory so that reprogramming is not required on loss of electrical power.

D. Enclosure: Unit mounted, NEMA 250, [Type 1] [Type 4] [Type 4x] <Insert type>, hinged or lockable.

E. Operator Interface: Multiple-character digital or graphic display with dynamic update of information and with keypad or touch-sensitive display located on front of control enclosure. Display the following information in either imperial or metric units selectable through the interface:

Verify availability of requirements in subparagraphs below with manufacturers.

1. Date and time.

2. Operating or alarm status.

3. Operating hours.

4. Outdoor-air temperature if required for chilled-water reset.

5. Temperature and pressure of operating set points.

6. Entering and leaving temperatures of chilled and condenser water.

7. Refrigerant temperature.

8. Solution concentration and temperature.

9. Indication of solution and purge-pump operation.

10. Generator shell pressure.

11. Number of starts.

12. Number of purge cycles.

13. Entering and leaving hot-water temperatures.

14. Burner firing rate displayed in percent.

15. <Insert status display items>.

F. Control Functions:

Verify availability of requirements in subparagraphs below with manufacturers.

1. Manual or automatic startup and shutdown time schedule.

2. Automatic cycle to prevent crystallization.

3. Entering and leaving chilled-water temperatures and control set points. Chilled-water temperature shall be reset based on [return-water] [outdoor-air] [space] <Insert condition> temperature.

4. Entering and leaving hot-water temperatures and control set points. Hot-water temperature shall be reset based on [return-water] [outdoor-air] [space] <Insert condition> temperature.

5. Condenser-fluid temperature.

LEED Credit EA 5 requires measurement of performance according to International Performance Measurement and Verification Protocol. If pursuing Credit EA 5, retain first two subparagraphs below along with satisfying other requirements. See Evaluations.

6. Cooling provided and heating energy used within programmable time periods, minimum monthly.

7. Heating provided and heating energy used within programmable time periods, minimum monthly.

8. <Insert control functions>.

G. Capacity Control: Automatically controls burner firing rate to maintain chilled-water temperature set point for cooling loads and heating-water temperature set point for heating loads ranging from [30] <Insert number> to 100 percent.

H. Safety Shutdowns: Chiller shall automatically shut down and require manual restart. Display a message following each safety shutdown.

Verify availability of requirements in subparagraphs below with manufacturers.

1. Crystallization.

2. Low refrigerant temperature.

3. Loss of chilled- or condenser-water flow.

4. Low leaving chilled-water temperature[, 2 deg F (1 deg C) below set point] <Insert condition>.

5. First-stage generator low-solution level.

6. First-stage generator high temperature or pressure.

7. Burner alarm or control malfunction.

8. Power failure.

9. Solution pump overloads.

10. External auxiliary safety shutdown.

11. High solution concentration.

12. Incomplete dilution cycle.

13. <Insert conditions>.

I. Warning Conditions: Chiller shall remain operational but inhibit burner firing rate to prevent safety shutdown. Control panel shall close warning contacts and generate a message when one of the following operating conditions is detected:

Verify availability of requirements in subparagraphs below with manufacturers.

1. Low refrigerant temperature.

2. High generator temperature or pressure.

3. High or low entering condenser-water temperature.

4. Solution temperature sensor failure.

5. Low chilled-water flow.

6. Purge-pump current overload.

7. <Insert warning conditions>.

J. Cycling Shutdowns: Permit automatic restart when preprogrammed limits are reached. Display a message following each cycle shutdown.

Verify availability of requirements in subparagraphs below with manufacturers.

1. Cooling Mode:

a. Loss of condenser-water flow.

b. Low leaving chilled-water temperature.

c. Power failure.

d. <Insert conditions>.

2. Heating Mode:

a. Loss of hot-water flow.

b. High leaving hot-water temperature.

c. Power failure.

d. <Insert conditions>.

K. Trending: Capability to trend analog data up to five parameters simultaneously over an adjustable period and frequency of polling.

L. Security Access: Provide electronic security access to controls through identification and password with at least three levels of access: view only; view and operate; and view, operate, and service.

M. Control Authority: At least four conditions: Off, local manual control at chiller, local automatic control at chiller, and automatic control through a remote source.

N. Communication Port: RS-232 port, USB 2.0 port, or equivalent connection capable of connecting a printer[ and a notebook computer].

Retain paragraph below if chiller controls interface with the BAS. Coordinate with Section 230900 "Instrumentation and Control for HVAC."

O. BAS Interface: Factory-installed hardware and software to enable the BAS to monitor, control, and display chiller status and alarms.

Retain first subparagraph below if interface with the BAS is through hardwired points and minimal interface is required.

1. Hardwired Points:

a. Monitoring: On-off status, [common trouble alarm] <Insert monitoring point>.

b. Control: On-off operation, [chilled-water, discharge temperature set-point adjustment] [hot-water, discharge temperature set-point adjustment] <Insert control point>.

Delete "Hardwired Points" Subparagraph above and retain subparagraph below if extensive interface with the BAS is required and is beyond what hardwired points can provide. Requirement may exclude some manufacturers.

2. [ASHRAE 135 (BACnet)] [LonTalk] [Modbus] [Industry-accepted, open-protocol] <Insert type of interface> communication interface with the BAS shall enable the BAS operator to remotely control and monitor the chiller from an operator workstation. Control features and monitoring points displayed locally at chiller control panel shall be available through the BAS.

2.15 FINISH

A. Paint chiller, using manufacturer's standard procedures, except comply with the following minimum requirements:

1. Provide at least one coat of primer with a total dry film thickness of at least 2 mils (0.05 mm).

2. Provide at least two coats of [alkyd-modified, vinyl enamel] [epoxy] [polyurethane] finish with a total dry film thickness of at least 4 mils (0.10 mm).

3. Paint surfaces that are to be insulated before applying the insulation.

4. Paint installed insulation to match adjacent uninsulated surfaces.

5. Color of finish coat to be [manufacturer's standard] [custom color selected by Architect] <Insert color description>.

2.16 ACCESSORIES

A. Sight Glasses: Equip unit with sight glasses for visual inspection of absorbent solution and refrigerant levels. Provide at least one sight glass in absorber and evaporator sections.

Retain one or both paragraphs below to add features furnished by chiller manufacturer.

B. Flow Switches:

1. Chiller manufacturer shall furnish a switch for each [condenser] [evaporator and condenser] and shall verify field-mounting location before installation.

Retain one of two subparagraphs below. Consult manufacturers for flow-switch requirements.

2. Paddle Flow Switches:

a. Vane operated to actuate a double-pole, double-throw switch with one pole field wired to the chiller control panel and the other pole field wired to the BAS.

b. Contacts: Platinum alloy, silver alloy, or gold-plated switch contacts with a rating of 10 A at 120-V ac.

c. Pressure rating equal to pressure rating of heat exchanger.

d. Construct body and wetted parts of Type 316 stainless steel.

e. House switch in an NEMA 250, [Type 4] <Insert type> enclosure constructed of die-cast aluminum.

f. Vane length to suit installation.

3. Pressure Differential Switches:

a. Construction: Wetted parts of body and trim constructed of Type 316 stainless steel.

b. Performance: Switch shall withstand, without damage, the full-pressure rating of the heat exchanger applied to either port and exhibit zero set point shift due to variation in working pressure.

c. Set Point: Screw type, field adjustable.

d. Electrical Connections: Internally mounted, screw-type terminal blocks.

e. Switch Enclosure: NEMA 250, [Type 4] <Insert type>.

f. Switch Action: Double-pole, double-throw switch with one pole field wired to the chiller control panel and the other pole field wired to the BAS.

C. Vibration Isolation:

1. Chiller manufacturer shall furnish neoprene-pad vibration isolation for each chiller.

a. Two layers of 0.375-inch- (10-mm-) thick, ribbed- or waffle-pattern neoprene pads separated by a 16-gage, stainless-steel plate.

b. Fabricate pads from 40- to 50-durometer neoprene.

c. Provide stainless-steel square bearing plate to load the pad uniformly between 20 and 40 psig (138 and 276 kPa) with a 0.12- to 0.16-inch (3- to 4-mm) deflection.

2.17 CAPACITIES AND CHARACTERISTICS

If Project has more than one type or configuration of direct-fired absorption chiller, delete this article and schedule chillers on Drawings.

A. Capacity: <Insert tons (kW)>.

LEED Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1.

B. Full-Load Efficiency (COP): <Insert number>.

Retain first option in first paragraph below if operating conditions reference ARI standard rating conditions; retain second option if operating conditions are other than ARI standard rating conditions.

C. Part-Load Efficiency [(IPLV)] [(NPLV)]: <Insert number>.

D. Evaporator:

1. Pressure Rating: [150 psig (1035 kPa)] [300 psig (2070 kPa)] <Insert psig (kPa)>.

2. Number of Passes: [Two] [Three] [Four].

3. Fluid Type: [Water] <Insert fluid type>.

4. Design Fluid Flow Rate: <Insert gpm (L/s)>.

5. Minimum Fluid Flow Rate: <Insert gpm (L/s)>.

6. Entering-Fluid Temperature: <Insert deg F (deg C)>.

7. Leaving-Fluid Temperature: <Insert deg F (deg C)>.

8. Fluid Pressure Drop: <Insert feet of head (kPa)>.

9. Fluid Velocity: <Insert fps (m/s)>.

Fouling-factor units in subparagraph below are consistent with ARI 560; first option is based on ARI 560 standard rating.

10. Fouling Factor: [0.0001 sq. ft. x h x deg F/Btu (0.000018 sq. m x deg C/W)] [0.00025 sq. ft. x h x deg F/Btu (0.000045 sq. m x deg C/W)] [0.0005 sq. ft. x h x deg F/Btu (0.00011 sq. m x deg C/W)] <Insert value>.

E. Absorber/Condenser:

1. Pressure Rating: [150 psig (1035 kPa)] [300 psig (2070 kPa)] <Insert psig (kPa)>.

2. Number of Passes: [One] [Two] [Three].

3. Fluid Type: [Water] <Insert fluid type>.

4. Design Fluid Flow Rate: <Insert gpm (L/s)>.

5. Entering-Fluid Temperature: <Insert deg F (deg C)>.

6. Leaving-Fluid Temperature: <Insert deg F (deg C)>.

7. Fluid Pressure Drop: <Insert feet of head (kPa)>.

8. Fluid Velocity: <Insert fps (m/s)>.

Fouling-factor units in subparagraph below are consistent with ARI 560; first option is based on ARI 560 standard rating.

9. Fouling Factor: [0.00025 sq. ft. x h x deg F/Btu (0.000045 sq. m x deg C/W)] [0.0005 sq. ft. x h x deg F/Btu (0.00011 sq. m x deg C/W)] [0.001 sq. ft. x h x deg F/Btu (0.00022 sq. m x deg C/W)] <Insert value>.

Retain first paragraph below for chillers equipped with dedicated hot-water heat exchanger.

F. Dedicated Hot-Water Heat Exchanger:

1. Capacity: <Insert MBtu/h (kW)>.

2. Pressure Rating: [150 psig (1035 kPa)] [300 psig (2070 kPa)] <Insert psig (kPa)>.

3. Number of Passes: [One] [Two] [Three] [Four].

4. Fluid Type: [Water] <Insert fluid type>.

5. Design Fluid Flow Rate: <Insert gpm (L/s)>.

6. Entering-Fluid Temperature: <Insert deg F (deg C)>.

7. Leaving-Fluid Temperature: <Insert deg F (deg C)>.

8. Fluid Pressure Drop: <Insert feet of head (kPa)>.

9. Fluid Velocity: <Insert fps (m/s)>.

Fouling-factor units in subparagraph below are consistent with ARI 560; first option is based on ARI 560 standard rating.

10. Fouling Factor: [0.0001 sq. ft. x h x deg F/Btu (0.000018 sq. m x deg C/W)] [0.00025 sq. ft. x h x deg F/Btu (0.000045 sq. m x deg C/W)] [0.0005 sq. ft. x h x deg F/Btu (0.00011 sq. m x deg C/W)] <Insert value>.

Consider impact of site altitude on fan and motor.

G. Burner Blower:

1. Motor Horsepower: <Insert value>.

2. RPM: <Insert value>.

H. Pump Horsepower:

1. Purge: <Insert value>.

2. Refrigerant: <Insert value>.

3. Solution: <Insert value>.

I. Chiller Control Electrical Requirements:

1. Power Input: <Insert kilowatts>.

2. Minimum Circuit Ampacity: <Insert value>.

3. Maximum Overcurrent Protection Device: <Insert amperage>.

4. Characteristics: [120] <Insert value>-V ac, single phase, 60 Hz.

J. Chiller Electrical Requirements:

1. Power Input: <Insert kilowatts>.

2. Minimum Circuit Ampacity: <Insert value>.

3. Maximum Overcurrent Protection Device: <Insert amperage>.

4. Characteristics: [208] [240] [480] <Insert value>-V ac, three phase, 60 Hz.

Consider actual heating value of fuel source if retaining first paragraph below. Contact fuel supplier and chiller manufacturers to determine impact. Insert text indicating heating value of fuel if applicable.

K. Natural-Gas Heating Value: <Insert Btu/cu. ft. (kJ/L)>.

L. Gas Input: <Insert cfh (mL/s)>.

Consider actual heating value of fuel source if retaining first paragraph below. Contact fuel supplier and chiller manufacturers to determine impact. Insert text indicating heating value of fuel if applicable.

M. Fuel-Oil Heating Value: <Insert Btu/gal. ((MJ/L))>.

N. Oil Input: <Insert gph (mL/s)>.

O. Noise Rating: [80] [85] <Insert dBA> sound power level when measured according to ARI 575. Provide factory-installed sound treatment if necessary to achieve the performance indicated.

2.18 SOURCE QUALITY CONTROL

Not all manufacturers "run test" chillers. Verify availability of run tests with manufacturers.

Retain first paragraph below if required. Independent certification may be acceptable to authorities having jurisdiction without further monitoring of plant's quality-control and testing program by Owner.

A. Perform functional [run ]tests of chillers before shipping.

B. Factory test and inspect absorber, generator, evaporator, and condenser according to ASME Boiler and Pressure Vessel Code: Section VIII, Division 1. Pressure test tube-side of heat exchangers, including water boxes, to 1.5 times the rated pressure. Vacuum and pressure test shells for leaks.

C. Rate sound power level according to ARI 575.

Retain first paragraph below for factory testing of factory-assembled chillers.

D. Burner Test: Factory adjust burner to eliminate excess oxygen, carbon dioxide, oxides of nitrogen emissions, and carbon monoxide in flue gas and to achieve combustion requirements indicated.

E. Prepare test report indicating test procedures, instrumentation, test conditions, and results. Submit copy of results within one week of test date.

PART 3 -  EXECUTION

3.1 CHILLER INSTALLATION

Retain first paragraph below if chillers are to be installed on a support structure other than a concrete base. Indicate design of support structure on Drawings.

A. Install chillers on support structure indicated.

B. Equipment Mounting:

Retain first subparagraph below to require equipment to be installed on cast-in-place concrete equipment bases.

1. Install chillers on cast-in-place concrete equipment bases. Comply with requirements for equipment bases and foundations specified in [Section 033000 "Cast-in-Place Concrete."] [Section 033053 "Miscellaneous Cast-in-Place Concrete."]

Retain one of two subparagraphs below. Retain first for projects in seismic areas; retain second for projects not in seismic areas. Indicate vibration isolation and seismic-control device type and minimum deflection in supported equipment schedule on Drawings.

2. Comply with requirements for vibration isolation and seismic control devices specified in Section 230548 "Vibration and Seismic Controls for HVAC."

3. Comply with requirements for vibration isolation devices specified in Section 230548.13 "Vibration Controls for HVAC."

C. Maintain manufacturer's recommended clearances for service and maintenance.

D. Charge chiller with absorbent and refrigerant if not factory charged.

E. Install separate devices furnished by manufacturer and not factory installed.

F. Insulate hot and cold chiller surfaces that are recommended by chiller manufacturer to be insulated. Comply with requirements in Section 230716 "HVAC Equipment Insulation."

G. Install electrical devices furnished with chiller but not specified to be factory mounted.

H. Install control wiring to field-mounted electrical devices.

3.2 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in Section 232113 "Hydronic Piping" and Section 232116 "Hydronic Piping Specialties."Section 15179 "Hydronic Piping Specialties." If Drawings are explicit enough, these requirements may be reduced or omitted.

If using hot water as a heating source, verify that the water temperature used on Project is within the applicable temperature range of the other Sections referenced. Otherwise, revise Sections to suit Project. This temperature range is of concern if water temperature is above 250 deg F (121 deg C).

A. Comply with requirements for hydronic piping in Section 232113 "Hydronic Piping" and Section 232116 "Hydronic Piping Specialties."Section 15179 "Hydronic Piping Specialties." Drawings indicate general arrangement of piping, fittings, and specialties.

Retain first three paragraphs below for chillers fed with a fuel-gas source.

B. Comply with requirements for gas piping in Section 231123 "Facility Natural-Gas Piping" or Section 231126 "Facility Liquefied-Petroleum Gas Piping." Drawings indicate general arrangement of piping, fittings, and specialties.

C. Connect gas piping full size to gas-train inlet with shutoff valve and union.

D. Install gas-fired boilers according to NFPA 54.

Retain first three paragraphs below for chillers fed with a fuel-oil source.

E. Comply with requirements for fuel-oil piping in Section 231113 "Facility Fuel-Oil Piping." Drawings indicate general arrangement of piping, fittings, and specialties.

F. Connect oil piping full size to burner inlet with shutoff valve and union.

G. Install oil-fired boilers according to NFPA 31.

H. Install piping adjacent to chiller to allow service and maintenance.

Retain first paragraph below for chillers equipped with a separate hot-water heat exchanger.

I. Hot-Water Heat-Exchanger Connections: Connect to heat-exchanger inlet with shutoff valve, [strainer,] [flexible connector,] thermometer, and plugged tee with shutoff valve and pressure gage. Connect to heat-exchanger outlet with shutoff valve, check valve, balancing valve,[ flexible connector,] flow switch, thermometer, plugged tee with shutoff valve and pressure gage,[ flow meter,] and drain connection with valve. Make connections to chiller with a [flange] [or] [mechanical coupling].

J. Evaporator-Fluid Connections: Connect to evaporator inlet with shutoff valve, [strainer,] [flexible connector,] thermometer, and plugged tee with shutoff valve and pressure gage. Connect to evaporator outlet with shutoff valve, balancing valve,[ flexible connector,] flow switch, thermometer, plugged tee with shutoff valve and pressure gage,[ flow meter,] and drain connection with valve. Make connections to chiller with a [flange] [or] [mechanical coupling].

K. Absorber/Condenser-Fluid Connections: Connect to inlet with shutoff valve, [strainer,] [flexible connector,] thermometer, and plugged tee with shutoff valve and pressure gage. Connect to outlet with shutoff valve, balancing valve,[ flexible connector,] flow switch, thermometer, plugged tee with shutoff valve and pressure gage,[ flow meter,] and drain connection with valve. Make connections to chiller with a [flange] [or] [mechanical coupling].

1. If not factory furnished or installed, provide pipe connecting fluid connection of absorber discharge and condenser inlet.

L. Refrigerant Pressure Relief Device Connections: Extend [vent piping] [separate vent piping for each chiller] to the outdoors without valves or restrictions. Comply with ASHRAE 15. Connect to chiller pressure relief device with flexible connector and dirt leg with drain valve.

M. Extend [purge vent piping] [separate purge vent piping for each chiller] to the outdoors. Comply with ASHRAE 15.

N. Connect each chiller drain connection with a union and drain pipe, and extend pipe, full size of connection, to floor drain. Provide a shutoff valve at each connection.

O. Comply with requirements for chimney system in Section 235100 "Breechings, Chimneys, and Stacks." Drawings indicate general arrangement of pipe, fittings, and specialties. Connect chimney system to chiller burner outlet and extend to the outdoors.

P. Connect fuel-fired burner assembly and blower and associated damper for combustion air.

3.3 STARTUP SERVICE

A. [Engage a factory-authorized service representative to perform] [Perform] startup service.

1. Complete installation and startup checks according to manufacturer's written instructions.

2. Operate chiller for run-in period.

3. Verify that absorbent and refrigerant charge is sufficient and chiller has been leak tested.

4. Verify that pumps are installed and functional.

5. Verify that thermometers and gages are installed.

6. Operate chiller for run-in period.

7. Verify that refrigerant pressure relief device is vented to the outdoors.

8. Verify proper motor rotation.

9. Verify proper fuel supply. Adjust air-fuel ratio and combustion.

10. Verify proper combustion-air source.

11. Verify proper exhaust emissions.

12. Verify static deflection of vibration isolators including deflection during chiller startup and shutdown.

13. Verify and record performance of fluid flow and low-temperature interlocks for evaporator and condenser.

14. Verify and record performance of chiller protection devices.

15. Test and adjust controls and safeties. Replace damaged or malfunctioning controls and equipment.

Retain subparagraph below for field-assembled burners.

16. Burner Test: Adjust burner to eliminate excess oxygen, carbon dioxide, oxides of nitrogen emissions, and carbon monoxide in flue gas.

B. Inspect field-assembled components, equipment installation, and piping and electrical connections for proper assembly, installation, and connection.

C. Prepare test and inspection startup reports.

END OF SECTION 236413.13

	DIRECT-FIRED ABSORPTION WATER CHILLERS
	236413.13 - 1



