Copyright 2011 AIA
MasterSpec Professional
09/11

Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 238113 - PACKAGED TERMINAL AIR-CONDITIONERS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

This Section does not include requirements for the LEED Rating System. Equipment specified in this Section may not qualify for LEED Rating System prerequisites and credits. To achieve prerequisites and obtain credits, HVAC system design alternatives that do not include packaged terminal air conditioners may be required.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section includes packaged terminal air conditioners and their accessories and controls, in the following configurations:

1. [Through-the-wall] [Freestanding] [Through-the-wall and freestanding] air conditioners.

2. Cooling-only units.

3. Heat-pump units.

4. Cooling units with electric heat.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product indicated.

B. Shop Drawings: For packaged terminal air conditioners. Include plans, elevations, sections, details for wall penetrations,[ seismic bracing,] and attachments to other work.

1. Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

2. Wiring Diagrams: For power, signal, and control wiring.

C. Color Samples: For unit cabinet, discharge grille, and exterior louver, and for each color and texture specified.

1.3 INFORMATIONAL SUBMITTALS

A. Field quality-control reports.

1.4 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

1.5 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

In addition to establishing minimum ventilation rates, ASHRAE 62.1 includes requirements for controls, surfaces in contact with the airstream, particulate and gaseous filtration, humidification and dehumidification, drain pan construction and connection, finned-tube coil selection and cleaning, and equipment access. Verify, with manufacturers, availability of units with components and features that comply with these requirements.

B. ASHRAE Compliance: Applicable requirements in ASHRAE 62.1, Section 4 - "Outdoor Air Quality," Section 5 - "Systems and Equipment," Section 6 - "Ventilation Rate Procedures," and Section 7 - "Construction and Startup."

Verify requirements in paragraph below with manufacturers.

C. ASHRAE/IESNA Compliance: Applicable requirements in ASHRAE/IESNA 90.1.

1.6 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this article are not less than remedies available to Owner under prevailing local laws.

A. Special Warranty: Manufacturer's standard form in which manufacturer agrees to repair or replace components of packaged terminal air conditioners that fail in materials or workmanship within specified warranty period.

Verify available warranties and warranty periods for units and components with manufacturers listed in Part 2.

1. Warranty Period for Sealed Refrigeration System: Manufacturer's standard, but not less than [five] <Insert number> years from date of Substantial Completion, including components and labor.

2. Warranty Period for Nonsealed System Parts: Manufacturer's standard, but not less than [five] <Insert number> years from date of Substantial Completion, including only components and excluding labor.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of two paragraphs and list of manufacturers in this article. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Carrier Corporation; a United Technologies company.

2. ClimateMaster, Inc.

3. Friedrich Air Conditioning Co.

4. General Electric Company; GE Consumer & Industrial - Appliances.

5. McQuay International.

6. Trane; a business of American Standard Companies.

7. <Insert manufacturer's name>.

2.2 MANUFACTURED UNITS

Retain first option in paragraph below for heating and cooling units and for heat pumps with supplemental heat.

A. Description: Factory-assembled and -tested, self-contained, packaged terminal air conditioner with room cabinet, electric refrigeration system,[ heating,] and temperature controls; fully charged with refrigerant and filled with oil; with [cord-connected] [hardwired] chassis.

2.3 CHASSIS

A. Cabinet: [0.052-inch- (1.32-mm-)] <Insert dimension> thick steel with removable front panel with concealed latches.

Retain first three subparagraphs below if units are not scheduled on Drawings.

1. Mounting: [Wall with wall sleeve] [Floor with subbase].

2. Discharge Grille: [Punched-louver discharge grille allowing four-way discharge-air pattern] [Extruded-aluminum discharge grille] [Reversible polycarbonate discharge grille allowing upward and horizontal airflow].

3. Louvers: [Extruded aluminum with enamel finish] [Stamped aluminum with clear-anodized finish] [Stamped steel with enamel finish]; [white] [bronze] [brown] [beige] <Insert color> color.

4. Finish: [Epoxy coating] [Baked enamel].

5. Access Door: Hinged door in top of cabinet for access to controls.

6. Cabinet Extension: Matching cabinet in construction and finish, allowing diversion of airflow to adjoining room; with grille.

Retain first subparagraph below if required by Project requirements or authorities having jurisdiction. Verify requirements in first subparagraph below with manufacturers.

7. Finish of Interior Surfaces: Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1.

Retain first subparagraph below for floor-mounted units.

8. Subbase: Enameled steel with adjustable leveling feet and adjustable end plates[, with factory-installed and -wired, fused disconnect switch and receptacle sized for unit].

9. Wall Sleeves: [Galvanized steel with polyester finish] [Molded polymer] [Molded fiberglass-reinforced polyester].

B. Refrigeration System: Direct-expansion indoor coil with capillary restrictor; and hermetically sealed scroll compressor with vibration isolation and overload protection.

1. Indoor and Outdoor Coils: Seamless copper tubes mechanically expanded into aluminum fins[ with capillary tube distributor on indoor coil].

Retain first three subparagraphs below for heat-pump units.

2. Accumulator.

3. Constant-pressure expansion valve.

4. Reversing valve.

Retain one of two subparagraphs below to require a specific refrigerant type; delete both if any refrigerant type is acceptable. Retain second or third option in first subparagraph or retain second subparagraph if required by Project requirements or authorities having jurisdiction.

5. Charge: [R-22] [R-407C] [R-410A].

6. Charge: R-407C or R-410A.

C. Indoor Fan: Forward curved, centrifugal; with motor and positive-pressure ventilation damper with [concealed manual] [electric] operator.

Filters in first paragraph below are optional feature. Washable filters may not comply with requirements in ASHRAE 62.1 for a minimum MERV 6. Verify filter efficiency with manufacturers.

D. Filters: Washable polyurethane in molded plastic frame.

E. Condensate Drain: Drain pan [to direct condensate to outdoor coil for re-evaporation] [and piping to direct condensate to building waste and vent piping].

In subparagraph below, verify drain pan construction and connection requirements with manufacturers if required by Project requirements or authorities having jurisdiction. ASHRAE 62.1 has specific requirements for drain pan construction and connections.

1. Comply with ASHRAE 62.1 for drain pan construction and connections.

F. Outdoor Fan: [Forward curved, centrifugal] [Propeller] [Forward curved, centrifugal or propeller] type [with separate] [driven by indoor fan] motor.

Default motor characteristics are specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

1. Indoor and Outdoor Fan Motors: Two speed; comply with NEMA designation, temperature rating, service factor, enclosure type, and efficiency requirements for motors specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

a. Fan Motors: Permanently lubricated split capacitor.

b. Motor Sizes: Minimum size as indicated. If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

c. Controllers, Electrical Devices, and Wiring: Comply with requirements for electrical devices and connections specified in electrical Sections.

Retain paragraph below for heating and cooling units or for heat pumps with supplemental heat.

G. Electric-Resistance Heating Coil: Nickel-chromium-wire, electric-resistance heating elements with contactor and high-temperature-limit switch.

2.4 CONTROLS

If required by Project requirements or authorities having jurisdiction, verify that manufacturers can provide units with controls that comply with requirements.

A. Control Module: Unit-mounted digital panel with touchpad temperature control and with touchpad for heating, cooling, and fan operation. Include the following features:

1. Low Ambient Lockout Control: Prevents cooling-cycle operation below 40 deg F (5 deg C) outdoor air temperature.

Retain first subparagraph below for heat-pump units.

2. Heat-Pump Ambient Control: Field-adjustable switch changes to heat-pump heating operation above 40 deg F (5 deg C) and to supplemental heating below plus 25 deg F (minus 4 deg C).

Retain option in first subparagraph below for heating and cooling units and for heat pumps.

3. Temperature-Limit Control: Prevents occupant from exceeding preset[ setback or] setup temperature.

4. Reverse-Cycle Defrost: Solid-state sensor monitors frost buildup on [indoor] [outdoor] coil and reverses unit to melt frost.

B. Remote Control: Standard unit-mounted controls with remote-mounted, low-voltage adjustable thermostat with heat anticipator, [heat-off-cool-auto] [heat-off-cool] switch, and[ on-auto] fan switch.

Retain one of two "Outdoor Air" Paragraphs below. Retain first paragraph if required by Project requirements or authorities having jurisdiction.

C. Outdoor Air: Motorized intake damper. Open intake when unit indoor air fan runs.

D. Outdoor Air: Manual intake damper.

2.5 CAPACITIES AND CHARACTERISTICS

If Project has more than one type or configuration of packaged terminal air conditioners, delete this article and schedule packaged terminal air conditioners on Drawings.

A. Airflow: <Insert cfm (L/s)>.

B. Outdoor Air-Intake Rate: <Insert cfm (L/s)>.

C. Cooling Capacity:

1. Total: <Insert Btu/h (kW)>.

2. Sensible: <Insert Btu/h (kW)>.

3. Energy-Efficiency Ratio: <Insert number>.

4. Indoor Coil Entering-Air Dry Bulb Temperature: <Insert deg F (deg C)>.

5. Indoor Coil Entering-Air Wet Bulb Temperature: <Insert deg F (deg C)>.

6. Indoor Coil Leaving-Air Dry Bulb Temperature: <Insert deg F (deg C)>.

7. Indoor Coil Leaving-Air Wet Bulb Temperature: <Insert deg F (deg C)>.

8. Outdoor Coil Entering-Air Temperature: <Insert deg F (deg C)>.

D. Heat-Pump Capacity:

1. Total: <Insert Btu/h (kW)>.

2. Outdoor Temperature: <Insert deg F (deg C)>.

E. Electric Heat Capacity: <Insert Btu/h (kW)>.

F. Sound:

1. Indoor: <Insert Bels>.

2. Outdoor: <Insert Bels>.

G. Electrical Characteristics:

1. Volts: <Insert value>.

2. Phase: [Single] [Three].

3. Hertz: 60.

4. Full-Load Amperes: <Insert value>.

5. Minimum Circuit Ampacity: <Insert value>.

6. Maximum Overcurrent Protection: <Insert amperage>.

2.6 SOURCE QUALITY CONTROL

A. Sound-Power Level Ratings: Factory test to comply with ARI 300, "Sound Rating and Sound Transmission Loss of Packaged Terminal Equipment."

B. Unit Performance Ratings: Factory test to comply with ARI 310/380/CSA C744, "Packaged Terminal Air-Conditioners and Heat Pumps."

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Install units level and plumb, maintaining manufacturer's recommended clearances and tolerances.

B. Install wall sleeves in finished wall assembly; seal and weatherproof. Joint-sealant materials and applications are specified in Section 079200 "Joint Sealants."

Retain paragraph below in seismic areas. Equipment protection may be required for some types of buildings. Verify requirements with model building codes and ASCE/SEI 7.

C. Install and anchor wall sleeves to withstand, without damage to equipment and structure, seismic forces required by building code.

3.2 FIELD QUALITY CONTROL

A. Tests and Inspections:

1. Inspect for and remove shipping bolts, blocks, and tie-down straps.

2. After installing packaged terminal air conditioners and after electrical circuitry has been energized, test for compliance with requirements.

3. Operational Test: After electrical circuitry has been energized, start units to confirm proper motor rotation and unit operation.

4. Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

B. Packaged terminal air conditioners will be considered defective if they do not pass tests and inspections.

C. Prepare test and inspection reports.

END OF SECTION 238113

	PACKAGED TERMINAL AIR-CONDITIONERS
	238113 - 1



