Copyright 2011 AIA
MasterSpec Professional
09/11

Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 238119 - SELF-CONTAINED AIR-CONDITIONERS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

This Section includes requirements for the LEED Rating System. However, equipment specified in this Section may not qualify for LEED Rating System prerequisites and credits. Verify, with manufacturers, that the requirements for prerequisites and credits can be met. To achieve prerequisites and obtain credits, HVAC system design alternatives that do not include self-contained air conditioners may be required.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section includes packaged, air-cooled air-conditioning units with refrigerant compressors and controls intended for indoor installations.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product indicated.

B. LEED Submittals:

Coordinate "Product Data for Credit EA 4" Subparagraph below with requirements for refrigerants.

1. Product Data for Credit EA 4: Documentation indicating that equipment and refrigerants comply.

2. Product Data for Prerequisite IEQ 1: Documentation indicating that units comply with ASHRAE 62.1, Section 5 - "Systems and Equipment."

C. Shop Drawings: Include plans, elevations, sections, details, and attachments to other work.

1. Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

2. Wiring Diagrams: For power, signal, and control wiring.

1.3 INFORMATIONAL SUBMITTALS

A. Warranty: Sample of special warranty.

1.4 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

1.5 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

B. ARI Compliance:

Retain one or more of three subparagraphs below depending on types of units in Project. Retain first subparagraph for units with cooling capacity less than 65,000 Btu/h (19 kW); retain second subparagraph for units with cooling capacity from 65,000 to 250,000 Btu/h (19 to 73 kW); retain third subparagraph for vertical configuration in a commercial or industrial application.

1. Applicable requirements in ARI 210/240.

2. Applicable requirements in ARI 340/360.

3. Applicable requirements in ARI 390.

C. ASHRAE Compliance:

1. Fabricate and label refrigeration system to comply with ASHRAE 15, "Safety Standard for Refrigeration Systems."

"ASHRAE Compliance" Paragraph below may be required to comply with Project requirements or authorities having jurisdiction. LEED Prerequisite IEQ 1 requires compliance with requirements in ASHRAE 62.1. In addition to establishing minimum ventilation rates, ASHRAE 62.1 includes requirements for controls, surfaces in contact with the airstream, particulate and gaseous filtration, humidification and dehumidification, drain pan construction and connection, finned-tube coil selection and cleaning, and equipment access. See "LEED Rating System" Article in the Evaluations for discussion on this prerequisite. Verify, with manufacturers, availability of units with components and features that comply with these requirements.

2. ASHRAE Compliance: Applicable requirements in ASHRAE 62.1, Section 4 - "Outdoor Air Quality," Section 5 - "Systems and Equipment," Section 6 - "Ventilation Rate Procedures," and Section 7 - "Construction and Startup."

"ASHRAE/IESNA Compliance" Paragraph below may be required to comply with Project requirements or authorities having jurisdiction. LEED Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1. See "LEED Rating System" Article in the Evaluations for discussion on this prerequisite.

D. ASHRAE/IESNA Compliance: Applicable requirements in ASHRAE/IESNA 90.1.

1.6 WARRANTY

A. Special Warranty: Manufacturer's standard form in which manufacturer agrees to repair or replace components of self-contained air conditioners that fail in materials or workmanship within specified warranty period.

Verify available warranties and warranty periods for units and components with manufacturers listed.

1. Warranty Period:

Retain the applicable level of warranty in three subparagraphs below. Flexibility exists in the level of warranty that can be purchased; not all manufacturers' standard warranty is the same and differences add/subtract base unit cost. Extended warranties will affect construction costs.

a. For Compressor: [One] [Five] <Insert number> year(s) from date of Substantial Completion.

b. For Parts: [One] [Five] <Insert number> year(s) from date of Substantial Completion.

c. For Labor: [One] [Five] <Insert number> year(s) from date of Substantial Completion.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of two paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Bard Manufacturing Company.

2. Carrier Corporation; Home Comfort and HVAC Building & Industrial Systems.

3. Engineered Air.

4. Marshall Engineered Products Co. (MEPCO).

5. McQuay International.

6. Trane Inc.

7. USA Coil & Air.

8. Whalen Company (The).

9. <Insert manufacturer's name>.

2.2 PACKAGED UNITS

A. Description: Factory assembled, wired, and tested; and fully charged with refrigerant and oil.

Retain one of three "Configuration" paragraphs below.

B. Configuration: Horizontal, ceiling[-plenum] mounted.

C. Configuration: Vertical, floor mounted; [vertical] [and] [horizontal] discharge.

D. Configuration: Horizontal, ceiling mounted and vertical, floor mounted; [vertical] [and] [horizontal] discharge.

E. Disconnect Switch: Factory mounted [in control panel] [on cabinet].

2.3 Cabinet

A. Frame and Panels: Structural-steel frame with galvanized-steel panels and access doors or panels.

Retain first subparagraph below if units are exposed in finished spaces.

1. Exterior-Surface Finish: Factory painted in color selected by Architect.

ASHRAE compliance in "Interior-Surface Finish" Subparagraph below may be required to comply with Project requirements or authorities having jurisdiction. Retain subparagraph to comply with LEED Prerequisite IEQ 1. See "LEED Rating System" Article in the Evaluations for discussion on this prerequisite.

2. Interior-Surface Finish: Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1.

B. Insulation: 1-inch- (25-mm-) thick, glass-fiber duct liner complying with ASTM C 1091 and having a microbial coating on cabinet interior and control panel. 1/2-inch- (13-mm-) thick liner is acceptable for units smaller than 15 tons (50 kW).

C. Return-Air Opening: Rear, [open] [flange for duct connection].

D. Corrosion-Resistant Treatment: Phenolic coating on unit interior and exterior.

2.4 Supply-air Fan

A. Fan Material: Galvanized steel.

B. Configuration: Double-width, double-inlet, forward-curved centrifugal fan; statically and dynamically balanced. [Vertical] [Horizontal] discharge with flexible discharge collar.

Retain one of two drive types in first paragraph below.

C. Drive: [Belt, with fan mounted on permanently lubricated bearings] [Direct, with fan and motor resiliently mounted].

Retain first three paragraphs below for belt-driven units.

D. Fan Sheaves: Variable pitch, dynamically balanced, bored to fit shafts, and keyed for initial startup.

E. Motor Sheave: Variable and adjustable pitch, dynamically balanced, and selected to achieve specified rpm when set at midposition.

F. Belt Rating: As recommended by manufacturer or a minimum of one and one-half times nameplate rating of motor.

Default motor characteristics are specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

G. Comply with NEMA designation, temperature rating, service factor, enclosure type, and efficiency requirements for motors specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

1. Special Motor Features: Premium efficiency, as defined in Section 230513 "Common Motor Requirements for HVAC Equipment."

If unique characteristics are required for motors in this Section, insert in subparagraph below.

2. <Insert unique motor characteristics>.

H. Outdoor-Air-Intake Accessories:

1. Barometric Outdoor-Air Damper: Adjustable-blade damper allowing induction of up to 25 percent outdoor air when evaporator fan is running.

2. Motorized Outdoor-Air Damper: Motorized, two-position blade damper allowing induction of up to 25 percent outdoor air; with spring-return, low-voltage damper motor.

3. Energy-Recovery Ventilator: Assembly of desiccant-coated, heat-recovery wheels and centrifugal exhaust fans to transfer approximately 67 percent of the difference between the sensible and latent heat of outdoor and exhaust air.

4. Air-Side Economizer: Damper assembly allowing induction of up to 100 percent outdoor air to maintain a selected mixed-air temperature; and exhaust damper and spring-return, low-voltage, modulating damper motor with minimum position adjustment.

2.5 REFRIGERATION SYSTEM

A. Compressor: Scroll type, hermetically sealed, 3600 rpm maximum, and resiliently mounted with positive lubrication and internal motor protection.

B. Refrigerant Coils (Indoor and Outdoor for Air-Cooled Units): Seamless copper tubes expanded into aluminum fins.

Corrosion-resistant treatment in first subparagraph below is an optional feature.

1. Corrosion-Resistant Treatment: Phenolic coating applied with multiple dips and baked.

2. Refrigerant Circuits: A separate circuit for each compressor, with externally equalized thermal-expansion valve, filter dryer, and charging valves.

ASHRAE compliance option in first subparagraph below may be required to comply with Project requirements or authorities having jurisdiction. Retain first option in first subparagraph to comply with LEED Prerequisite IEQ 1. See "LEED Rating System" Article in the Evaluations for discussion on this prerequisite.

3. Mount coil assembly over stainless-steel drain pan[ complying with ASHRAE 62.1] [and] [having a condensate pump unit with integral float switch, pump-motor assembly, and condensate reservoir].

Retain option in first subparagraph below if any refrigerant type is acceptable. Delete to comply with LEED-NC, LEED-CS, and LEED for Schools Credit EA 4.

4. Refrigerant: [R-22, ]R-407C or R-410A.

First subparagraph below is required for heat-pump units only. Retain other appropriate components to suit Project.

5. Expansion valve with replaceable thermostatic element.

6. Refrigerant dryer.

7. High-pressure switch.

8. Low-pressure switch.

9. Thermostat for coil freeze-up protection during low ambient temperature operation or loss of air.

10. Low ambient temperature switch.

11. Brass service valves installed in discharge and liquid lines.

2.6 Heating Coil

A. Electric Coil: Helical, nickel-chrome, resistance-wire heating elements with refractory ceramic support bushings; automatic-reset thermal cutout; built-in magnetic contactors; manual-reset thermal cutout; airflow-proving device; and one-time fuses in terminal box for overcurrent protection.

2.7 CONTROLS

A. Control Package: Factory wired, including contactor, high- and low-pressure cutouts, internal-winding thermostat for compressor, control-circuit transformer, and noncycling reset relay.

B. Time-Delay Relay: Five-minute delay to prevent compressor cycling.

Revise first paragraph below to suit unit configuration.

C. Adjustable Thermostat: [Unit mounted] [Remote] to control the following:

1. Supply fan.

2. Compressor.

3. Condenser.

4. Electric heater.

D. System Selector Switch: [Heat-off-cool] [Off-heat-auto-cool].

E. Fan Control Switch: Auto-on.

F. Microprocessor Control Panel: Controls unit functions as standalone or network operation, including refrigeration and safety controls, with unit-mounted display, and the following:

Revise subparagraphs below to suit unit configuration.

1. Supply fan.

2. Supply-fan motor speed.

3. Compressors.

4. Air-cooled condenser.

5. Multistep, electric heater.

6. Time-of-day control to cycle unit on and off.

7. Night-heat, morning warm-up cycle.

8. Economizer control.

9. Panel-mounted control switch to operate unit in remote or local control mode or to stop or reset.

10. Panel-mounted indication of the following:

a. Operating status.

b. System diagnostics and safety alarms.

c. Supply-air temperature set point.

d. Zone heating-temperature set point.

e. Supply-air pressure set point.

f. Economizer minimum position set point.

g. Supply-air-pressure, high-limit set point.

LEED-NC and LEED for Schools Credit EA 5, LEED-CI Credit EA 3, and LEED-CS Credit EA 5.1 require continuous metering equipment for monitoring building's energy consumption performance over time. Retain four subparagraphs below if required to comply with the requirements for this credit. Verify availability of control features with unit manufacturers.

h. Monitor motor loads.

i. Monitor economizer cycle.

j. Monitor cooling load.

k. Monitor air distribution static pressure and ventilation air volumes.

If Project has more than one type or configuration of self-contained air conditioner, delete article below and schedule self-contained air conditioners on Drawings.

2.8 Capacities and Characteristics

A. Cooling Capacity:

1. Total: <Insert Btu/h (kW)>.

2. Sensible: <Insert Btu/h (kW)>.

Retain first subparagraph below for units with cooling capacity of 5 tons (17 kW) or less.

3. Seasonal Energy Efficiency Ratio: [10.0] [12.0] [13.0] [14.0] [16.0] <Insert ratio>.

Retain first subparagraph below for units with cooling capacity of more than 5 tons (17 kW).

4. Energy Efficiency Ratio: [10.0] [12.0] [13.0] [14.0] [16.0] <Insert ratio>.

5. Moisture Removal Rate: <Insert pints/h (L/h)>.

6. Entering-Air Temperature:

a. Dry Bulb: <Insert deg F (deg C)>.

b. Wet Bulb: <Insert deg F (deg C)>.

7. Leaving-Air Temperature:

a. Dry Bulb: <Insert deg F (deg C)>.

b. Wet Bulb: <Insert deg F (deg C)>.

B. Heating Capacity:

1. Total: <Insert Btu/h (kW)>.

2. Air-Temperature Rise: <Insert deg F (deg C)>.

3. Heat Pump:

a. Coefficient of Performance: <Insert value>.

b. Heating Season Performance Factor: [7.7] [8.0] <Insert value>.

4. Electric Heat:

a. Total Capacity: <Insert Btu/h (kW)>.

b. Air-Temperature Rise: <Insert deg F (deg C)>.

c. Control Steps: [One] [Two] [Three] <Insert number>.

Auxiliary heat may be required for heat-pump units.

C. Auxiliary Electric Heat:

1. Total Capacity: <Insert Btu/h (kW)>.

2. Air-Temperature Rise: <Insert deg F (deg C)>.

3. Control Steps: [One] [Two] [Three] <Insert number>.

D. Supply-Air Fan:

1. Fan motor.

2. Size: <Insert value> hp.

3. [Multispeed, PSC] [Open-dripproof] [Totally enclosed fan-cooled] type.

4. Total Airflow:

Retain first two subparagraphs below for variable-speed fans.

a. High: <Insert cfm (L/s)>.

b. Low: <Insert cfm (L/s)>.

5. Outdoor Airflow: <Insert cfm (L/s)>.

E. Air-Cooled Condenser:

1. Fan Quantity: [Two] [Four] <Insert number>.

2. Motor Speed: <Insert value> rpm.

3. Motor Horsepower: <Insert value>.

F. Filters:

1. Prefilters:

a. Type: [Flat] [Pleated] disposable panel.

b. MERV: <Insert number>.

c. Face Area: <Insert sq. ft. (sq. m)>.

d. Surface Area: <Insert sq. ft. (sq. m)>.

e. Thickness or Depth: [2 inches (50 mm)] [4 inches (100 mm)].

f. Number of Filters: <Insert number>.

g. Maximum or Rated Face Velocity: <Insert fpm (m/s)>.

h. Initial Resistance: <Insert inches wg (Pa)>.

i. Recommended Final Resistance: <Insert inches wg (Pa)>.

j. Access Location: [Front] [Back] [Side].

2. Final Filter:

a. Type: [Flat] [Pleated] disposable panel.

LEED Prerequisite IEQ 1 requires compliance with ASHRAE 62.1, which requires a MERV rating of 6 or higher. See "LEED Rating System" Article in the Evaluations for discussion on this prerequisite.

b. MERV: <Insert number>.

c. Face Area: <Insert sq. ft. (sq. m)>.

d. Surface Area: <Insert sq. ft. (sq. m)>.

e. Thickness or Depth: [2 inches (50 mm)] [4 inches (100 mm)].

f. Number of Filters: <Insert number>.

g. Maximum or Rated Face Velocity: <Insert fpm (m/s)>.

h. Initial Resistance: <Insert inches wg (Pa)>.

i. Recommended Final Resistance: <Insert inches wg (Pa)>.

j. Access Location: [Front] [Back] [Side].

G. Accessories:

1. Manual outdoor-air damper.

2. Motorized outdoor-air damper.

3. Air-side economizer.

4. Hot-gas bypass.

H. Single-Point Electrical Characteristics:

1. Volts: [120] [208] [230] [460] <Insert value>.

2. Phase: [Single] [Three].

3. Hertz: 60.

4. Full-Load Amperes: <Insert value>.

5. Minimum Circuit Ampacity: <Insert value>.

6. Maximum Overcurrent Protection: <Insert amperage>.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Install units level and plumb.

B. Anchor units to structure.

Retain first paragraph below if seismic design is required.

C. Install seismic restraints.

Retain paragraph below for units connected to ducts. Coordinate duct installation requirements with schematics on Drawings and with requirements specified for duct systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

D. Duct Connections: Duct installation requirements are specified in Section 233113 "Metal Ducts." Drawings indicate the general arrangement of ducts. Connect supply[ and return] ducts to self-contained air conditioners with flexible duct connectors. Flexible duct connectors are specified in Section 233300 "Air Duct Accessories."

3.2 FIELD QUALITY CONTROL

A. Perform tests and inspections.

Retain subparagraph below to require a factory-authorized service representative to assist Contractor with inspections, tests, and adjustments.

1. Manufacturer's Field Service: Engage a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

B. Tests and Inspections:

1. Operational Test: After electrical circuitry has been energized, start units to confirm proper motor rotation and unit operation, and inspect for refrigerant leaks.

2. Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

C. Units will be considered defective if they do not pass tests and inspections.

D. Prepare test and inspection reports.

END OF SECTION 238119

	SELF-CONTAINED AIR-CONDITIONERS
	238119 - 1



