Copyright 2011 AIA
MasterSpec Professional
09/11

Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 238123 - COMPUTER-ROOM AIR-CONDITIONERS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

This Section includes requirements for the LEED Rating System. However, equipment specified in this Section may not qualify for LEED Rating System prerequisites and credits. Verify with manufacturers that the requirements for prerequisites and credits can be met. To achieve prerequisites and obtain credits, HVAC system design alternatives that do not include computer-room air conditioners may be required.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Floor-mounted computer-room air conditioners, 6 tons (21 kW) and larger.

2. Floor-mounted computer-room air conditioners, 5 tons (18 kW) and smaller.

3. Ceiling-mounted computer-room air conditioners.

4. Console computer-room air conditioners.

1.2 PERFORMANCE REQUIREMENTS

Retain this article with "Seismic Qualification Certificates" Paragraph in "Informational Submittals" Article for projects requiring seismic design. Model building codes and ASCE/SEI 7 establish criteria for buildings subject to earthquake motions. Verify requirements of authorities having jurisdiction.

A. Seismic Performance: Computer-room air conditioners shall withstand the effects of earthquake motions determined according to [ASCE/SEI 7] <Insert requirement>.

Retain subparagraph below to define the term "withstand" as it applies to this Project. Definition varies with type of building and occupancy and is critical to valid certification. Option is used for essential facilities where equipment must operate immediately after an earthquake.

1. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified[ and the unit will be fully operational after the seismic event]."

1.3 ACTION SUBMITTALS

A. Product Data: For each type of product indicated.

B. LEED Submittals:

Coordinate "Product Data for Credit EA 4" Subparagraph below with requirements for refrigerants.

1. Product Data for Credit EA 4: Documentation indicating that equipment and refrigerants comply.

2. Product Data for Prerequisite IEQ 1: Documentation indicating that units comply with ASHRAE 62.1, Section 5 - "Systems and Equipment."

C. Shop Drawings: For computer-room air conditioners. Include plans, elevations, sections, details, and attachments to other work.

1. Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

2. Wiring Diagrams: For power, signal, and control wiring.

D. Color Samples: For unit cabinet, discharge grille, and exterior louver and for each color and texture specified.

1.4 INFORMATIONAL SUBMITTALS

Retain first paragraph below if required by seismic criteria applicable to Project. Coordinate with Section 230548 "Vibration and Seismic Controls for HVAC." See ASCE/SEI 7 for certification requirements for equipment and components.

A. Seismic Qualification Certificates: For computer-room air conditioners, accessories, and components, from manufacturer.

B. Field quality-control reports.

1.5 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

1.6 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

B. ASHRAE Compliance:

1. Fabricate and label refrigeration system to comply with ASHRAE 15, "Safety Standard for Refrigeration Systems."

"ASHRAE Compliance" Paragraph below may be required to comply with Project requirements or authorities having jurisdiction. LEED Prerequisite IEQ 1 requires compliance with requirements in ASHRAE 62.1. In addition to establishing minimum ventilation rates, ASHRAE 62.1 includes requirements for controls, surfaces in contact with the airstream, particulate and gaseous filtration, humidification and dehumidification, drain pan construction and connection, finned-tube coil selection and cleaning, and equipment access. See "LEED Rating System" Article in the Evaluations for discussion on this prerequisite. Verify, with manufacturers, availability of units with components and features that comply with these requirements.

2. ASHRAE Compliance: Applicable requirements in ASHRAE 62.1, Section 4 - "Outdoor Air Quality," Section 5 - "Systems and Equipment," Section 6 - "Ventilation Rate Procedures," and Section 7 - "Construction and Startup."

"ASHRAE/IESNA Compliance" Paragraph below may be required to comply with Project requirements or authorities having jurisdiction. LEED Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1. See "LEED Rating System" Article in the Evaluations for discussion on this prerequisite.

C. ASHRAE/IESNA Compliance: Applicable requirements in ASHRAE/IESNA 90.1.

D. ASME Compliance: Fabricate and label water-cooled condenser shell to comply with ASME Boiler and Pressure Vessel Code: Section VIII, "Pressure Vessels," Division 1.

1.7 WARRANTY

A. Special Warranty: Manufacturer's standard form in which manufacturer agrees to repair or replace components of computer-room air conditioners that fail in materials or workmanship within specified warranty period.

Verify available warranties and warranty periods for units and components with manufacturers listed in Part 2 articles.

1. Warranty Period for Compressors: Manufacturer's standard, but not less than [five] [10] <Insert number> years from date of Substantial Completion.

2. Warranty Period for Humidifiers: Manufacturer's standard, but not less than [three] <Insert number> years from date of Substantial Completion.

3. Warranty Period for Control Boards: Manufacturer's standard, but not less than [three] <Insert number> years from date of Substantial Completion.

PART 2 -  PRODUCTS

2.1 FLOOR-MOUNTED UNITS 6 TONS (21 kW) AND LARGER

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Airflow Company; a division of The McClain Company, Inc.

2. Carrier Corporation; a United Technologies company.

3. Compu-Aire, Inc.

4. Data Aire Inc.

5. Koldwave, Inc.; a Mestek company.

6. Liebert Corporation.

7. McQuay International.

8. Stulz-ATS.

9. Trane; a business of American Standard Companies.

10. <Insert manufacturer's name>.

C. Description: Packaged, factory assembled, prewired, and prepiped; consisting of cabinet, fans, filters, humidifier, and controls.

D. Cabinet and Frame: Welded steel, braced for rigidity, and supporting compressors and other mechanical equipment and fittings.

1. Doors and Access Panels: Galvanized steel with polyurethane gaskets, hinges, and concealed fastening devices.

2. Insulation: Thermally and acoustically insulate cabinet interior with 1-inch- (25-mm-) thick duct liner.

ASHRAE compliance in "Finish of Interior Surfaces" Subparagraph below may be required to comply with Project requirements or authorities having jurisdiction. Retain first subparagraph to comply with LEED Prerequisite IEQ 1. See "LEED Rating System" Article in the Evaluations for discussion on this prerequisite.

3. Finish of Interior Surfaces: Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1.

4. Finish of Exterior Surfaces: Baked-on, textured vinyl enamel; color [as selected from manufacturer's standard colors] [to match computer equipment].

Retain subparagraph below for downflow units; delete for upflow units.

5. Floor Stand: Welded tubular steel, <Insert required height> high, with adjustable legs and vibration isolation pads.

E. Supply-Air Fan(s):

1. Double-inlet, forward-curved centrifugal fan(s); statically and dynamically balanced.

2. Drive: V-belt, with steel shaft with self-aligning ball bearings and cast-iron or steel sheaves, variable- and adjustable-pitch motor sheave, minimum of two matched belts, with drive rated at a minimum of two times the nameplate rating of motor.

Retain first paragraph below for units with direct-expansion refrigerant cooling.

F. Refrigeration System:

Retain one of first three subparagraphs below.

1. Compressors: Semihermetic reciprocating; with suction-gas-cooled, 1750-rpm motors; thermal overloads; oil sight glass; suction-line strainer; and reversible oil pumps; with[ oil strainer, internal motor overload protection,] resilient suspension system, crankcase heater, manual-reset high-pressure switch, and pump-down low-pressure switch.

2. Compressors: Hermetic reciprocating; with[ oil strainer, internal motor overload protection,] resilient suspension system, crankcase heater, manual-reset high-pressure switch, and pump-down low-pressure switch.

3. Compressors: Hermetic scroll; with[ oil strainer, internal motor overload protection,] resilient suspension system, crankcase heater, manual-reset high-pressure switch, and pump-down low-pressure switch.

4. Refrigeration Circuits: Two; each with hot-gas mufflers, thermal-expansion valve with external equalizer, liquid-line solenoid valve, liquid-line filter-dryer, sight glass with moisture indicator, service shutoff valves, charging valves, and charge of refrigerant.

Retain one of first two subparagraphs below to require a specific refrigerant type; delete both if any refrigerant type is acceptable. Retain second or third option in first subparagraph or retain second subparagraph to comply with LEED-NC, LEED-CS, and LEED for Schools Credit EA 4.

5. Refrigerant: [R-22] [R-407C] [R-410A] <Insert type>.

6. Refrigerant: R-407C or R-410A.

7. Refrigerant Evaporator Coil: Alternate-row or split-face-circuit, direct-expansion coil of seamless copper tubes expanded into aluminum fins.

ASHRAE compliance option in first subparagraph below may be required to comply with Project requirements or authorities having jurisdiction. Retain first option in first subparagraph to comply with LEED Prerequisite IEQ 1. See "LEED Rating System" Article in the Evaluations for discussion on this prerequisite.

a. Mount coil assembly over stainless-steel drain pan[ complying with ASHRAE 62.1] [and] [having a condensate pump unit with integral float switch, pump-motor assembly, and condensate reservoir].

Retain first option in subparagraph below to require unit manufacturer to provide a factory-installed disconnect switch. Standard unit does not come with disconnect switch. Switches provided by manufacturers may not be of quality required for Project. Coordinate with Section 262816 "Enclosed Switches and Circuit Breakers."

8. Remote Air-Cooled Refrigerant Condenser: Corrosion-resistant cabinet, copper-tube aluminum-fin coils arranged for two circuits, multiple direct-drive propeller fans with permanently lubricated ball bearings, and single-phase motors with internal overload protection and integral electric control panel[ and disconnect switch]. Control capacity by [cycling fans] [modulating fan speeds] [three-way refrigerant bypass with receiver and isolation valve].

Retain one of first four paragraphs below for units with heating.

G. Electric-Resistance Heating Coil: Enclosed finned-tube electric elements arranged for minimum of three stages, with thermal safety switches, manual-reset overload protection, and branch-circuit overcurrent protection.

H. Refrigerant Heating Coil: Hot-gas coil of seamless copper tubes expanded into aluminum fins with three-way solenoid valve on first-stage refrigerant circuit.

I. Hot-Water Heating Coil: Seamless copper tubes expanded into aluminum fins with two-way modulating control valve and strainer.

1. Control Valve: Class 125 body.

a. Maximum Pressure Drop: [3 psig (21 kPa)] [5 psig (35 kPa)] <Insert value> at design flow rate.

b. Close-Off (Differential) Pressure Rating: 100 percent of pressure differential across valve or 100 percent of total system (pump) head.

J. Extended-Surface, Disposable, Panel Filter: Pleated, lofted, nonwoven, reinforced cotton fabric; supported and bonded to welded-wire grid; enclosed in cardboard frame[ with 2-inch- (50-mm-) thick, disposable, glass-fiber prefilter].

Retain five subparagraphs below if multiple units are not scheduled on Drawings.

1. Thickness: [2 inches (50 mm)] [4 inches (100 mm)].

2. Initial Resistance: <Insert inches wg (Pa)>.

3. Recommended Final Resistance: <Insert inches wg (Pa)>.

4. Arrestance (ASHRAE 52.1): [90] <Insert number> percent.

LEED Prerequisite IEQ 1 requires compliance with ASHRAE 62.1, which requires a MERV rating of 6 or higher. See "LEED Rating System" Article in the Evaluations for discussion on this prerequisite.

5. Merv (ASHRAE 52.2): [7] <Insert value>.

Retain one or both of first two paragraphs below for units with humidifiers. Retain more than one paragraph to allow Contractor to choose.

K. Infrared Humidifier: High-intensity quartz lamps mounted above stainless-steel evaporator pan, serviceable without disconnecting water, drain, or electrical connections; prepiped and using condensate water from cooling coils with stainless-steel or brass float-valve mechanism; located in bypass airstream; with flush-cycle timer and solenoid drain valve.

L. Evaporative Pan Humidifier: Stainless-steel pan and cover, serviceable without disconnecting water, drain, or electrical connections; prepiped with stainless-steel or brass float-valve mechanism; electric-resistance heating coil; low-water-cutoff switch; flush-cycle timer; and solenoid drain valve.

M. Integral Electrical Controls: Unit-mounted electrical enclosure with piano-hinged door, grounding lug, combination magnetic starters with overload relays, circuit breakers and cover interlock, and fusible control-circuit transformer.

Retain first paragraph below to require unit manufacturer to provide a factory-installed disconnect switch. Standard unit does not come with disconnect switch. Switches provided by manufacturers may not be of quality required for Project. Coordinate with Section 262816 "Enclosed Switches and Circuit Breakers."

N. Disconnect Switch: Nonautomatic, molded-case circuit breaker with handle accessible when panel is closed and capable of preventing access until switched to off position.

Paragraph below is representative of standard electronic controls, which are offered by most manufacturers.

O. Electronic-Control System: Solid state, with start button, stop button, temporary loss of power indicator, manual-reset circuit breakers, temperature control, humidity control, and monitor panel.

1. Monitor Panel: Backlighted, with no visible indicator lights until operating function is activated; indicators include cooling, humidification, loss of airflow, change filters, high temperature, low temperature, high humidity, low humidity, high head pressure (each compressor), and low suction pressure (each compressor).

2. Temperature- and Humidity-Control Modules: Solid state, plug-in; with adjustable set point, push-to-test calibration check button, and built-in visual indicators to show mode of operation.

3. Location: Behind hinged door in front of unit; isolated from conditioned airstream to allow service while system is operating.

2.2 FLOOR-MOUNTED UNITS 5 TONS (18 kW) AND SMALLER

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Airflow Company; a division of The McClain Company, Inc.

2. Carrier Corporation; a United Technologies company.

3. Compu-Aire, Inc.

4. Data Aire Inc.

5. Koldwave, Inc.; a Mestek company.

6. Liebert Corporation.

7. McQuay International.

8. Stulz-ATS.

9. Trane; a business of American Standard Companies.

10. <Insert manufacturer's name>.

C. Description: Self-contained, factory assembled, prewired, and prepiped; consisting of cabinet, fan, filters, and controls; for vertical floor mounting in upflow or downflow configuration.

D. Cabinet and Frame: Welded tubular-steel frame with removable steel panels with baked-enamel finish, insulated with 1-inch- (25-mm-) thick duct liner.

Retain first subparagraph below for downflow units; delete for upflow units.

1. Floor Stand: Welded tubular steel, <Insert required height> high, with adjustable legs and vibration isolation pads.

Retain subparagraph below to comply with LEED Prerequisite IEQ 1. See "LEED Rating System" Article in the Evaluations for discussion on this prerequisite.

2. Finish of Interior Surfaces: Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1.

E. Supply-Air Fan: Forward curved, centrifugal, and with adjustable V-belt drive.

Retain first paragraph below for units with direct-expansion refrigerant cooling.

F. Refrigeration System:

1. Compressor: Hermetic, with oil strainer, internal motor overload protection, resilient suspension system, and crankcase heater.

2. Refrigeration Circuit: Low-pressure switch, manual-reset high-pressure switch, thermal-expansion valve with external equalizer, sight glass with moisture indicator, service shutoff valves, charging valves, and charge of refrigerant.

Retain one of first two subparagraphs below to require a specific refrigerant type; delete both if any refrigerant type is acceptable. Retain second or third option in first subparagraph or retain second subparagraph to comply with LEED-NC, LEED-CS, and LEED for Schools Credit EA 4.

3. Refrigerant: [R-22] [R-407C] [R-410A] <Insert type>.

4. Refrigerant: R-407C or R-410A.

5. Refrigerant Evaporator Coil: Direct-expansion coil of seamless copper tubes expanded into aluminum fins, with two circuits, each with solenoid valve.

Retain first option in first subparagraph below to comply with LEED Prerequisite IEQ 1. See "LEED Rating System" Article in the Evaluations for discussion on this prerequisite.

a. Mount coil assembly over stainless-steel drain pan[ complying with ASHRAE 62.1] [and] [having a condensate pump unit with integral float switch, pump-motor assembly, and condensate reservoir].

6. Remote Air-Cooled Refrigerant Condenser: Integral, copper-tube aluminum-fin coil with [propeller] [centrifugal] fan, [direct] [belt] driven.

7. Split system shall have suction- and liquid-line compatible fittings and refrigerant piping for field interconnection.

Retain first paragraph below for units with heating.

G. Electric-Resistance Heating Coil: Finned-tube electric elements with contactor and high-temperature-limit switches.

H. Filter: 2-inch- (50-mm-) thick, disposable, glass-fiber media.

Retain four subparagraphs below if multiple units are not scheduled on Drawings.

1. Initial Resistance: <Insert inches wg (Pa)>.

2. Recommended Final Resistance: <Insert inches wg (Pa)>.

3. Arrestance (ASHRAE 52.1): [90] <Insert number> percent.

LEED Prerequisite IEQ 1 requires compliance with ASHRAE 62.1, which requires a MERV rating of 6 or higher. See "LEED Rating System" Article in the Evaluations for discussion on this prerequisite.

4. Merv (ASHRAE 52.2): [7] <Insert value>.

Humidifiers are optional features on this type of equipment.

I. Infrared Humidifier: High-intensity quartz lamps mounted above stainless-steel evaporator pan, serviceable without disconnecting water, drain, or electrical connections; prepiped and located in bypass airstream; with flush-cycle timer and solenoid drain valve.

Retain first paragraph below to require unit manufacturer to provide a factory-installed disconnect switch. Standard unit does not come with disconnect switch. Switches provided by manufacturers may not be of quality required for Project. Coordinate with Section 262816 "Enclosed Switches and Circuit Breakers."

J. Disconnect Switch: Nonautomatic, molded-case circuit breaker with handle accessible when panel is closed and capable of preventing access until switched to off position.

K. Control System: Unit-mounted panel with main fan contactor, compressor contactor, compressor start capacitor, control transformer with circuit breaker, solid-state temperature-[ and humidity-]control modules[, humidity contactor], time-delay relay, Heating contactor, and high-temperature thermostat. Provide solid-state, wall-mounted control panel with start-stop switch[, adjustable humidity set point,] and adjustable temperature set point.

2.3 CEILING-MOUNTED UNITS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Airflow Company; a division of The McClain Company, Inc.

2. Carrier Corporation; a United Technologies company.

3. Compu-Aire, Inc.

4. Data Aire Inc.

5. Koldwave, Inc.; a Mestek company.

6. Liebert Corporation.

7. McQuay International.

8. Stulz-ATS.

9. Trane; a business of American Standard Companies.

10. <Insert manufacturer's name>.

C. Description: Self-contained, factory assembled, prewired, and prepiped; consisting of cabinet, fan, filters, and controls; for horizontal ceiling mounting to fit T-bar ceiling opening of 24 by 48 inches (610 by 1220 mm).

D. Cabinet: Galvanized steel with baked-enamel finish, insulated with 1/2-inch- (13-mm-) thick duct liner.

Retain first subparagraph below for units where grilles are available, usually 1.5 tons (5.2 kW) and smaller.

1. Integral factory-supplied supply and return grille to fit ceiling grid kit of 24 by 48 inches (610 by 1220 mm), with filter.

Retain subparagraph below to comply with LEED Prerequisite IEQ 1. See "LEED Rating System" Article in the Evaluations for discussion on this prerequisite.

2. Finish of Interior Surfaces: Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1.

E. Supply-Air Fan: Forward curved, centrifugal, and directly driven by two-speed motor.

Retain first paragraph below for units with direct-expansion refrigerant cooling.

F. Refrigeration System:

1. Compressor: Hermetic, with oil strainer, internal motor overload protection, resilient suspension system, and crankcase heater.

2. Refrigeration Circuit: Low-pressure switch, manual-reset high-pressure switch, thermal-expansion valve with external equalizer, sight glass with moisture indicator, service shutoff valves, charging valves, and charge of refrigerant.

Retain one of first two subparagraphs below to require a specific refrigerant type; delete both if any refrigerant type is acceptable. Retain second or third option in first subparagraph or retain second subparagraph to comply with LEED-NC, LEED-CS, and LEED for Schools Credit EA 4.

3. Refrigerant: [R-22] [R-407C] [R-410A] <Insert type>.

4. Refrigerant: R-407C or R-410A.

5. Refrigerant Evaporator Coil: Direct-expansion coil of seamless copper tubes expanded into aluminum fins.

Retain first option in first subparagraph below to comply with LEED Prerequisite IEQ 1. See "LEED Rating System" Article in the Evaluations for discussion on this prerequisite.

a. Mount coil assembly over stainless-steel drain pan[ complying with ASHRAE 62.1] [and] [having a condensate pump unit with integral float switch, pump-motor assembly, and condensate reservoir].

6. Remote Air-Cooled Refrigerant Condenser: Integral, copper-tube aluminum-fin coil with [propeller] [centrifugal] fan, direct driven.

7. Split system shall have suction- and liquid-line compatible fittings and refrigerant piping for field interconnection.

Retain first paragraph below for units with heating.

G. Electric-Resistance Heating Coil: Finned-tube electric elements with contactor, dehumidification relay, and high-temperature-limit switches.

H. Filter: 1-inch- (25-mm-) thick, disposable, glass-fiber media.

Retain four subparagraphs below if multiple units are not scheduled on Drawings.

1. Initial Resistance: <Insert inches wg (Pa)>.

2. Recommended Final Resistance: <Insert inches wg (Pa)>.

3. Arrestance (ASHRAE 52.1): [90] <Insert number> percent.

LEED Prerequisite IEQ 1 requires compliance with ASHRAE 62.1, which requires a MERV rating of 6 or higher. See "LEED Rating System" Article in the Evaluations for discussion on this prerequisite.

4. Merv (ASHRAE 52.2): [7] <Insert value>.

Humidifiers are optional features on this type of equipment.

I. Atomizing Humidifier: Centrifugal atomizer with stainless-steel pan, demister pad, and solenoid valve.

Retain first paragraph below to require unit manufacturer to provide a factory-installed disconnect switch. Standard unit does not come with disconnect switch. Switches provided by manufacturers may not be of quality required for Project. Coordinate with Section 262816 "Enclosed Switches and Circuit Breakers."

J. Disconnect Switch: Nonautomatic, molded-case circuit breaker with handle accessible when panel is closed and capable of preventing access until switched to off position.

K. Control System: Unit-mounted panel with main fan contactor, compressor contactor, compressor start capacitor, control transformer with circuit breaker, solid-state temperature-[ and humidity-]control modules[, humidity contactor], time-delay relay, Heating contactor, and high-temperature thermostat. Provide solid-state, wall-mounted control panel with start-stop switch[, adjustable humidity set point,] and adjustable temperature set point.

2.4 CONSOLE UNITS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Carrier Corporation; a United Technologies company.

2. Compu-Aire, Inc.

3. Data Aire Inc.

4. Koldwave, Inc.; a Mestek company.

5. Liebert Corporation.

6. McQuay International.

7. Stulz-ATS.

8. Trane; a business of American Standard Companies.

9. <Insert manufacturer's name>.

C. Description: Split system consisting of evaporator section for floor or wall mounting and remote condensing section.

D. Evaporator Cabinet: Furniture-grade steel with baked-enamel finish; with front access and containing direct-drive centrifugal fans and two-speed motor.

Retain subparagraph below to comply with LEED Prerequisite IEQ 1. See "LEED Rating System" Article in the Evaluations for discussion on this prerequisite.

1. Finish of Interior Surfaces: Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1.

E. Condenser Cabinet: Steel with baked-enamel finish and containing compressor and condenser.

Retain first paragraph below for units with direct-expansion refrigerant cooling.

F. Refrigeration System:

1. Compressor: Hermetic, with oil strainer, internal motor overload protection, resilient suspension system, and crankcase heater.

2. Refrigeration Circuit: Filter/dryer, manual-reset high-pressure switch, thermal-expansion valve with external equalizer, sight glass with moisture indicator, service shutoff valves, charging valves, and charge of refrigerant.

Retain one of first two subparagraphs below to require a specific refrigerant type; delete both if any refrigerant type is acceptable. Retain second or third option in first subparagraph or retain second subparagraph to comply with LEED-NC, LEED-CS, and LEED for Schools Credit EA 4.

3. Refrigerant: [R-22] [R-407C] [R-410A] <Insert type>.

4. Refrigerant: R-407C or R-410A.

5. Refrigerant Evaporator Coil: Direct-expansion coil of seamless copper tubes expanded into aluminum fins.

Retain first option in first subparagraph below to comply with LEED Prerequisite IEQ 1. See "LEED Rating System" Article in the Evaluations for discussion on this prerequisite.

a. Mount coil assembly over stainless-steel drain pan[ complying with ASHRAE 62.1] [and] [having a condensate pump unit with integral float switch, pump-motor assembly, and condensate reservoir].

6. Remote Air-Cooled Refrigerant Condenser: Integral, copper-tube aluminum-fin coil with [propeller] [centrifugal] fan, direct driven.

7. Split system shall have suction- and liquid-line compatible fittings and refrigerant piping for field interconnection.

Retain first paragraph below for units with heating.

G. Electric-Resistance Heating Coil: Finned-tube electric elements with contactor and high-temperature-limit switches.

Retain one of first two paragraphs below. LEED Prerequisite IEQ 1 requires compliance with ASHRAE 62.1, which requires a MERV rating of 6 or higher. See "LEED Rating System" Article in the Evaluations for discussion on this prerequisite. Retain second paragraph and MERV 7 or higher if applying for LEED credits. Verify availability with manufacturers.

H. Filter: Cleanable.

I. Filter: 1-inch- (25-mm-) thick, disposable, glass-fiber media.

Retain four subparagraphs below if multiple units are not scheduled on Drawings.

1. Initial Resistance: <Insert inches wg (Pa)>.

2. Recommended Final Resistance: <Insert inches wg (Pa)>.

3. Arrestance (ASHRAE 52.1): [90] <Insert number> percent.

4. Merv (ASHRAE 52.2): [7] <Insert value>.

Retain first paragraph below to require unit manufacturer to provide a factory-installed disconnect switch. Standard unit does not come with disconnect switch. Switches provided by manufacturers may not be of quality required for Project. Coordinate with Section 262816 "Enclosed Switches and Circuit Breakers."

J. Disconnect Switch: Nonautomatic, molded-case circuit breaker with handle accessible when panel is closed and capable of preventing access until switched to off position.

K. Control System: Unit-mounted panel with contactors, control transformer with circuit breaker, and solid-state temperature-[ and humidity-]control modules. Provide solid-state, unit-mounted control panel with start-stop switch[, adjustable humidity set point,] and adjustable temperature set point.

2.5 FAN MOTORS

Default motor characteristics are specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

A. Comply with NEMA designation, temperature rating, service factor, enclosure type, and efficiency requirements for motors specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

1. Motor Sizes: Minimum size as indicated. If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

2. Controllers, Electrical Devices, and Wiring: Comply with requirements for electrical devices and connections specified in electrical Sections.

If unique characteristics are required for motors in this Section, insert paragraphs below.

B. <Insert unique motor characteristics>.

2.6 CAPACITIES AND CHARACTERISTICS

If Project has more than one type or configuration of computer-room air conditioner, delete this article and schedule units on Drawings.

Retain first paragraph below for floor-mounted units; delete for ceiling-mounted and console units.

A. Unit Configuration:

1. [Upflow] [Downflow].

2. [Draw] [Blow] through.

B. Supply-Air Fan:

1. Number of Fans: [One] [Two] <Insert number>.

2. Airflow: <Insert cfm (L/s)>.

3. Minimum Static Pressure: <Insert inches wg (kPa)>.

4. Motor Size: <Insert number> hp.

C. Refrigeration System:

Retain first subparagraph below if unit is equipped with refrigeration system.

1. Unit Energy Efficiency: <Insert COP or EER>.

2. Refrigerant Compressor:

a. Total Unit Cooling Capacity: <Insert Btu/h (kW)>.

b. Sensible Unit Cooling Capacity: <Insert Btu/h (kW)>.

c. Number of Compressors: [One] [Two] <Insert number>.

d. Motor Size: <Insert number> hp.

3. Refrigerant Evaporator Coil:

a. Cooling Capacity: <Insert Btu/h (kW)>.

b. Entering-Air Dry-Bulb Temperature: <Insert deg F (deg C)>.

c. Entering-Air Wet-Bulb Temperature: <Insert deg F (deg C)>.

d. Leaving-Air Dry-Bulb Temperature: <Insert deg F (deg C)>.

e. Leaving-Air Wet-Bulb Temperature: <Insert deg F (deg C)>.

Retain subparagraph below for air-cooled units.

4. Air-Cooled Refrigerant Condenser:

a. Cooling Capacity: <Insert Btu/h (kW)>.

b. Entering-Air Temperature: <Insert deg F (deg C)>.

c. Number of Condenser Fan Motors: <Insert number>.

d. Condenser Fan Motors: <Insert number> hp.

Retain first paragraph below for units with electric-resistance heating coils.

D. Electric-Resistance Heating Coil:

1. Total Capacity: <Insert kW>.

2. Stages of Heating: [1] [2]<Insert number>.

Retain first paragraph below for units with humidifiers.

E. Humidifier:

1. Total: <Insert lb/h (kg/h)>.

2. Input: <Insert Btu/h (kW)>.

F. Electrical Characteristics:

1. Volts: [120] [208] [240] [277] [480] <Insert value>.

2. Phase: [Single] [Three].

3. Hertz: 60.

4. Full-Load Amperes: <Insert value>.

5. Minimum Circuit Ampacity: <Insert value>.

6. Maximum Overcurrent Protection: <Insert amperage>.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Install computer-room air conditioners level and plumb, maintaining manufacturer's recommended clearances.[ Install according to ARI Guideline B.]

Retain one or more of three paragraphs below. Coordinate with Drawings and Sections specifying vibration and seismic controls. Retain or insert amount of required deflection.

B. Computer-Room Air-Conditioner Mounting: Install using [elastomeric pads] [elastomeric mounts] [restrained spring isolators] <Insert device>. Comply with requirements for vibration isolation devices specified in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

1. Minimum Deflection: [1/4 inch (6 mm)] [1 inch (25 mm)] <Insert dimension>.

C. Suspended Computer-Room Air Conditioners: Install using continuous-thread hanger rods and [elastomeric hangers] [spring hangers] [spring hangers with vertical-limit stop] of size required to support weight of computer-room air conditioner.

1. Comply with requirements for vibration isolation devices specified in [Section 230548 "Vibration and Seismic Controls for HVAC."] [Section 230548.13 "Vibration Controls for HVAC."] Fabricate brackets or supports as required.

2. Comply with requirements for hangers and supports specified in Section 230529 "Hangers and Supports for HVAC Piping and Equipment."

D. Air-Cooled Refrigerant Condenser Mounting: Install using [elastomeric pads] [elastomeric mounts] [restrained spring isolators] <Insert device>. Comply with requirements for vibration isolation devices specified in [Section 230548 "Vibration and Seismic Controls for HVAC."] [Section 230548.13 "Vibration Controls for HVAC."]

1. Minimum Deflection: [1/4 inch (6 mm)] [1 inch (25 mm)] <Insert dimension>.

3.2 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Piping installation requirements are specified in other heating, ventilating, and air-conditioning Sections. Drawings indicate general arrangement of piping, fittings, and specialties.

B. Install piping adjacent to machine to allow service and maintenance.

C. Water and Drainage Connections: Comply with applicable requirements in Section 221116 "Domestic Water Piping." Provide adequate connections for water-cooled units, condensate drain, and humidifier flushing system.

D. Refrigerant Piping: Comply with applicable requirements in Section 232300 "Refrigerant Piping." Provide shutoff valves and piping.

3.3 FIELD QUALITY CONTROL

A. Tests and Inspections:

1. Inspect for and remove shipping bolts, blocks, and tie-down straps.

2. After installing computer-room air conditioners and after electrical circuitry has been energized, test for compliance with requirements.

3. Operational Test: After electrical circuitry has been energized, start units to confirm proper motor rotation and unit operation.

4. Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

B. Computer-room air conditioners will be considered defective if they do not pass tests and inspections.

C. Prepare test and inspection reports.

D. After startup service and performance test, change filters and flush humidifier.

3.4 ADJUSTING

A. Adjust initial temperature[ and humidity] set points.

B. Set field-adjustable switches and circuit-breaker trip ranges as indicated.

C. Occupancy Adjustments: When requested within [12] <Insert number> months of date of Substantial Completion, provide on-site assistance in adjusting system to suit actual occupied conditions. Provide up to [two] <Insert number> visits to Project during other-than-normal occupancy hours for this purpose.

END OF SECTION 238123

	COMPUTER-ROOM AIR-CONDITIONERS
	238123 - 1



