Copyright 2011 AIA
MasterSpec Professional
09/11

Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 238126 - SPLIT-SYSTEM AIR-CONDITIONERS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

This Section includes requirements for the LEED Rating System. However, equipment specified in this Section may not qualify for LEED Rating System prerequisites and credits. Verify with manufacturers that the requirements for prerequisites and credits can be met. To achieve prerequisites and obtain credits, HVAC system design alternatives that do not include split-system air conditioners may be required.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section includes split-system air-conditioning and heat-pump units consisting of separate evaporator-fan and compressor-condenser components.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product indicated.

B. LEED Submittals:

Coordinate "Product Data for Credit EA 4" Subparagraph below with requirements for refrigerants.

1. Product Data for Credit EA 4: Documentation indicating that equipment and refrigerants comply.

2. Product Data for Prerequisite IEQ 1: Documentation indicating that units comply with ASHRAE 62.1, Section 5 - "Systems and Equipment."

C. Shop Drawings: Include plans, elevations, sections, details, and attachments to other work.

1. Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

1.3 INFORMATIONAL SUBMITTALS

A. Warranty: Sample of special warranty.

1.4 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

1.5 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

B. ASHRAE Compliance:

1. Fabricate and label refrigeration system to comply with ASHRAE 15, "Safety Standard for Refrigeration Systems."

"ASHRAE Compliance" Subparagraph below may be required to comply with Project requirements or authorities having jurisdiction. LEED Prerequisite IEQ 1 requires compliance with requirements in ASHRAE 62.1. In addition to establishing minimum ventilation rates, ASHRAE 62.1 includes requirements for controls, surfaces in contact with the airstream, particulate and gaseous filtration, humidification and dehumidification, drain-pan construction and connection, finned-tube coil selection and cleaning, and equipment access. See "LEED Rating System" Article in the Evaluations for discussion on this prerequisite. Verify, with manufacturers, availability of units with components and features that comply with these requirements.

2. ASHRAE Compliance: Applicable requirements in ASHRAE 62.1, Section 4 - "Outdoor Air Quality," Section 5 - "Systems and Equipment," Section 6 - " Procedures," and Section 7 - "Construction and System Start-up."

"ASHRAE/IESNA" Compliance Paragraph below may be required to comply with Project requirements or authorities having jurisdiction. LEED Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1. See "LEED Rating System" Article in the Evaluations for discussion on this prerequisite.

C. ASHRAE/IESNA Compliance: Applicable requirements in ASHRAE/IESNA 90.1.

1.6 WARRANTY

A. Special Warranty: Manufacturer's standard form in which manufacturer agrees to repair or replace components of split-system air-conditioning units that fail in materials or workmanship within specified warranty period.

Verify available warranties and warranty periods for units and components with manufacturers listed in Part 2 articles.

1. Warranty Period:

a. For Compressor: [One] [Five] <Insert number> year(s) from date of Substantial Completion.

b. For Parts: [One] [Five] <Insert number> year(s) from date of Substantial Completion.

c. For Labor: [One] [Five] <Insert number> year(s) from date of Substantial Completion.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of two paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

Verify that manufacturers retained in the list below make combination of unit components retained.

1. Carrier Corporation; Home Comfort and HVAC Building & Industrial Systems.

2. Coleman Company Inc. (The).

3. First Operations LP.

4. Friedrich Air Conditioning Company.

5. Koldwave, Inc.; a Mestek company.

6. Lennox International Inc.

7. Mitsubishi Electric & Electronics USA, Inc.; HVAC Advanced Products Division.

8. Mitsubishi Electric Sales Canada Inc.

9. Mitsubishi Heavy Industries America, Inc.

10. SANYO North America Corporation; SANYO Fisher Company.

11. Trane; a business of American Standard companies.

12. YORK; a Johnson Controls company.

13. <Insert manufacturer's name>.

2.2 INDOOR UNITS (5 TONS (18 kW) OR LESS)

A. Concealed Evaporator-Fan Components:

1. Chassis: Galvanized steel with flanged edges, removable panels for servicing, and insulation on back of panel.

2. Insulation: Faced, glass-fiber duct liner.

3. Refrigerant Coil: Copper tube, with mechanically bonded aluminum fins and thermal-expansion valve. Comply with ARI 206/110.

Retain one of first two subparagraphs below if heating coil is required.

4. Water Coil: Copper tube, with mechanically bonded aluminum fins spaced no closer than 0.1 inch (2.5 mm); leak tested to 300 psig (2070 kPa) underwater; with a two-position control valve.

5. Electric Coil: Helical, nickel-chrome, resistance-wire heating elements; with refractory ceramic support bushings, automatic-reset thermal cutout, built-in magnetic contactors, manual-reset thermal cutout, airflow proving device, and one-time fuses in terminal box for overcurrent protection.

6. Fan: Forward-curved, double-width wheel of galvanized steel; directly connected to motor.

7. Fan Motors:

a. Comply with NEMA designation, temperature rating, service factor, enclosure type, and efficiency requirements specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

b. Multitapped, multispeed with internal thermal protection and permanent lubrication.

c. Wiring Terminations: Connect motor to chassis wiring with plug connection.

ASHRAE compliance in "Airstream Surfaces" Subparagraph below may be required to comply with Project requirements or authorities having jurisdiction. Retain first subparagraph to comply with LEED Prerequisite IEQ 1.

8. Airstream Surfaces: Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1.

9. Filters: Permanent, cleanable.

10. Condensate Drain Pans:

First option in first subparagraph below is minimum slope in ASHRAE 62.1.

a. Fabricated with [one] [two] percent slope in at least two planes to collect condensate from cooling coils (including coil piping connections, coil headers, and return bends) and humidifiers, and to direct water toward drain connection.

ASHRAE compliance option in "Length" Subparagraph below may be required to comply with Project requirements or authorities having jurisdiction. Retain option in first subparagraph to comply with LEED Prerequisite IEQ 1; otherwise, insert distance.

1) Length: Extend drain pan downstream from leaving face [to comply with ASHRAE 62.1] <Insert distance>.

2) Depth: A minimum of [2 inches (50 mm)] <Insert depth> deep.

Retain one of first two subparagraphs below. Retain second subparagraph if drain-pan temperature is expected to fall below surrounding dew point temperature.

b. Single-wall, [galvanized] [stainless]-steel sheet.

c. Double-wall, [galvanized] [stainless]-steel sheet with space between walls filled with foam insulation and moisture-tight seal.

d. Drain Connection: Located at lowest point of pan and sized to prevent overflow. Terminate with threaded nipple on [one end] [both ends] of pan.

1) Minimum Connection Size: [NPS 1 (DN 25)] [NPS 2 (DN 50)] <Insert size>.

Retain first subparagraph below for galvanized-steel drain pans; delete for stainless-steel drain pans.

e. Pan-Top Surface Coating: Asphaltic waterproofing compound.

f. Units with stacked coils shall have an intermediate drain pan to collect condensate from top coil.

B. Floor-Mounted, Evaporator-Fan Components:

1. Cabinet: Enameled steel with removable panels on front and ends in color selected by Architect.

a. Discharge Grille: [Steel with surface-mounted frame] [Welded steel bars forming a linear grille and welded into supporting panel].

b. Insulation: Faced, glass-fiber duct liner.

c. Drain Pans: Galvanized steel, with connection for drain; insulated.

2. Refrigerant Coil: Copper tube, with mechanically bonded aluminum fins and thermal-expansion valve. Comply with ARI 206/110.

Retain one of first two subparagraphs below if heating coil is required.

3. Water Coil: Copper tube, with mechanically bonded aluminum fins spaced no closer than 0.1 inch (2.5 mm); leak tested to 300 psig (2070 kPa) underwater; with a two-position control valve.

4. Electric Coil: Helical, nickel-chrome, resistance-wire heating elements; with refractory ceramic support bushings, automatic-reset thermal cutout, built-in magnetic contactors, manual-reset thermal cutout, airflow proving device, and one-time fuses in terminal box for overcurrent protection.

5. Fan: Direct drive, centrifugal[, with power-induced outside air].

6. Fan Motors:

a. Comply with NEMA designation, temperature rating, service factor, enclosure type, and efficiency requirements specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

b. Multitapped, multispeed with internal thermal protection and permanent lubrication.

7. Air Filtration Section:

See Evaluations for discussion on filter characteristics and applications. LEED Prerequisite IEQ 1 requires compliance with ASHRAE 62.1, which requires a MERV rating of 6 or higher.

a. General Requirements for Air Filtration Section:

1) Comply with NFPA 90A.

2) Minimum Arrestance: According to ASHRAE 52.1 and MERV according to ASHRAE 52.2.

3) Filter-Holding Frames: Arranged for flat or angular orientation, with access doors on both sides of unit. Filters shall be removable from one side or lifted out from access plenum.

b. Disposable Panel Filters:

Retain one or more of first seven subparagraphs below, as applicable. If Project has more than one filter type, indicate filter type for each unit on Drawings.

1) Factory-fabricated, viscous-coated, flat-panel type.

2) Thickness: [1 inch (25 mm)] [2 inches (50 mm)].

3) Dust-Holding Capacity: <Insert lb (kg)>.

4) Initial Resistance: <Insert inches wg (Pa)>.

5) Recommended Final Resistance: <Insert inches wg (Pa)>.

6) Arrestance according to ASHRAE 52.1: [80] <Insert value>.

7) Merv according to ASHRAE 52.2: [5] <Insert value>.

8) Media: Interlaced glass fibers sprayed with nonflammable adhesive[ and antimicrobial agent].

9) Frame: Galvanized steel, with metal grid on outlet side, steel rod grid on inlet side, and hinged; with pull and retaining handles.

c. Extended-Surface, Disposable Panel Filters:

1) Factory-fabricated, dry, extended-surface type.

2) Thickness: [1 inch (25 mm)] [2 inches (50 mm)] [4 inches (100 mm)].

3) Dust-Holding Capacity: <Insert lb (kg)>.

4) Initial Resistance: <Insert inches wg (Pa)>.

5) Recommended Final Resistance: <Insert inches wg (Pa)>.

6) Arrestance according to ASHRAE 52.1: [90] <Insert value>.

7) Merv according to ASHRAE 52.2: [7] <Insert value>.

8) Media: Fibrous material formed into deep-V-shaped pleats[ with antimicrobial agent] and held by self-supporting wire grid.

9) Media-Grid Frame: [Nonflammable cardboard] [Galvanized steel] [Fire-retardant, 3/4-inch (20-mm) particleboard with gaskets].

10) Mounting Frames: Welded, galvanized steel, with gaskets and fasteners; suitable for bolting together into built-up filter banks.

C. Wall-Mounted, Evaporator-Fan Components:

1. Cabinet: Enameled steel with removable panels on front and ends in color selected by Architect, and discharge drain pans with drain connection.

2. Refrigerant Coil: Copper tube, with mechanically bonded aluminum fins and thermal-expansion valve. Comply with ARI 206/110.

Retain "Electric Coil" Subparagraph below for heat-pump units and supplemental electric heat.

3. Electric Coil: Helical, nickel-chrome, resistance-wire heating elements; with refractory ceramic support bushings, automatic-reset thermal cutout, built-in magnetic contactors, manual-reset thermal cutout, airflow proving device, and one-time fuses in terminal box for overcurrent protection.

4. Fan: Direct drive, centrifugal.

5. Fan Motors:

a. Comply with NEMA designation, temperature rating, service factor, enclosure type, and efficiency requirements specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

b. Multitapped, multispeed with internal thermal protection and permanent lubrication.

Retain first subparagraph below if enclosure is not open-dripproof type. Retain second subparagraph for premium efficiency.

c. Enclosure Type: Totally enclosed, fan cooled.

d. NEMA Premium (TM) efficient motors as defined in NEMA MG 1.

e. Controllers, Electrical Devices, and Wiring: Comply with requirements for electrical devices and connections specified in electrical Sections.

Retain first subparagraph below to require that disconnect switches be supplied with unit.

f. Mount unit-mounted disconnect switches on [exterior] [interior] of unit.

If unique characteristics are required for motors in this Section, insert subparagraphs below.

g. <Insert unique motor characteristics>.

ASHRAE compliance in "Airstream Surfaces" Subparagraph below may be required to comply with Project requirements or authorities having jurisdiction. Retain first subparagraph to comply with LEED Prerequisite IEQ 1.

6. Airstream Surfaces: Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1.

7. Condensate Drain Pans:

First option in first subparagraph below is minimum slope in ASHRAE 62.1.

a. Fabricated with [one] [two] percent slope in at least two planes to collect condensate from cooling coils (including coil piping connections, coil headers, and return bends) and humidifiers, and to direct water toward drain connection.

ASHRAE compliance option in "Length" Subparagraph below may be required to comply with Project requirements or authorities having jurisdiction. Retain option in first subparagraph to comply with LEED Prerequisite IEQ 1; otherwise, insert distance.

1) Length: Extend drain pan downstream from leaving face [to comply with ASHRAE 62.1] <Insert distance>.

2) Depth: A minimum of [1 inch (25 mm)] <Insert depth> deep.

Retain one of first two subparagraphs below.

b. Single-wall, [galvanized] [stainless]-steel sheet.

c. Double-wall, [galvanized] [stainless]-steel sheet with space between walls filled with foam insulation and moisture-tight seal.

d. Drain Connection: Located at lowest point of pan and sized to prevent overflow. Terminate with threaded nipple on [one end] [both ends] of pan.

1) Minimum Connection Size: [NPS 1 (DN 25)] [NPS 2 (DN 50)] <Insert size>.

Retain first subparagraph below for galvanized-steel drain pans; delete for stainless-steel drain pans.

e. Pan-Top Surface Coating: Asphaltic waterproofing compound.

8. Air Filtration Section:

See Evaluations for discussion on filter characteristics and applications. LEED Prerequisite IEQ 1 requires compliance with ASHRAE 62.1, which requires a MERV rating of 6 or higher.

a. General Requirements for Air Filtration Section:

1) Comply with NFPA 90A.

2) Minimum Arrestance: According to ASHRAE 52.1 and MERV according to ASHRAE 52.2.

3) Filter-Holding Frames: Arranged for flat or angular orientation, with access doors on both sides of unit. Filters shall be removable from one side or lifted out from access plenum.

b. Disposable Panel Filters:

Retain one or more of first seven subparagraphs below, as applicable. If Project has more than one filter type, indicate filter type for each unit on Drawings.

1) Factory-fabricated, viscous-coated, flat-panel type.

2) Thickness: [1 inch (25 mm)] [2 inches (50 mm)].

3) Dust-Holding Capacity: <Insert lb (kg)>.

4) Initial Resistance: <Insert inches wg (Pa)>.

5) Recommended Final Resistance: <Insert inches wg (Pa)>.

6) Arrestance according to ASHRAE 52.1: [80] <Insert value>.

7) Merv according to ASHRAE 52.2: [5] <Insert value>.

8) Media: Interlaced glass fibers sprayed with nonflammable adhesive[ and antimicrobial agent].

9) Frame: Galvanized steel, with metal grid on outlet side, steel rod grid on inlet side, and hinged; with pull and retaining handles.

c. Extended-Surface, Disposable Panel Filters:

1) Factory-fabricated, dry, extended-surface type.

2) Thickness: [1 inch (25 mm)] [2 inches (50 mm)] [4 inches (100 mm)].

3) Dust-Holding Capacity: <Insert lb (kg)>.

4) Initial Resistance: <Insert inches wg (Pa)>.

5) Recommended Final Resistance: <Insert inches wg (Pa)>.

6) Arrestance according to ASHRAE 52.1: [90] <Insert value>.

7) Merv according to ASHRAE 52.2: [7] <Insert value>.

8) Media: Fibrous material formed into deep-V-shaped pleats[ with antimicrobial agent] and held by self-supporting wire grid.

9) Media-Grid Frame: [Nonflammable cardboard] [Galvanized steel] [Fire-retardant, 3/4-inch (20-mm) particleboard with gaskets].

10) Mounting Frames: Welded, galvanized steel, with gaskets and fasteners; suitable for bolting together into built-up filter banks.

2.3 OUTDOOR UNITS (5 TONS (18 kW) OR LESS)

A. Air-Cooled, Compressor-Condenser Components:

1. Casing: Steel, finished with baked enamel in color selected by Architect, with removable panels for access to controls, weep holes for water drainage, and mounting holes in base. Provide brass service valves, fittings, and gage ports on exterior of casing.

2. Compressor: Hermetically sealed with crankcase heater and mounted on vibration isolation device. Compressor motor shall have thermal- and current-sensitive overload devices, start capacitor, relay, and contactor.

a. Compressor Type: Scroll.

Feature in first subparagraph below is not available from all manufacturers.

b. Two-speed compressor motor with manual-reset high-pressure switch and automatic-reset low-pressure switch.

LEED Credit EA 4 awards a single point if all HVAC&R equipment has HCFC-free refrigerants. R-407C and R-410A are HCFC-free refrigerants.

c. Refrigerant Charge: [R-22] [R-407C] [R-410A] <Insert type>.

d. Refrigerant Coil: Copper tube, with mechanically bonded aluminum fins and liquid subcooler. Comply with ARI 206/110.

Retain first subparagraph below for heat-pump units.

3. Heat-Pump Components: Reversing valve and low-temperature-air cutoff thermostat.

4. Fan: Aluminum-propeller type, directly connected to motor.

5. Motor: Permanently lubricated, with integral thermal-overload protection.

6. Low Ambient Kit: Permits operation down to 45 deg F (7 deg C).

7. Mounting Base: Polyethylene.

2.4 ACCESSORIES

Retain one of first three paragraphs below. Retain first paragraph if controls are part of overall temperature control system.

A. Control equipment and sequence of operation are specified in Section 230900 "Instrumentation and Control for HVAC" and Section 230993 "Sequence and Operations for HVAC Controls."

B. Thermostat: Low voltage with subbase to control compressor and evaporator fan.

C. Thermostat: Wireless infrared functioning to remotely control compressor and evaporator fan, with the following features:

1. Compressor time delay.

2. 24-hour time control of system stop and start.

3. Liquid-crystal display indicating temperature, set-point temperature, time setting, operating mode, and fan speed.

4. Fan-speed selection including auto setting.

D. Automatic-reset timer to prevent rapid cycling of compressor.

E. Refrigerant Line Kits: Soft-annealed copper suction and liquid lines factory cleaned, dried, pressurized, and sealed; factory-insulated suction line with flared fittings at both ends.

F. Drain Hose: For condensate.

LEED-NC and LEED for Schools Credit EA 5, LEED-CI Credit EA 3, and LEED-CS Credit EA 5.1 require continuous metering equipment for monitoring building energy consumption performance over time. Retain paragraph below if required to comply with requirements for this credit. Verify availability of control features with unit manufacturers or if required by Project requirements or authorities having jurisdiction.

G. Additional Monitoring:

1. Monitor constant and variable motor loads.

2. Monitor variable-frequency-drive operation.

3. Monitor economizer cycle.

4. Monitor cooling load.

5. Monitor air distribution static pressure and ventilation air volumes.

2.5 CAPACITIES AND CHARACTERISTICS

A. Cooling Capacity:

1. Total: <Insert value> Btu/h (kW).

2. Sensible: <Insert value> Btu/h (kW).

Retain "SEER" Subparagraph below for units with capacities 5 tons (18 kW) and less.

3. SEER: [10.0] [12.0] [13.0] [14.0] [16.0] <Insert ratio>.

Retain "EER" Subparagraph below for units with capacities 6 tons (21 kW) or more.

4. EER: [10.0] [12.0] [13.0] [14.0] [16.0] <Insert ratio>.

5. Moisture Removal: <Insert pints/h (L/h)>.

6. Entering-Air Temperature:

a. Dry Bulb: <Insert deg F (deg C)>.

b. Wet Bulb: <Insert deg F (deg C)>.

7. Leaving-Air Temperature:

a. Dry Bulb: <Insert deg F (deg C)>.

b. Wet Bulb: <Insert deg F (deg C)>.

B. Heating Capacity:

1. Type: [Electric] [Natural gas].

2. Total Capacity: <Insert value> Btu/h (kW).

3. Air-Temperature Rise: <Insert deg F (deg C)>.

Retain one or both of first two subparagraphs below for heat pumps.

4. Coefficient of Performance: <Insert value>.

5. Heating Season Performance Factor: [7.7] [8.0] <Insert value>.

Retain first subparagraph below for hydronic heating coil.

6. Hot Water:

a. Entering-Water Temperature: <Insert deg F (deg C)>.

b. Leaving-Water Temperature: <Insert deg F (deg C)>.

c. Water Flow: <Insert gpm (L/s)>.

d. Water Pressure Drop: <Insert feet of head (kPa)>.

Retain first subparagraph below for electric heating coil.

7. Electric Heating Coil:

a. Total Capacity: <Insert value> kW.

b. Volts: [120] [208] [230] [460] <Insert value>.

c. Phase: [Single] [Poly].

d. Hertz: 60.

e. Steps: [One] [Two] [Three] <Insert number>.

Retain subparagraph below for natural or propane gas heat.

8. Gas Heating Section:

a. Input: <Insert cfh (mL/s)>.

b. Output: <Insert cfh (mL/s)>.

C. Auxiliary Heating Capacity:

Retain first six subparagraphs below for heat pumps with auxiliary electric heat.

1. Type: [Electric] [Natural gas] [Propane].

2. Total Capacity: <Insert value> Btu/h (kW.)
3. Volts: [120] [208] [230] [460] <Insert value>.

4. Phase: [Single] [Poly].

5. Hertz: 60.

6. Steps: [One] [Two] [Three] <Insert number>.

Retain two subparagraphs below for auxiliary gas heat.

7. Input: <Insert cfh (mL/s)>.

8. Output: <Insert cfh (mL/s)>.

D. Indoor Unit:

1. Fan Motor Electrical Characteristics:

a. Volts: [120] [208] [230] [460] <Insert value>.

b. Phase: [Single] [Poly].

c. Hertz: 60.

2. Airflow: <Insert value> cfm (L/s).

E. Outdoor Unit:

1. Type: [Air cooled] [Water cooled].

2. Electrical Characteristics:

a. Volts: [120] [208] [230] [460] <Insert value>.

b. Phase: [Single] [Poly].

c. Hertz: 60.

d. Minimum Circuit Ampacity: <Insert value>.

e. Maximum Overcurrent Protection: <Insert amperage>.

f. Fan Motor Full-Load Amperes: <Insert value>.

g. Compressor Full-Load Amperes: <Insert value>.

h. Compressor Locked-Rotor Amperes: <Insert value>.

3. Sound-Pressure Level: <Insert value> dBa.

Retain subparagraph below for water-cooled outdoor units.

4. Water:

a. Entering-Water Temperature: <Insert deg F (deg C)>.

b. Water Flow: <Insert gpm (L/s)>.

c. Water Pressure Drop: <Insert feet of head (kPa)>.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Install units level and plumb.

B. Install evaporator-fan components using manufacturer's standard mounting devices securely fastened to building structure.

C. Install roof-mounted, compressor-condenser components on equipment supports specified in Section 077200 "Roof Accessories." Anchor units to supports with removable, cadmium-plated fasteners.

D. Equipment Mounting:

Retain first subparagraph below to require ground-mounted units to be installed on cast-in-place concrete equipment bases.

1. Install ground-mounted, compressor-condenser components on cast-in-place concrete equipment base(s). Comply with requirements for equipment bases and foundations specified in [Section 033000 "Cast-in-Place Concrete."] [Section 033053 "Miscellaneous Cast-in-Place Concrete."]

2. Install ground-mounted, compressor-condenser components on polyethylene mounting base.

Retain one of two subparagraphs below. Retain first for projects in seismic areas; retain second for projects not in seismic areas. Indicate vibration isolation and seismic-control device type and minimum deflection in supported equipment schedule on Drawings.

3. Comply with requirements for vibration isolation and seismic control devices specified in Section 230548 "Vibration and Seismic Controls for HVAC."

4. Comply with requirements for vibration isolation devices specified in Section 230548.13 "Vibration Controls for HVAC."

E. Install and connect precharged refrigerant tubing to component's quick-connect fittings. Install tubing to allow access to unit.

3.2 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Piping installation requirements are specified in other Sections. Drawings indicate general arrangement of piping, fittings, and specialties.

Retain first subparagraph below for units with hot-water coils.

1. Water Coil Connections: Comply with requirements specified in Section 232113 "Hydronic Piping" and Section 232116 "Hydronic Piping Specialties."Section 15179 "Hydronic Piping Specialties." Connect hydronic piping to supply and return coil connections with shutoff-duty valve and union or flange on the supply connection and with throttling-duty valve and union or flange on the return connection.

Retain subparagraph below for units with remote water-cooled condenser.

2. Remote, Water-Cooled Condenser Connections: Comply with requirements specified in Section 232113 "Hydronic Piping" and Section 232116 "Hydronic Piping Specialties."Section 15179 "Hydronic Piping Specialties." Connect hydronic piping to supply and return connections with shutoff-duty valve and union or flange on the supply connection and with throttling-duty valve and union or flange on the return connection.

B. Where piping is installed adjacent to unit, allow space for service and maintenance of unit.

Retain paragraph below for units connected to ducts. Coordinate duct installation requirements with schematics on Drawings and with requirements specified for duct systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

C. Duct Connections: Duct installation requirements are specified in Section 233113 "Metal Ducts." Drawings indicate the general arrangement of ducts. Connect supply[ and return] ducts to split-system air-conditioning units with flexible duct connectors. Flexible duct connectors are specified in Section 233300 "Air Duct Accessories."

3.3 FIELD QUALITY CONTROL

A. Perform tests and inspections.

Retain subparagraph below to require a factory-authorized service representative to assist Contractor with inspections, tests, and adjustments.

1. Manufacturer's Field Service: Engage a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

Retain first paragraph below to describe tests and inspections to be performed.

B. Tests and Inspections:

1. Leak Test: After installation, charge system and test for leaks. Repair leaks and retest until no leaks exist.

2. Operational Test: After electrical circuitry has been energized, start units to confirm proper motor rotation and unit operation.

3. Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.

C. Remove and replace malfunctioning units and retest as specified above.

D. Prepare test and inspection reports.

3.4 DEMONSTRATION

A. [Engage a factory-authorized service representative to train] [Train] Owner's maintenance personnel to adjust, operate, and maintain units.

END OF SECTION 238126

	SPLIT-SYSTEM AIR-CONDITIONERS
	238126 - 1



