Copyright 2012 AIA
MasterSpec Professional
03/12

Copyright 2012 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 238146.13 - WATER-TO-AIR HEAT PUMPS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

This Section includes requirements for the LEED Rating System. However, equipment specified in this Section may not qualify for LEED Rating System prerequisites and credits. Verify, with manufacturers, that the requirements for prerequisites and credits can be met. To achieve prerequisites and obtain credits, HVAC system design alternatives that do not include water-source unitary heat pumps may be required.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Concealed horizontal or vertical units, 6 tons (21 kW) and smaller.

2. Exposed, floor-mounted console units.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product.

B. LEED Submittals:

1. Product Data for Credit EA 4: Documentation indicating that equipment and refrigerants comply.

2. Product Data for Prerequisite IEQ 1: Documentation indicating that units comply with ASHRAE 62.1, Section 5 - "Systems and Equipment."

C. Shop Drawings: Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

1. Include diagrams for power, signal, and control wiring.

1.3 INFORMATIONAL SUBMITTALS

A. Field quality-control reports.

B. Sample Warranty: For special warranty.

1.4 CLOSEOUT SUBMITTALS

A. Operation and maintenance data

1.5 QUALITY ASSURANCE

A. ASHRAE Compliance:

1. ASHRAE 15.

2. Applicable requirements in ASHRAE 62.1, Section 5 - "Systems and Equipment" and Section 7 - "Construction and Startup."

B. ASHRAE/IESNA Compliance: Applicable requirements in ASHRAE/IESNA 90.1, Section 6 - "Heating, Ventilating, and Air-Conditioning."

C. Comply with NFPA 70.

D. Comply with safety requirements in UL 484 for assembly of free-delivery, water-source heat pumps.

E. Comply with safety requirements in UL 1995 for duct-system connections.

1.6 WARRANTY

A. Special Warranty: Manufacturer agrees to repair or replace components of water-source heat pumps that fail in materials or workmanship within specified warranty period.

1. Failures include, but are not limited to, refrigeration components.

2. Warranty Period: [Four] <Insert number> years from date of Substantial Completion.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

2.1 CONCEALED WATER-SOURCE HEAT PUMPS, 6 TONS (21 kW) AND SMALLER

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Carrier Corporation.

2. ClimateMaster, Inc.

3. FHP Manufacturing Inc.

4. Hydro-Temp Corporation, Inc.

5. Mammoth Inc.

6. McQuay International.

7. Trane Inc.

8. WaterFurnace International, Inc.

9. <Insert manufacturer's name>.

C. Description: Packaged water-source heat pump with temperature controls; factory assembled, tested, and rated according to ASHRAE/ARI/ISO-13256-1.

1. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a testing agency acceptable to authorities having jurisdiction, and marked for intended location and application.

D. Cabinet and Chassis: Galvanized-steel casing with the following features:

1. Access panel for access and maintenance of internal components.

2. Knockouts for electrical and piping connections.

3. Flanged duct connections.

4. Cabinet Insulation: Glass-fiber liner, minimum 1/2 inch (13 mm) thick, complying with UL 181, ASTM C 1071, and ASTM G 21.

5. Units field convertible for various discharge configurations.

ASHRAE compliance option in "Condensate Drainage" Subparagraph below may be required to comply with Project requirements or authorities having jurisdiction. Retain option in subparagraph to comply with LEED Prerequisite IEQ 1.

6. Condensate Drainage: High-density polyethylene plastic or stainless-steel drain pan with condensate drain piping projecting through unit cabinet[ and complying with ASHRAE 62.1].

a. Condensate Overflow Protection Switch: Solid state electronic; mechanical float switch not permitted.

ASHRAE compliance in "Airstream Surfaces" Subparagraph below may be required to comply with Project requirements or authorities having jurisdiction. Retain subparagraph to comply with LEED Prerequisite IEQ 1.

7. Airstream Surfaces: Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1.

E. Fan: Direct driven, centrifugal, with multispeed motor resiliently mounted in fan inlet and with inlet rings to allow wheel removal from one side without removing housing.

1. General requirements for motors are specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

2. Motor: Multispeed, permanently lubricated, [permanent split capacitor] [ECM] motor.

F. Water Circuit:

1. Refrigerant-to-Water Heat Exchangers:

Retain one of first two subparagraphs below.

a. Coaxial heat exchangers with [copper] [cupronickel] water tube with enhanced heat-transfer surfaces inside a steel shell; both shell and tube are leak tested to 450 psig (3102 kPa) on refrigerant side and 400 psig (2758 kPa) on water side. Factory mount heat exchanger in unit on resilient rubber vibration isolators.

b. Stainless-steel, brazed-plate heat exchanger is leak tested to 450 psig (3102 kPa) on refrigerant side and 400 psig (2758 kPa) on water side. Factory mount heat exchanger in unit on resilient rubber vibration isolators.

2. Water-Regulating Valves: Limit water flow through refrigerant-to-water heat exchanger, and control head pressure on compressor during cooling and heating. Valves shall close when heat-pump compressor is not running.

3. Motorized Water Valve: Stop water flow through the unit when compressor is off.

G. Refrigerant-to-Air Coils: Copper tubes with aluminum fins, leak tested to 450 psig (3102 kPa).

H. Refrigerant Circuit Components:

1. Sealed Refrigerant Circuit: Charge with R-410A refrigerant.

2. Filter-Dryer: Factory installed to clean and dehydrate the refrigerant circuit.

3. Charging Connections: Service fittings on suction and liquid for charging and testing on each circuit.

4. Reversing Valve: Four-way, solenoid-activated valve designed to be fail-safe in heating position with replaceable magnetic coil.

5. Compressor: Hermetic [rotary] [reciprocating] [scroll], [single-stage] [two-stage] compressor installed on vibration isolators and housed in an acoustically treated enclosure with factory-installed safeties as follows:

a. Antirecycle timer.

b. High-pressure cutout.

c. Low-pressure cutout or loss of charge switch.

d. Internal thermal-overload protection.

e. Freezestat to stop compressor if water-loop temperature in refrigerant-to-water heat exchanger falls below [35 deg F (2 deg C)] <Insert temperature>.

f. Condensate overflow switch to stop compressor with high condensate level in condensate drain pan.

g. Water-coil, low-temperature switch.

h. Air-coil, low-temperature switch.

6. Refrigerant Piping Materials: ASTM B 743 copper tube with wrought-copper fittings and brazed joints.

7. Pipe Insulation: Refrigerant minimum 3/8-inch- (10-mm-) thick, flexible elastomeric insulation on piping exposed to airflow through the unit. Maximum 25/50 flame-spread/smoke-developed indexes according to ASTM E 84.

8. Refrigerant Metering Device: Thermal-expansion valve.

9. Refrigerant Metering Device: Dual-port, thermal-expansion valve to allow specified operation with entering-water temperatures from [25 to 125 deg F (minus 4 to plus 52 deg C)] <Insert temperature range>.

10. Hot-Gas Reheat Valve: Pilot-operated, sliding-type valve with replaceable magnetic coil.

I. Electric Heating Coil: Helix-wound, nickel-chromium, wire-heating elements in ceramic insulators mounted on steel supports. Energize on call for heating when entering-water-loop temperature is less than [25 deg F (minus 4 deg C)] [40 deg F (5 deg C)] [60 deg F (15 deg C)] <Insert temperature>.

J. Hot-Gas Reheat: Reheat valve diverts refrigerant hot gas to reheat coil when remote humidistat calls for dehumidification.

Retain one of two "Filters" paragraphs below. Verify availability of filter options in first paragraph with manufacturers. Retain second paragraph if applying for LEED certification. LEED Prerequisite IEQ 1 requires compliance with ASHRAE 62.1, which requires a MERV rating of 6 or higher.

K. Filters: Disposable, glass-fiber, flat type, [1 inch (25 mm)] <Insert dimension> thick, treated with adhesive, and having a minimum efficiency reporting value of 5 according to ASHRAE 52.2.

L. Filters: Disposable, pleated type, [1 inch (25 mm)] <Insert dimension> thick and with a minimum efficiency reporting value of 7 according to ASHRAE 52.2.

M. Controls:

1. Basic Unit Control Modes and Devices:

a. Dehumidification mode.

b. Unit shutdown on high or low refrigerant pressures.

c. Unit shutdown on low water temperature.

d. Low- and high-voltage protection.

e. Overcurrent protection for compressor and fan motor.

f. Random time delay, three to ten seconds, start on power-up.

g. Time delay override for servicing.

h. Control voltage transformer.

i. Water-coil freeze protection (selectable for water or antifreeze).

j. Air-coil freeze protection (check filter switch).

k. Condensate overflow shutdown switch.

l. Option to reset unit at thermostat or disconnect.

m. Fault type shall be retained in memory if reset at thermostat.

n. Automatic intelligent reset. Unit shall automatically reset five minutes after trip if the fault has cleared. Should a fault reoccur three times sequentially, lockout requiring manual reset occurs.

o. Ability to defeat time delays for servicing.

p. Light-emitting diodes (LED) to indicate high pressure, low pressure, low voltage, and high voltage.

q. The low-pressure switch SHALL NOT be monitored for the first 90 seconds after a compressor start command to prevent nuisance safety trips.

r. Remote fault-type indication at thermostat.

s. Selectable 24-V dc or pilot duty dry contact alarm output.

t. 24-V dc output to cycle a motorized water valve with compressor contactor.

u. Electric heat output to control two stages of electric heat (emergency heat).

v. Service test mode for troubleshooting and service.

w. Unit-performance sentinel warns when the heat pump is running inefficiently.

2. Thermostat:

a. Wall-Mounted Thermostat:

1) Heat-cool-off switch.

2) Fan on-auto switch.

3) [Manual] [Automatic] changeover.

4) [Concealed] [Exposed] temperature set point.

5) [Concealed] [Exposed] temperature indication.

6) Deg [F] [C] indication.

b. Wall-Mounted Humidistat: [Concealed] [Exposed].

1) Temperature set point.

2) Temperature indication.

c. Wall-mounted temperature sensor.

d. Unoccupied period override push button.

e. LED to indicate fault condition at heat pump.

f. Data entry and access port.

1) Input data include room temperature and humidity set points for occupied and unoccupied periods.

2) Output data include room temperature and humidity, supply-air temperature, entering-water temperature, operating mode, and status.

3. Terminal Controller:

a. Scheduled operation for occupied and unoccupied periods on [seven] [365]-day clock with minimum of four programmable periods per day.

b. [Two] <Insert number>-hour unoccupied override period.

c. Remote-control panel to contain programmable timer and LED for fault condition.

d. Compressor disable relay to stop compressor operation for demand limiting or switch to unoccupied operation.

e. Automatic restart after five minutes if fault clears. Lockout after three attempts to restart following fault. Indicate fault for service technician.

f. Return-air temperature high-limit (firestat). Stop unit on high temperature.

g. Backup for volatile memory.

h. Differential pressure switch to indicate fan status. Fan failure alarm.

i. Differential pressure switch to indicate filter status. Dirty filter alarm.

N. Electrical Connection: Single electrical connection[ with fused disconnect].

If Project has more than one of this type of heat pump, delete "Capacities and Characteristics" Paragraph below and schedule heat pumps on Drawings.

O. Capacities and Characteristics:

1. Fan:

a. Airflow: <Insert cfm (L/s)>.

b. External Static Pressure: <Insert inches wg (kPa)>.

c. Fan Speed: <Insert rpm>.

d. Motor Speed: <Insert rpm>.

e. Motor Horsepower: <Insert value>.

2. Water Supply:

a. Water Flow: <Insert gpm (L/s)>.

b. Pressure Loss: <Insert feet wg (kPa)>.

c. Entering-Water Temperature (Cooling): <Insert deg F (deg C)>.

d. Entering-Water Temperature (Heating): <Insert deg F (deg C)>.

e. Antifreeze Protection Chemical: <Insert chemical name>.

f. Antifreeze Concentration: <Insert percentage>.

3. Cooling:

a. Total Capacity: <Insert Btu/h (kW)>.

b. Sensible Capacity: <Insert Btu/h (kW)>.

LEED Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1, Table 6.8.1B, "Electrically Operated Unitary and Applied Heat Pumps - Minimum Efficiency Requirements."

c. Minimum Energy-Efficiency Ratio (EER): <Insert value>.

d. Entering-Air Temperature Dry Bulb: <Insert deg F (deg C)>.

e. Entering-Air Temperature Wet Bulb: <Insert deg F (deg C)>.

4. Heating:

a. Capacity: <Insert Btu/h (kW)>.

b. Entering-Air Temperature: <Insert deg F (deg C)>.

c. Air Temperature Rise: <Insert deg F (deg C)>.

LEED Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1, Table 6.8.1B, "Electrically Operated Unitary and Applied Heat Pumps - Minimum Efficiency Requirements."

d. Minimum Coefficient of Performance (COP): <Insert value>.

5. Electric Heating Coil (Optional Feature):

a. Capacity: <Insert Btu/h (kW)>.

b. Number of Steps: <Insert number>.

6. Filters:

a. Face Area: <Insert sq. ft. (sq. m)>.

b. Maximum Face Velocity: <Insert fpm (m/s)>.

7. Electrical Characteristics for Single Connection:

a. Volts: [120] [208] [230] <Insert value>.

b. Phase: [Single] [Three].

c. Hertz: 60.

d. Full-Load Amperes (F.L.A.): <Insert value>.

e. Maximum Circuit Amperage (MCA): <Insert value>.

f. Maximum Overcurrent Protection (MOCP): <Insert amperes>.

2.2 EXPOSED, CONSOLE WATER-SOURCE HEAT PUMPS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Carrier Corporation.

2. ClimateMaster, Inc.

3. FHP Manufacturing Inc.

4. Hydro-Temp Corporation, Inc.

5. Mammoth Inc.

6. McQuay International.

7. Trane Inc.

8. WaterFurnace International, Inc.

9. <Insert manufacturer's name>.

C. Description: Packaged water-source heat pump with temperature controls; factory assembled, tested, and rated according to ASHRAE/ARI/ISO-13256-1.

1. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a testing agency acceptable to authorities having jurisdiction, and marked for intended location and application.

D. Cabinet and Chassis: Manufacturer's [standard] [low] [standard- and low]-height, [flat] [sloped]-top, [extended ]galvanized-steel casing with the following features:

1. Access panel for access and maintenance of internal components.

2. Knockouts for electrical and piping connections.

3. Cabinet Insulation: Glass-fiber liner, minimum 1/2 inch (13 mm) thick, complying with UL 181, ASTM C 1071, and ASTM G 21.

4. Cabinet Insulation: Glass-fiber liner, minimum 1/2 inch (13 mm) thick, complying with ASTM C 1071 and NAIMA AH124, "Fibrous Glass Duct Liner Standard."

ASHRAE compliance option in "Condensate Drainage" Subparagraph below may be required to comply with Project requirements or authorities having jurisdiction. Retain option to comply with LEED Prerequisite IEQ 1.

5. Condensate Drainage: High-density polyethylene plastic or stainless-steel drain pan with condensate drain piping projecting to unit exterior[ and complying with ASHRAE 62.1].

a. Condensate Overflow Protection: Solid state electronic; mechanical float switch not permitted.

6. Discharge Grille: Steel, aluminum, or plastic grille for adjustable discharge air pattern.

7. Color: Selected by Architect from manufacturer's [standard] [custom] color selection.

ASHRAE compliance with "Airstream Surfaces" Subparagraph below may be required to comply with Project requirements or authorities having jurisdiction. Retain subparagraph to comply with LEED Prerequisite IEQ 1.

8. Airstream Surfaces: Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1.

E. Fan: Direct driven, centrifugal, with multispeed motor mounted on a removable fan-motor board.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Section 230513 "Common Motor Requirements for HVAC Equipment." If different characteristics are required, add subparagraphs below to suit Project.

1. General requirements for motors are specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

2. Motor: Multispeed, permanently lubricated, [permanent split capacitor] [ECM].

F. Water Circuit:

1. Refrigerant-to-Water Heat Exchanger: Coaxial heat exchanger with [copper] [cupronickel] water tube with enhanced heat-transfer surfaces inside a steel shell; both shell and tube are leak tested to 450 psig (3102 kPa) for refrigerant side and 400 psig (2758 kPa) for water side. Factory mount heat exchanger in unit on resilient rubber vibration isolators.

2. Water-Regulating Valves: Limit water flow through refrigerant-to-water heat exchanger and control head pressure on compressor during cooling and heating. Valves shall close when heat-pump compressor is not running.

G. Refrigerant-to-Air Coils: Copper tubes with aluminum fins, leak tested to 450 psig (3102 kPa).

H. Refrigerant Circuit Components:

1. Sealed Refrigerant Circuit: Charge with R-410A refrigerant.

Filter-dryer is unavailable from some manufacturers.

2. Filter-Dryer: Factory installed to clean and dehydrate the refrigerant circuit.

3. Charging Connections: Service fittings on suction and liquid for charging and testing.

4. Reversing Valve: Four-way, solenoid-activated valve designed to be fail-safe in heating position with replaceable magnetic coil.

5. Compressor: Hermetic rotary compressor installed on vibration isolators housed in an acoustically treated enclosure with factory-installed safeties as follows:

a. Antirecycle timer.

b. High-pressure cutout.

c. Low-pressure cutout or loss of charge switch.

d. Internal thermal-overload protection.

e. Freezestat to stop compressor if water-loop temperature in refrigerant-to-water heat exchanger falls below [35 deg F (2 deg C)] <Insert temperature>.

f. Condensate overflow switch to stop compressor with high condensate level in condensate drain pan.

g. Water-coil, low-temperature switch.

h. Air-coil, low-temperature switch.

6. Refrigerant Piping Materials: ASTM B 743 copper tube with wrought-copper fittings and brazed joints.

7. Pipe Insulation: Refrigerant minimum 3/8-inch- (10-mm-) thick, flexible elastomeric insulation on piping exposed to airflow through the unit. Maximum 25/50 flame-spread/smoke-developed indexes per ASTM E 84.

8. Refrigerant Metering Device: Dual-port, thermal-expansion valve to allow specified operation with entering-water temperatures from [25 to 125 deg F (minus 4 to 52 deg C)] <Insert temperature range>.

9. Hot-Gas Reheat Valve: Pilot-operated, sliding-type valve with replaceable magnetic coil.

I. Electric Heating Coil: Energized on call for heating when entering-water-loop temperature is less than [60 deg F (15 deg C)] <Insert temperature>.

J. Hot-Gas Reheat: Reheat valve diverts refrigerant hot gas to reheat coil when [remote] [unit-mounted] humidistat calls for dehumidification.

ASHRAE/IESNA 90.1 sets requirements for dampers. If applying for LEED certification, retain second option in "Outdoor-Air Damper" Paragraph below to comply with ASHRAE/IESNA 90.1.

K. Outdoor-Air Damper: Two-position, [manual] [motorized] outdoor-air damper for fixed minimum intake up to 25 percent of fan capacity.

Retain one of two "Filters" paragraphs below. Verify availability of filter options in first paragraph with manufacturers. Retain second paragraph if applying for LEED certification. LEED Prerequisite IEQ 1 requires compliance with ASHRAE 62.1, which requires a MERV rating of 6 or higher.

L. Filters: Disposable, glass-fiber, flat type, [1 inch (25 mm)] <Insert dimension> thick, treated with adhesive, and having a minimum efficiency reporting value of 5 according to ASHRAE 52.2.

M. Filters: Disposable, pleated type, [1 inch (25 mm)] <Insert dimension> thick and with a minimum efficiency reporting value of 7 according to ASHRAE 52.2.

N. Controls:

1. Basic Unit Control Modes and Devices:

a. Dehumidification mode.

b. Unit shutdown on high or low refrigerant pressures.

c. Unit shutdown on low water temperature.

d. Low- and high-voltage protection.

e. Overcurrent protection for compressor and fan motor.

f. Random time delay, three to ten seconds, start on power-up.

g. Time delay override for servicing.

h. Control voltage transformer.

i. Water-coil freeze protection (selectable for water or antifreeze).

j. Air-coil freeze protection (check filter switch).

k. Condensate overflow shutdown switch.

l. Option to reset unit at thermostat or disconnect.

m. Fault type shall be retained in memory if reset at thermostat.

n. Automatic intelligent reset. Unit shall automatically reset five minutes after trip if the fault has cleared. Should a fault reoccur three times sequentially, lockout requiring manual reset occurs.

o. Ability to defeat time delays for servicing.

p. Light-emitting diodes (LED) to indicate high pressure, low pressure, low voltage, and high voltage.

q. The low-pressure switch SHALL NOT be monitored for the first 90 seconds after a compressor start command to prevent nuisance safety trips.

r. Remote fault-type indication at thermostat.

s. Selectable 24-V dc or pilot duty dry contact alarm output.

t. 24V dc output to cycle a motorized water valve with compressor contactor.

u. Electric heat output to control two stages of electric heat (emergency heat).

v. Service test mode for troubleshooting and service.

w. Unit-performance sentinel warns when the heat pump is running inefficiently.

2. Thermostat:

a. [Wall] [Unit]-Mounted Thermostat:

1) Heat-cool-off switch.

2) Fan on-auto switch.

3) [Manual] [Automatic] changeover.

4) [Concealed] [Exposed] temperature set point.

5) [Concealed] [Exposed] temperature indication.

6) Deg [F] [C] indication.

b. [Wall] [Unit]-Mounted Humidistat: [Concealed] [Exposed].

1) Temperature set point.

2) Temperature indication.

c. [Wall] [Unit]-mounted temperature sensor.

d. Unoccupied period override push button.

e. LED to indicate fault condition at heat pump.

f. Data entry and access port.

1) Input data include room temperature and humidity set points for occupied and unoccupied periods.

2) Output data include room temperature and humidity, supply-air temperature, entering-water temperature, operating mode, and status.

3. Terminal Controller:

a. Scheduled operation for occupied and unoccupied periods on [seven] [365]-day clock with minimum of four programmable periods per day.

b. [Two] <Insert number>-hour unoccupied override period.

c. Compressor disable relay to stop compressor operation for demand limiting or switch to unoccupied operation.

d. Automatic restart after five minutes if fault clears. Lockout after three attempts to restart following fault. Indicate fault for service technician.

e. Backup for volatile memory.

f. Differential pressure switch to indicate fan status. Fan failure alarm.

g. Differential pressure switch to indicate filter status. Dirty filter alarm.

O. Electrical Connection: Single electrical connection[ with fused disconnect].

If Project has more than one of this type of heat pump, delete "Capacities and Characteristics" Paragraph below and schedule heat pumps on Drawings.

P. Capacities and Characteristics:

1. Fan:

a. Airflow: <Insert cfm (L/s)>.

b. External Static Pressure: <Insert inches wg (kPa)>.

c. Fan Speed: <Insert rpm>.

d. Motor Speed: <Insert rpm>.

e. Motor Horsepower: <Insert value>.

2. Water Supply:

a. Water Flow: <Insert gpm (L/s)>.

b. Pressure Loss: <Insert feet wg (kPa)>.

c. Entering-Water Temperature (Cooling): <Insert deg F (deg C)>.

d. Entering-Water Temperature (Heating): <Insert deg F (deg C)>.

e. Antifreeze Protection Chemical: <Insert chemical name>.

f. Antifreeze Concentration: <Insert percentage>.

3. Cooling:

a. Total Capacity: <Insert Btu/h (kW)>.

b. Sensible Capacity: <Insert Btu/h (kW)>.

LEED Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1, Table 6.8.1B, "Electrically Operated Unitary and Applied Heat Pumps - Minimum Efficiency Requirements."

c. Minimum Energy-Efficiency Ratio (EER): <Insert value>.

d. Entering-Air Temperature Dry Bulb: <Insert deg F (deg C)>.

e. Entering-Air Temperature Wet Bulb: <Insert deg F (deg C)>.

4. Heating:

a. Capacity: <Insert Btu/h (kW)>.

b. Entering-Air Temperature: <Insert deg F (deg C)>.

c. Air Temperature Rise: <Insert deg F (deg C)>.

LEED Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1, Table 6.8.1B, "Electrically Operated Unitary and Applied Heat Pumps - Minimum Efficiency Requirements."

d. Minimum Coefficient of Performance (COP): <Insert value>.

5. Electric Heating Coil (Optional Feature):

a. Capacity: <Insert Btu/h (kW)>.

b. Number of Steps: <Insert number>.

6. Filters:

a. Face Area: <Insert sq. ft. (sq. m)>.

b. Maximum Face Velocity: <Insert fpm (m/s)>.

7. Electrical Characteristics for Single Connection:

a. Volts/Phase/Hertz: <Insert values>.

b. Full-Load Amperes (F.L.A.): <Insert value>.

c. Maximum Circuit Amperage (MCA): <Insert value>.

d. Maximum Overcurrent Protection (MOCP): <Insert amperes>.

2.3 HOSE KITS

Retain this article for hose kits furnished with each water-source heat pump. Revise for size and components. Delete this article if retaining "Hose Kit Assemblies" Article.

A. General: Hose kits shall be designed for minimum 400-psig (2758-kPa) working pressure and operating temperatures from 33 to 211 deg F (0.5 to 99 deg C). Tag hose kits to equipment designations.

B. Hose: Length [24 inches (600 mm)] [36 inches (900 mm)] braided stainless steel, complete with adapters, <Insert dimension>. Minimum diameter, equal to water-source, heat-pump connection size.

C. Isolation Valves: Two-piece, bronze-body ball valves with stainless-steel, standard-port ball and stem with normal pipe thread (NPT) connections, and galvanized-steel lever handle. Provide valve for supply and return. If balancing device is combination shutoff type with memory stop, the isolation valve may be omitted on the return.

D. Strainer: Y-type with blowdown valve in supply connection.

E. Balancing Device: Mount in return connection. Include meter ports to allow flow measurement with differential pressure gage.

Retain one of three subparagraphs below. Retain more than one if using different balancing valves on different heat-pump types.

1. Automatic balancing valve, factory set to operate within 10 percent of design flow rate over a 40:1 differential pressure range of 2 to 80 psig (13.8 to 552 kPa).

2. Manual, calibrated-orifice balancing valve.

3. Manual, venturi-type balancing valve.

F. Motorized Water Valve: Slow-acting, 24-V dc, with NPT connections.

2.4 HOSE KIT ASSEMBLIES

The assemblies in this article ship with the valves already assembled to the hose described.

A. Supply and return hoses having ball valve with pressure temperature port.

B. Supply hose having ball valve with pressure temperature port; return hose having automatic flow regulator valve with pressure temperature ports, and ball valve.

C. Supply hose having "Y" strainer with blowdown valve, and ball valve with pressure temperature port; return hose having automatic flow regulator with PT ports, and ball valve.

D. Supply hose having "Y" strainer with blowdown valve, and ball valve with pressure temperature port.

E. Return hose having ball valve with pressure temperature port.

2.5 PUMP MODULE

Retain this article for individual heat pumps that stand alone from a central circulating water loop. Values in first paragraph below are examples only; verify actual values with manufacturer.

A. Minimum [1/6] <Insert value>-hp, 230-V, single-phase pump rated to move at least [16 gpm (1 L/s)] <Insert value> at [20-feet wg (59-kPa)] <Insert value> head pressure.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Section 230513 "Common Motor Requirements for HVAC Equipment." If different characteristics are required, add subparagraphs below to suit Project.

1. General requirements for motors are specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

B. Include pump module hose kit with thread to barb fittings, hose, and hose clamps.

C. Three-way brass shut-off/flushing/purging valve.

D. Include controls to operate pump as required to maintain room temperature and ventilation set points.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Equipment Mounting:

Retain first subparagraph below to require equipment to be installed on cast-in-place concrete equipment bases.

1. Install water-source heat pumps on cast-in-place concrete equipment base(s). Comply with requirements for equipment bases and foundations specified in [Section 033000 "Cast-in-Place Concrete."] [Section 033053 "Miscellaneous Cast-in-Place Concrete."]

Retain one of two subparagraphs below. Retain first for projects in seismic areas; retain second for projects not in seismic areas. Indicate vibration isolation and seismic-control device type and minimum deflection in supported equipment schedule on Drawings.

2. Comply with requirements for vibration isolation and seismic control devices specified in Section 230548 "Vibration and Seismic Controls for HVAC."

3. Comply with requirements for vibration isolation devices specified in Section 230548.13 "Vibration Controls for HVAC."

B. Install wall-mounting thermostats, humidistats, and switch controls in electrical outlet boxes at heights to match lighting controls or as required in Section 230900 "Instrumentation and Control for HVAC."

C. Connect supply and return hydronic piping to heat pump.

D. Connect heat-pump condensate drain pan to indirect waste connection with condensate trap of adequate depth to seal against fan pressure. Install cleanouts in piping at changes of direction.

E. Connect supply and return ducts to water-source heat pumps with flexible duct connectors specified in Section 233300 "Air Duct Accessories."

F. Install electrical devices furnished by manufacturer but not specified to be factory mounted.

G. Install piping adjacent to machine to allow service and maintenance.

H. Ground equipment according to Section 260526 "Grounding and Bonding for Electrical Systems."

I. Connect wiring according to Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

3.2 FIELD QUALITY CONTROL

A. Perform the following field tests and inspections:

1. After installing water-source heat pumps and after electrical circuitry has been energized, test units for compliance with requirements.

2. Inspect for and remove shipping bolts, blocks, and tie-down straps.

3. Operational Test: After electrical circuitry has been energized, start units to confirm proper motor rotation and unit operation.

4. Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.

B. Heat pumps will be considered defective if they do not pass tests and inspections.

C. Prepare test and inspection reports.

END OF SECTION 238146.13

	WATER-TO-AIR HEAT PUMPS
	238146.13 - 1



